APPENDIX D
Form 400C:  Add the following front page to the following north, central and south Florida back pages:  
FLORIDA ENERGY EFFICIENCY CODE FOR BUILDING CONSTRUCTION
SUBCHAPTER 4 – Commercial Building Compliance Methods
Form 400C-04                                                                                                                                                                                              North
Building Prescriptive Envelope Method                                                                                                                                                   Compliance Zones 1 2 3	
Project Name:	Zone:	
Address:	Building Classification:	
City, Zip Code:	Building Permit No.:	
Builder:	Permitting Office:	
Owner:	Jurisdiction No.:	
	
BUILDING ENVELOPE INFORMATION	

ENVELOPE COMPONENT	Non-residential	Residential	Semiheated	
	U-factor	R-value	U-factor	R-value	U-factor	R-value	
Roof type:							
Wall type:							
Floor type:							
Fenestration 	Max. U-factor
Fixed/operable	Max. SHGC
All orientation.	Max. U-factor
Fixed/operable	Max. SHGC
All orientation	Max. U-factor
Fixed/operable	Max. SHGC
All orientation	
Vertical glazing type, % of wall: 							
Skylight type, % of roof:							
SYSTEMS INFORMATION	
SYSTEM	Type (describe system)	Size (capacity)	Sizing calc.	Efficiency	Rating	
Air conditioning system						
Heating system						
Ventilation						
Ducts	              Location::	Fan power:		R-value		
Piping	              Fluid design operating temp:	Size of pipe:	---------	Inches		
Hot water			---------	EF		
Electric power	Drawings	Y	N	Operations Manual available upon completion:            Y        N	
Motors 	Open or enclosed		Poles & speed		Horsepower:		
Lighting	Space type:		Lighting power density				
PRESCRIPTIVE MEASURES	
Components	Section 	Requirements	Check	
Operations Manual	102.1, 410, 413	Operations manual provided to owner		
Windows & Doors	406.1ABC.1.1	Glazed swinging entrance & revolving doors: max. 1.0 cfm/ft2;all other products: 0.4 cfm/ft2 		
Joints/Cracks	406.1.ABC.1.2	To be caulked, gasketed, weatherstripped or otherwise sealed.		
Dropped ceiling cavity	406.1.ABC.1.4	Vented: seal & insulate ceiling.  Unvented: seal & insulate roof & side walls.		
Reheat	407.1.BC	Electric resistance reheat prohibited.		
HVAC efficiency	407.1, 408.1	Minimum efficiencies: Cooling Tables 407.1.ABC.3.2A-D; Heating Tables 407.1.ABC.3.2B, 
407.1ABC.3.2D, 408.1.ABC.3.2E thru 408.1.ABC.3.2G.		
HVAC Controls	407.1.ABC.2	Zone controls prevent reheat (exceptions); separate thermostatic control per zone; 
combined HAC control 5oF deadband (exceptions).		
Ventilation	409.1.ABC.3	Motorized dampers reqd. except gravity dampers OK in 1) exhaust systems & 2) systems 
with design outside air intake or exhaust capacity <300 cfm		
HVAC Ducts	410.1.ABC	Air ducts, fittings, mechanical equipment & plenum chambers shall be mechanically 
attached, sealed, insulated & installed per Sec. 410.1.ABC.  Fan power limitations.		
Balancing	410.1.ABC.4	HVAC distribution system(s) tested & balanced. Report in construction documents.		
Piping insulation 	411.1.ABC	In accordance with Table 411.1.ABC.2.		
Water heaters	412.1.ABC	Performance requirements in accordance with Table 412.1.ABC.3. Heat trap required.		
Swimming pools	412.1.ABC.2.6	Cover on heated pools; Time switch (exceptions); Readily accessible on/off switch.		
Hot Water Pipe 
Insulation.	412.1.ABC.4	Table 411.1.ABC.2 for circulating systems, first 8’ outlet pipe from storage tank, between inlet pipe and heat trap.		
Water Fixtures	412.1.ABC.2.5.2	Shower heat water flow restricted to 2.5 gpm at 80 psi. Public lavatory fixture max. flow 
0.5 gpm; if self-closing valve 0.25 gallon circulating, 0.5 gallon non-circulating.		
Lighting Controls	415.1.ABC	Automatic control required for interior lighting in buildings <5,000s.f.; Space control; 
Exterior photo sensor; Tandem wiring where 1-3 linear fluorescent lamps > 30W.		
If required by Florida law, I hereby certify that the system design is in compliance with the Florida energy code.             Registration No.
ARCHITECT:_________________________________________________________________________________________________________
ELECTRICAL SYSTEM DESIGNER:______________________________________________________________________________________
LIGHTING SYSTEM DESIGNER:_________________________________________________________________________________________
MECHANICAL SYSTEM DESIGNER:______________________________________________________________________________________
PLUMBING SYSTEM DESIGNER:_________________________________________________________________________________________	
I hereby certify that the plans and specifications covered by the 
calculation are in compliance with the Florida energy code.
PREPARED BY:____________________________DATE:________
I hereby certify that this building is in compliance with the Florida 
energy code:
OWNER AGENT:___________________________DATE:__________	Review of plans and specifications covered by this calculation indicates 
compliance with the Florida energy code. Before construction is completed,
this building will be inspected for compliance in accordance with Section 
553.908, F.S.
BUILDING OFFICIAL:_________________________________________
DATE::_______________________________________________________	

 Form 400C-04  											Climate Zones, 1,2,3
Building Prescriptive Envelope Method								North
Opaque Elements	Nonresidential	Residential	Semiheated	
	Assembly Maximum	Insulation Min. R-value	Assembly Maximum	Insulation Min. R-Value	Assembly Maximum	Insulation Min.1 R-Value	
Roofs							
   Insulation all above deck	U-0.063	R-15.0 ci	U-0.063	R-15.0 ci	U-0.218	R-3.8 ci	
   Metal building	U-0.065	R-19.0	U-0.065	R-19	U-0.167	R-6.0	
   Attic and Other	R-0.034	R-30.0	U-0.034	R-30.0	U-0.081	R-13.0	
Walls, Above grade							
   Mass	U-0.580	NR	U-0.151	R-5.7 ci2	U-0.580	NR	
   Metal building	U-0.113	R-13.0	U-0.113	R-13.0	U-0.184	R-6.0	
   Steel framed	U-0.124	R-13.0	U-0.124	R-13.0	U-0.352	NR	
   Wood framed and Other	U-0.089	R-13.0	U-0.089	R-13.0	U-0.292	NR	
Walls, Below Grade							
   Below grade wall	C-1.140	NR	C-1.140	NR	C-1.140	NR	
Floors							
   Mass	U-0.137	R-4.2 ci	U-0.107	R-6.3 ci	U-0.322	NR	
   Steel joist	U-0.052	R-19.0	U-0.052	R-19.0	U-0.350	NR	
   Wood framed and Other	U-0.051	R-19.0	U-0.051	R-19.0	U-0.282	NR	
Slab-On-Grade Floors							
   Unheated	F-0.730	NR	F-0.730	NR	F-0.730	NR	
   Heated	F-1.020	R-7.5 for 12 in.	F-1.020	R-7.5 for 12 in.	F-1.020	R-7.5 for 12 in	
Opaque Doors							
   Swinging	U-0.700		U-0.700		U-0.700		
   Non-swinging	U-1.450		U-1.450		U-1.450		
Fenestration	Assembly 
Max. U
(Fixed/ Operable)	Assembly 
Max. SHGC 
(all orientations/
North-Oriented)	Assembly Max. U (Fixed/ Operable)	Assembly 
Max. SHGC 
(all orientations/ North-Oriented) 	Assembly Max. U (Fixed/ Operable)	Assembly 
Max. SHGC 
(all orientations/ North-Oriented)	
Vertical Glazing, % of wall							
   0 – 10%	Ufixed –1.22
Uoper-1.27	SHGCall – 0.39
SHGCnorth-0.61	Ufixed –1.22
Uoper-1.27	SHGCall – 0.61
SHGCnorth-0.61	Ufixed –1.22
Uoper-1.27	SHGCall – NR
SHGCnorth-NR	
   10.1 – 20%	Ufixed –1.22
Uoper-1.27	SHGCall – 0.25
SHGCnorth-0.61	Ufixed –1.22
Uoper-1.27	SHGCall – 0.44
SHGCnorth-0.61	Ufixed –1.22
Uoper-1.27	SHGCall – NR
SHGCnorth-NR	
   20.1 – 30%	Ufixed –1.22
Uoper-1.27	SHGCall – 0.25
SHGCnorth-0.61	Ufixed –1.22
Uoper-1.27	SHGCall – 0.44
SHGCnorth-0.61	Ufixed –1.22
Uoper-1.27	SHGCall – NR
SHGCnorth-NR	
   30.1 – 40%	Ufixed –1.22
Uoper-1.27	SHGCall – 0.25
SHGCnorth-0.61	Ufixed –1.22
Uoper-1.27	SHGCall – 0.40
SHGCnorth-0.61	Ufixed –1.22
Uoper-1.27	SHGCall – NR
SHGCnorth-NR	
   40.1 – 50%	Ufixed –1.22
Uoper-1.27	SHGCall – 0.17
SHGCnorth-0.42	Ufixed –1.22
Uoper-1.27	SHGCall – 0.29
SHGCnorth-0.41	Ufixed –0.98
Uoper-1.02	SHGCall – NR
SHGCnorth-NR	
Skylight with curb, glass, 
% roof    							
   0 – 2.0%	Uall -1.98	SHGCall – 0.39	Uall -1.98	SHGCall – 0.36	Uall -1.98	SHGCall – NR	
   2.1 – 5.0%	Uall -1.98	SHGCall – 0.25	Uall -1.98	SHGCall – 0.19	Uall -1.98	SHGCall – NR	
Skylight with curb, plastic
% roof							
   0 – 2.0%	Uall -1.90	SHGCall – 0.65	Uall -1.90	SHGCall – 0.27	Uall -1.90	SHGCall – NR	
   2.1 – 5.0%	Uall -1.90	SHGCall – 0.39	Uall -1.90	SHGCall – 0.27	Uall -1.90	SHGCall – NR	
Skylight without curb, all
% roof							
   0 – 2.0%	Uall -1.36	SHGCall – 0.39	Uall -1.36	SHGCall – 0.36	Uall -1.36	SHGCall – NR	
   2.1 – 5.0%	Uall -1.36	SHGCall – 0.25	Uall -1.36	SHGCall – 0.19	Uall -1.36	SHGCall – NR	
1The following definitions apply: ci=continuous insulation; NR=no (insulation) requirements. 2 Exception to 402.1.C.1 applies for mass walls.

Form 400C-04											Climate Zones 4,5,6
Building Prescriptive Envelope Method							Central
Opaque Elements	Nonresidential	Residential	Semiheated	
	Assembly Maximum	Insulation Min. R-value	Assembly Maximum	Insulation Min. R-Value	Assembly Maximum	Insulation Min.1 R-Value	
Roofs							
   Insulation all above deck	U-0.063	R-15.0 ci	U-0.063	R-15.0 ci	U-1.282	NR	
   Metal building	U-0.065	R-19.0	U-0.065	R-19.0	U-1.280	NR	
   Attic and Other	R-0.034	R-30.0	U-0.027	R-38.0	U-0.614	NR	
Walls, Above grade							
   Mass	U-0.580	NR	U-0.1511	R-5.7 ci2	U-0.580	NR	
   Metal building	U-0.113	R-13.0	U-0.113	R-13.0	U-1.180	NR	
   Steel framed	U-0.124	R-13.0	U-0.124	R-13.0	U-0.352	NR	
   Wood framed and Other	U-0.089	R-13.0	U-0.089	R-13.0	U-0.292	NR	
Walls, Below Grade							
   Below grade wall	C-1.140	NR	C-1.140	NR	C-1.140	NR	
Floors							
   Mass	U-0.322	NR	U-0.322	NR	U-0.322	NR	
   Steel joist	U-0.350	NR	U-0.350	NR	U-0.350	NR	
   Wood framed and Other	U-0.282	NR	U-0.282	NR	U-0.282	NR	
Slab-On-Grade Floors							
   Unheated	F-0.730	NR	F-0.730	NR	F-0.730	NR	
   Heated	F-1.020	R-7.5 for 12 in.	F-1.020	R-7.5 for 12 in.	F-1.020	R-7.5 for 12 in.	
Opaque Doors							
   Swinging	U-0.700		U-0.700		U-0.700		
   Non-swinging	U-1.450		U-1.450		U-1.450		
Fenestration	Assembly Max. U
(Fixed/ Operable)	Assembly 
Max. SHGC 
(all orientations/ North-Oriented)	Assembly Max. U (Fixed/ Operable)	Assembly 
Max. SHGC 
(all orientations/ North-Oriented) 	Assembly Max. U (Fixed/ Operable)	Assembly 
Max. SHGC 
(all orientations/ North-Oriented)	
Vertical Glazing, % of wall							
   0 – 10%	Ufixed –1.22
Uoper-1.27	SHGCall – 0.40
SHGCnorth-0.61	Ufixed –1.22
Uoper-1.27	SHGCall – 0.40
SHGCnorth-0.61	Ufixed –1.22
Uoper-1.27	SHGCall – NR
SHGCnorth-NR	
   10.1 – 20%	Ufixed –1.22
Uoper-1.27	SHGCall – 0.25
SHGCnorth-0.61	Ufixed –1.22
Uoper-1.27	SHGCall – 0.40
SHGCnorth-0.61	Ufixed –1.22
Uoper-1.27	SHGCall – NR
SHGCnorth-NR	
   20.1 – 30%	Ufixed –1.22
Uoper-1.27	SHGCall – 0.25
SHGCnorth-0.61	Ufixed –1.22
Uoper-1.27	SHGCall – 0.40
SHGCnorth-0.61	Ufixed –1.22
Uoper-1.27	SHGCall – NR
SHGCnorth-NR	
   30.1 – 40%	Ufixed –1.22
Uoper-1.27	SHGCall – 0.25
SHGCnorth-0.61	Ufixed –1.22
Uoper-1.27	SHGCall – 0.40
SHGCnorth-0.61	Ufixed –1.22
Uoper-1.27	SHGCall – NR
SHGCnorth-NR	
   40.1 – 50%	Ufixed –1.22
Uoper-1.27	SHGCall – 0.19
SHGCnorth-0.47	Ufixed –1.22
Uoper-1.27	SHGCall – 0.31
SHGCnorth-0.47	Ufixed –0.98
Uoper-1.02	SHGCall – NR
SHGCnorth-NR	
Skylight with curb, glass, 
% roof    							
   0 – 2.0%	Uall -1.98	SHGCall – 0.36	Uall -1.98	SHGCall – 0.19	Uall -1.98	SHGCall – NR	
   2.1 – 5.0%	Uall -1.98	SHGCall – 0.19	Uall -1.98	SHGCall – 0.19	Uall -1.98	SHGCall – NR	
Skylight with curb, plastic
% roof							
   0 – 2.0%	Uall -1.90	SHGCall – 0.39	Uall -1.90	SHGCall – 0.27	Uall -1.90	SHGCall – NR	
   2.1 – 5.0%	Uall -1.90	SHGCall – 0.34	Uall -1.90	SHGCall – 0.27	Uall -1.90	SHGCall – NR	
Skylight without curb, all, 
% roof							
   0 – 2.0%	Uall -1.36	SHGCall – 0.36	Uall -1.36	SHGCall – 0.19	Uall -1.36	SHGCall – NR	
   2.1 – 5.0%	Uall -1.36	SHGCall – 0.19	Uall -1.36	SHGCall – 0.19	Uall -1.36	SHGCall – NR	
1The following definitions apply:  ci=continuous insulation; NR=no (insulation) requirements.  2Exception to 402.1.C.1 applies for mass walls.

Form 400C-04 											Climate Zones, 7,8,9
Building Prescriptive Envelope Method							South
Opaque Elements	Nonresidential	Residential	Semiheated	
	Assembly Maximum	Insulation Min. R-value	Assembly Maximum	Insulation Min. R-Value	Assembly Maximum	Insulation Min.1 R-Value	
Roofs							
   Insulation all above deck	U-0.063	R-15.0 ci	U-0.063	R-15.0 ci	U-1.282	NR	
   Metal building	U-0.065	R-19.0	U-0.065	R-19	U-1.280	NR	
   Attic and Other	R-0.034	R-30.0	U-0.027	R-38.	U-0.614	NR	
Walls, Above grade							
   Mass	U-0.580	NR	U-0.1511	R-5.7 ci2	U-0.580	NR	
   Metal building	U-0.113	R-13.0	U-0.113	R-13.0	U-1.180	NR	
   Steel framed	U-0.124	R-13.0	U-0.124	R-13.0	U-0.352	NR	
   Wood framed and Other	U-0.089	R-13.0	U-0.089	R-13.0	U-0.292	NR	
Walls, Below Grade							
   Below grade wall	C-1.140	NR	C-1.140	NR	C-1.140	NR	
Floors							
   Mass	U-0.322	NR	U-0.322	NR	U-0.322	NR	
   Steel joist	U-0.350	NR	U-0.350	NR	U-0.350	NR	
   Wood framed and Other	U-0.282	NR	U-0.282	NR	U-0.282	NR	
Slab-On-Grade Floors							
   Unheated	F-0.730	NR	F-0.730	NR	F-0.730	NR	
   Heated	F-1.020	R-7.5 for 12 in.	F-1.020	R-7.5 for 12 in.	F-1.020	R-7.5 for 12 in.	
Opaque Doors							
   Swinging	U-0.700		U-0.700		U-0.700		
   Non-swinging	U-1.450		U-1.450		U-1.450		
Fenestration	Assembly Max. U
(Fixed/ Operable)	Assembly 
Max. SHGC 
(all orientations/ North-Oriented)	Assembly Max. U (Fixed/ Operable)	Assembly 
Max. SHGC 
(all orientations/ North-Oriented) 	Assembly Max. U (Fixed/ Operable)	Assembly 
Max. SHGC 
(all orientations/ North-Oriented)	
Vertical Glazing, % of wall							
   0 – 10%	Ufixed –1.22
Uoper-1.27	SHGCall – 0.25
SHGCnorth-0.61	Ufixed –1.22
Uoper-1.27	SHGCall – 0.25
SHGCnorth-0.61	Ufixed –1.22
Uoper-1.27	SHGCall – NR
SHGCnorth-NR	
   10.1 – 20%	Ufixed –1.22
Uoper-1.27	SHGCall – 0.25
SHGCnorth-0.61	Ufixed –1.22
Uoper-1.27	SHGCall – 0.25
SHGCnorth-0.61	Ufixed –1.22
Uoper-1.27	SHGCall – NR
SHGCnorth-NR	
   20.1 – 30%	Ufixed –1.22
Uoper-1.27	SHGCall – 0.25
SHGCnorth-0.61	Ufixed –1.22
Uoper-1.27	SHGCall – 0.25
SHGCnorth-0.61	Ufixed –1.22
Uoper-1.27	SHGCall – NR
SHGCnorth-NR	
   30.1 – 40%	Ufixed –1.22
Uoper-1.27	SHGCall – 0.25
SHGCnorth-0.44	Ufixed –1.22
Uoper-1.27	SHGCall – 0.25
SHGCnorth-0.44	Ufixed –1.22
Uoper-1.27	SHGCall – NR
SHGCnorth-NR	
   40.1 – 50%	Ufixed –1.22
Uoper-1.27	SHGCall – 0.19
SHGCnorth-0.33	Ufixed –1.22
Uoper-1.27	SHGCall – 0.19
SHGCnorth-0.33	Ufixed –0.98
Uoper-1.02	SHGCall – NR
SHGCnorth-NR	
Skylight with curb, glass, 
% roof    							
   0 – 2.0%	Uall -1.98	SHGCall – 0.36	Uall -1.98	SHGCall – 0.19	Uall -1.98	SHGCall – NR	
   2.1 – 5.0%	Uall -1.98	SHGCall – 0.19	Uall -1.98	SHGCall – 0.16	Uall -1.98	SHGCall – NR	
Skylight with curb, plastic, 
% roof							
   0 – 2.0%	Uall -1.90	SHGCall – 0.34	Uall -1.90	SHGCall – 0.27	Uall -1.90	SHGCall – NR	
   2.1 – 5.0%	Uall -1.90	SHGCall – 0.27	Uall -1.90	SHGCall – 0.27	Uall -1.90	SHGCall – NR	
Skylight without curb, all, 
% roof							
   0 – 2.0%	Uall -1.36	SHGCall – 0.36	Uall -1.36	SHGCall – 0.19	Uall -1.36	SHGCall – NR	
   2.1 – 5.0%	Uall -1.36	SHGCall – 0.19	Uall -1.36	SHGCall – 0.19	Uall -1.36	SHGCall – NR	
1The following definitions apply:  ci=continuous insulation; NR=no (insulation) requirements.  2 Exception to 402.1.C.1 applies for mass walls.

On Form 600A, all climate zones, make for the following changes:
Page 1
1)	They become FORM 600A-04 .
2)	Line 7 is amended to read as follows: 
     7.  Glass type1 and area:  (Label required. by 13-104.4.5 if not Default)	        Description	Area
	a.  U-factor:  (or Single or Double Pane DEFAULT)				7a. ___________   _________ sq.ft.
	b.  SHGC:  (or Clear or Tint DEFAULT)					7b. ___________   _________ sq.ft.
3)	Footnote 1 is added at the bottom of the page:
          1 Predominant glass type. For actual glass type and areas, see Summer & Winter Glass output on pages 2 & 4.

Page 2
4)	Change the Base Hot Water Multiplier on the bottom of the page as shown in the red circle for each climate zone.

Page 6
5)	On Table 6A-25, under Water Heaters, change Table 6-12 to 612.1.ABC.3.2.

On Form 600B, all climate zones, make the following changes:
Page 1
1)	Change Form title from 600B-01 to 04 on top left.

Page 2
1)	Change all Electric Resistance EF levels to 0.92 as shown in red circles. Change Gas & Oil minimum EF to 0.59.
2)	Just below Table 6B-1, change the Table name from 6-12 to 612.1.ABC.3.2
3)	Under Other Hot Water System Options, change the Electric resistance system EF to 0.92 and the natural gas EF to 0.59.
4)	On Table 6B-2, under Water Heaters, change Table 6-12 to 612.1.ABC.3.2.

On Form 600C, all climate zones, make the following changes:
Page 1
1)	Change Form title from 600C-01 to 04 on top left.
2)	To the two lines under the title box that start “Compliance with Method C of” add Sub- in from of Chapter 6. Also, take off the 01 dates after the Form numbers (this way we don’t have to fix them next time; in the red circles I showed them changed to 04)

Page 2
3)	In Table 6C-1, under Hot Water, change the EF for Electric Resistance to 0.92 and the EF for Gas to 0.59.
4)	On Table 6C-2, in the line that starts “Get certified”, change the Single clear SHGC to 0.75, double clear to 0.66 and single tint to 0.64.
5)	On Table 6C-3, under Water Heaters, change Table 6-12 to 612.1.ABC.3.2.

On Form 600D-01 (Desuperheater Heat Recovery Unit (HRU) Water Heater Efficiency Certification) change the date from 01 to 04.