TABLE 1015.1
EXIT ACCESS TRAVEL DISTANCEa

OCCUPANCY	WITHOUT SPRINKLER SYSTEM (feet)	WITH SPRINKLER SYSTEM (feet)	
A, E	200 150	250b 200b	
B	200 	300c 	
I-1	200 Not Permitted	250b 	
I-2	150 Not Permitted	200c 60c	
I-3	150 	200c 60c	
I-4, D	150	200c 	
M
	200 150

	250b   

	
R

	200 175

	250b  

	
S-1, F-1, F-2	200 	250b 	
S-2	300 	400b 	
H-1	Not Permitted 	75c 	
H-2, H-3, H-4, H-5	Not Permitted 	100c 	

For SI: 1 foot = 304.8 mm.
a. See the following sections for modifications to exit access travel distance requirements:
Section 402: For the distance limitation in malls.  
Section 404: For the distance limitation through an atrium space.
Section 1015.2: For increased limitation in Groups F-1 and S-1.
Section 1024.7: For increased limitation in assembly seating.
Section 1024.7: For increased limitation for assembly open-air seating.
Section 1018.2: For buildings with one exit.
Chapter 31: For the limitation in temporary structures.
b. Buildings equipped throughout with an automatic sprinkler system in accordance
with Section 903.3.1.1 or 903.3.1.2. See Section 903 for occupancies
where sprinkler systems according to Section 903.3.1.2 are permitted.
c. Buildings equipped throughout with an automatic sprinkler system in accordance
with Section 903.3.1.1.