## A
RESULTS5-2.XLS
This spreadsheet contains the IEA 12B/21C participant results which are
presented in the informational appendix containing example results.
This data is provided for the convenience of users who wish to plot
or tabulate their results along with the example results.
This speadsheet was originally created with Lotus 1-2-3 version 3.1 for DOS.
The spreadsheet contains only values and text (no formulas).
Various data can be found at the following addresses:
A61..L138 |  | Annual Loads (heating and sensible cooling)
A142..L180 |  | Annual Hourly Integrated Peak Heating Loads
A195..L233 |  | Annual Hourly Integrated Peak Sensible Cooling Loads
A249..L276 |  | Annual Free Float Temperature Output
A286..J335 |  | Various annual incident and annual transmitted solar
radiation outputs
A341..J901 |  | Various hourly incident solar, temperature, and load
output including temperature and bin frequency output
(this output was plotted in the example results appendix
but not presented in table format)
Q61..AB131 |  | Low Mass and High Mass Basic Sensitivity Tests
Q138..AB206 |  | In-Depth Sensitivity Tests, Cases 195 through 320
Q210..AB246 |  | In-Depth Sensitivity Tests, Cases 395 through 440
Q248..AB290 |  | High Mass Basic and In-Depth Sensitivity Tests
Q293..Z316 |  | Annual transmissivity and shading coefficients of windows
Q322..AT360 |  | Annual Hourly Integrated Peak Heating Loads
(including dates and hours)
Q375..AT413 |  | Annual Hourly Integrated Peak Sensible Cooling Loads
(including dates and hours)
Q429..AT456 |  | Annual Free Float Temperature Output
(including dates and hours)
A blank column with the header "YOUR DATA" has been provided with each
category of results. For data categories beginning in Column A, "YOUR
DATA" should be added to column J. For data categories beginning in
Column Q, "YOUR DATA" should be added to Column Z for Rows 65 to 316,
and to Columns AP through AR for Rows 326 to 456. This should
facilitate developing graphs and tables of your results which also
include the example results and/or ranges.
The Standard Output Report spreadsheet (Sec5-2out.XLS) has been designed
such that values input to Column B of Sec5-2out.XLS can be directly transferred to
Column J of this spreadsheet.
ANNUAL HEATING LOADS | [12 empty] | LOW MASS BASIC SENSITIVITY TESTS
| ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | ACCEPTANCE RANGE |  |  | ANNUAL HEATING [MWH]
| UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | MAX | MIN | Test |  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | ACCEPTANCE RANGE
CASE | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh | Result | CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | Max | Min | Result
600 | 4.296 | 4.773 | 5.709 | 5.226 | 5.596 | 4.882 | 4.872 | 5.362 | 4.994 | 5.7797 | 4.2253 | PASS | 610-600 | 0.059 | 0.033 | 0.077 | 0.054 | 0.024 | 0.089 | 0.098 | 0.021 | 0.048 | 0.10185 | 0.019801 | PASS
610 | 4.355 | 4.806 | 5.786 | 5.28 | 5.62 | 4.971 | 4.97 | 5.383 | 5.042 | 5.8576 | 4.2835 | PASS | 620-600 | 0.317 | 0.276 | 0.235 | 0.328 | 0.138 | 0.682 | 0.201 | 0.366 | 0.15 | 0.7092 | 0.1108 | PASS
620 | 4.613 | 5.049 | 5.944 | 5.554 | 5.734 | 5.564 | 5.073 | 5.728 | 5.144 | 6.0106 | 4.5465 | PASS | 630-620 | 0.437 | 0.31 | 0.525 | 0.329 | 0.267 | 0.531 | 0.551 |  | 0.364 | 0.56236 | 0.2528 | PASS
630 | 5.05 | 5.359 | 6.469 | 5.883 | 6.001 | 6.095 | 5.624 |  | 5.508 | 6.5457 | 4.8593 | PASS | 640-600 | -1.545 | -1.885 | -2.166 | -1.971 | -1.793 | -1.817 | -1.829 | -2.053 | -1.999 | -1.5139 | -2.1971 | PASS
640 | 2.751 | 2.888 | 3.543 | 3.255 | 3.803 | 3.065 | 3.043 | 3.309 | 2.995 | 3.8556 | 2.6984 | PASS | ANNUAL COOLING [MWH]
650 | 0 | 0 | 0 | 0 | 0 | 0 | 4.171e-06 | 0 | 0 |  |  | N/A |  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | ACCEPTANCE RANGE
900 | 1.17 | 1.61 | 1.872 | 1.897 | 1.988 | 1.73 | 1.655 | 2.041 | 1.301 | 2.0594 | 1.1264 | PASS | CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | Max | Min | Result
910 | 1.575 | 1.862 | 2.254 | 2.174 | 2.282 | 2.063 | 2.097 | 2.22 | 1.559 | 2.3218 | 1.4463 | PASS | 610-600 | -2.222 | -1.582 | -2.227 | -1.83 | -2.186 | -1.728 | -1.891 | -1.272 | -2.18 | -1.2242 | -2.272 | PASS
920 | 3.313 | 3.752 | 4.255 | 4.093 | 4.058 | 4.235 | 3.776 | 4.3 | 3.312 | 4.356 | 3.1246 | PASS | 620-600 | -2.72 | -2.341 | -2.745 | -2.645 | -2.96 | -2.481 | -2.591 | -2.427 | -2.798 | -2.3101 | -2.991 | PASS
930 | 4.143 | 4.347 | 5.335 | 4.755 | 4.728 | 5.168 | 4.74 |  | 4.249 | 5.4077 | 3.8077 | PASS | 630-620 | -1.288 | -0.984 | -1.845 | -1.14 | -1.303 | -1.522 | -1.485 |  | -2.021 | -0.94095 | -1.888 | FAIL
940 | 0.793 | 1.021 | 1.239 | 1.231 | 1.411 | 1.179 | 1.08 | 1.323 | 0.838 | 1.4419 | 0.7621 | PASS | 640-600 | -0.185 | -0.25 | -0.32 | -0.252 | -0.153 | -0.245 | -0.246 | -0.27 | -0.341 | -0.14465 | -0.32835 | FAIL
950 | 0 | 0 | 0 | 0 | 0 | 0 | 7.801e-06 | 0 | 0 |  |  | N/A | 650-600 | -1.321 | -1.293 | -1.284 | -1.384 | -1.419 | -1.404 | -1.373 | -1.322 | -1.376 | -1.2779 | -1.5467 | PASS
960 | 2.311 | 2.664 | 2.928 | 2.884 | 2.851 | 2.943 | 3.373 | 2.816 | 2.216 | 3.4276 | 2.2273 | FAIL | PEAK HEATING [KW]
195 | 4.167 | [7 empty] | 5.536 | 4.1896 | 4.1659 | FAIL |  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | ACCEPTANCE RANGE
200 | 5.252 | [8 empty] | 5.2795 | 5.2507 | No data | CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | Max | Min | Result
210 | 6.456 | 6.559 |  |  |  |  | 6.554 | 6.967 |  | 6.9925 | 6.4304 | No data | 610-600 | 0 | 0.001 | -0.011 | 0 |  | 0 | -0.0083333 | 0 | -0.012 | 0.0016973 | -0.013644 | PASS
215 | 5.547 | [8 empty] | 5.5964 | 5.5446 | No data | 620-600 | 0.154 | 0.001 | 0.001 | 0.019 |  | 0.24 | -0.0083333 | 0.025 | 0.018 | 0.25242 | -0.02075 | PASS
220 | 6.944 | 7.215 | 8.787 | 8.102 | 8.127 | 7.422 | 7.297 | 7.437 | 7.717 | 8.8792 | 6.897 | PASS | 630-620 | 0.001 | 0 | -0.021 | 0.003 |  | 0.001 | 0 |  | -0.023 | 0.0044341 | -0.027116 | PASS
230 | 10.376 | 10.74 | 12.243 | 11.633 | 11.649 | 11.037 | 10.84 | 10.964 | 11.128 | 12.3364 | 10.2826 | PASS | 640-600 | 1.795 | 1.546 | 1.898 | 2.272 |  | 2.31 | 1.7917 | 2.6 | 1.889 | 3.5697 | 1.4496 | PASS
240 | 5.649 | 6.009 | 7.448 | 6.769 | 6.786 | 6.194 | 6.076 | 6.234 | 6.436 | 7.538 | 5.5591 | PASS | PEAK COOLING [KW]
250 | 4.751 | 5.739 | 7.024 | 6.608 | 6.653 | 5.974 | 5.764 | 5.738 | 5.817 | 7.1377 | 4.6374 | PASS |  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | ACCEPTANCE RANGE
270 | 4.51 | 4.93 |  | 5.341 | 5.92 |  | 5.047 | 5.489 |  | 5.9905 | 4.4395 | No data | CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | Max | Min | Result
280 | 4.675 | 5.125 |  | 5.937 | 6.148 |  | 5.279 | 5.841 |  | 6.2217 | 4.6013 | No data | 610-600 | -0.525 | -0.141 | -0.592 | -0.456 |  | -0.116 | -0.81111 | -0.666 | -0.483 | -0.081244 | -0.84587 | PASS
290 | 4.577 | 4.959 |  | 5.406 | 5.942 |  | 5.132 | 5.509 |  | 6.0103 | 4.5087 | No data | 620-600 | -2.56 | -1.89 | -2.226 | -2.234 |  | -1.989 | -2.2111 | -1.716 | -2.286 | -1.6699 | -2.6849 | PASS
300 | 4.761 | 5.077 |  | 5.587 | 5.964 |  | 5.124 | 5.786 |  | 6.0278 | 4.6244 | No data | 630-620 | -0.562 | -0.371 | -0.842 | -0.477 |  | -0.632 | -0.66667 |  | -0.845 | -0.36339 | -0.86555 | PASS
310 | 5.221 | 5.327 |  | 5.85 | 6.165 |  | 5.61 |  |  | 6.2257 | 4.8906 | No data | 640-600 | -0.033 | -0.073 | -0.08 | -0.051 |  | -0.036 | -0.044444 | -0.041 | -0.062 | -0.03065 | -0.08235 | PASS
320 | 3.859 | 4.209 |  | 4.627 | 5.141 |  | 4.348 | 4.84 |  | 5.1413 | 3.7949 | No data | 650-600 | -0.163 | -0.134 | -0.14 | -0.156 |  | -0.143 | -0.10833 | -0.133 | -0.122 | -0.10746 | -0.2211 | PASS
395 | 4.984 | 4.799 | 5.835 | 5.199 | 5.201 | 4.967 | 4.855 | 4.839 | 5.472 | 5.8868 | 4.7472 | PASS
400 | 6.9 | 7.075 | 8.77 | 7.966 | 7.973 | 7.287 | 7.166 | 7.326 | 7.659 | 8.8635 | 6.8065 | PASS | HIGH MASS BASIC SENSITIVITY TESTS
410 | 8.596 | 8.873 | 10.506 | 9.726 | 9.734 | 9.019 | 8.936 | 9.085 | 9.38 | 10.6015 | 8.5562 | PASS | ANNUAL HEATING [MWH]
420 | 7.298 | 7.61 | 9.151 | 8.365 | 8.373 | 7.774 | 7.697 | 7.863 | 8.074 | 9.2437 | 7.2053 | PASS |  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | ACCEPTANCE RANGE
430 | 5.429 | 6.488 | 7.827 | 7.178 | 7.186 | 6.662 | 6.5 | 6.51 | 6.309 | 7.9469 | 5.3091 | PASS | CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | Max | Min | Result
440 | 4.449 | 4.987 |  | 5.652 | 5.811 |  | 5.098 | 5.642 |  | 5.8791 | 4.3809 | No data | 900-600 | -3.126 | -3.163 | -3.837 | -3.329 | -3.608 | -3.152 | -3.217 | -3.321 | -3.693 | -3.0905 | -3.8726 | PASS
800 | 4.868 | 5.953 | 7.228 | 6.611 | 6.6 | 6.161 | 5.94 | 5.861 | 5.353 | 7.3561 | 4.5371 | PASS | 910-900 | 0.405 | 0.252 | 0.382 | 0.277 | 0.294 | 0.333 | 0.442 | 0.179 | 0.258 | 0.45515 | 0.16585 | PASS
810 | 1.839 | 2.446 |  | 3.004 | 2.828 |  | 2.567 | 2.962 |  | 3.0622 | 1.8007 | No data | 920-900 | 2.143 | 2.142 | 2.383 | 2.196 | 2.07 | 2.505 | 2.121 | 2.259 | 2.011 | 2.5322 | 1.9334 | PASS
ANNUAL COOLING [MWH] | [12 empty] | 930-920 | 0.83 | 0.595 | 1.08 | 0.662 | 0.67 | 0.933 | 0.964 |  | 0.937 | 1.1042 | 0.57422 | PASS
| ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | ACCEPTANCE RANGE |  |  | 940-900 | -0.377 | -0.589 | -0.633 | -0.666 | -0.577 | -0.551 | -0.575 | -0.718 | -0.463 | -0.35995 | -0.73505 | PASS
| UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | MAX | MIN | Test | 960-900 | 1.141 | 1.054 | 1.056 | 0.987 | 0.863 | 1.213 | 1.718 | 0.775 | 0.915 | 1.7651 | 0.72785 | PASS
CASE# | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh | Result | ANNUAL COOLING [MWH]
600 | 6.137 | 6.433 | 7.079 | 7.278 | 7.964 | 6.492 | 6.492 | 6.778 | 8.054 | 8.0554 | 6.0457 | PASS |  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | ACCEPTANCE RANGE
610 | 3.915 | 4.851 | 4.852 | 5.448 | 5.778 | 4.764 | 4.601 | 5.506 | 5.874 | 5.8712 | 3.8219 | FAIL | CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | Max | Min | Result
620 | 3.417 | 4.092 | 4.334 | 4.633 | 5.004 | 4.011 | 3.901 | 4.351 | 5.256 | 5.0834 | 3.3377 | FAIL | 900-600 | -4.005 | -3.833 | -4.624 | -4.113 | -4.549 | -3.92 | -4.007 | -4.179 | -4.664 | -3.7935 | -4.6635 | FAIL
630 | 2.129 | 3.108 | 2.489 | 3.493 | 3.701 | 2.489 | 2.416 |  | 3.235 | 3.7796 | 2.1111 | PASS | 910-900 | -1.311 | -1.067 | -1.479 | -1.293 | -1.561 | -1.144 | -1.159 | -0.832 | -1.652 | -0.79555 | -1.5975 | FAIL
640 | 5.952 | 6.183 | 6.759 | 7.026 | 7.811 | 6.247 | 6.246 | 6.508 | 7.713 | 7.904 | 5.9406 | PASS | 920-900 | -0.292 | 0.016 | -0.015 | -0.222 | -0.323 | -0.115 | -0.067 | 0.014 | -0.221 | 0.03295 | -0.33995 | PASS
650 | 4.816 | 5.14 | 5.795 | 5.894 | 6.545 | 5.088 | 5.119 | 5.456 | 6.678 | 6.6315 | 4.7295 | FAIL | 930-920 | -0.801 | -0.682 | -1.174 | -0.77 | -0.854 | -1.018 | -1.002 |  | -1.346 | -0.6574 | -1.1986 | FAIL
900 | 2.132 | 2.6 | 2.455 | 3.165 | 3.415 | 2.572 | 2.485 | 2.599 | 3.39 | 3.4792 | 2.0679 | PASS | 940-900 | -0.053 | -0.064 | -0.115 | -0.129 | -0.174 | -0.083 | -0.102 | -0.083 | -0.118 | -0.04695 | -0.18005 | PASS
910 | 0.821 | 1.533 | 0.976 | 1.872 | 1.854 | 1.428 | 1.326 | 1.767 | 1.738 | 1.8747 | 0.76845 | PASS | 950-900 | -1.745 | -2.074 | -1.917 | -2.244 | -2.826 | -2.021 | -1.9244 | -1.828 | -2.641 | -1.6984 | -2.88 | PASS
920 | 1.84 | 2.616 | 2.44 | 2.943 | 3.092 | 2.457 | 2.418 | 2.613 | 3.169 | 3.1546 | 1.7774 | FAIL | 960-900 | -1.644 | -1.934 | -2.027 | -2.362 | -2.697 | -1.929 | -2.0737 | -1.813 | -2.535 | -1.5913 | -2.7497 | PASS
930 | 1.039 | 1.934 | 1.266 | 2.173 | 2.238 | 1.439 | 1.416 |  | 1.823 | 2.298 | 0.97905 | PASS | PEAK HEATING [KW]
940 | 2.079 | 2.536 | 2.34 | 3.036 | 3.241 | 2.489 | 2.383 | 2.516 | 3.272 | 3.2991 | 2.0209 | PASS |  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | ACCEPTANCE RANGE
950 | 0.387 | 0.526 | 0.538 | 0.921 | 0.589 | 0.551 | 0.5606 | 0.771 | 0.749 | 0.9477 | 0.3603 | PASS | CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | Max | Min | Result
960 | 0.488 | 0.666 | 0.428 | 0.803 | 0.718 | 0.643 | 0.4113 | 0.786 | 0.855 | 0.81155 | 0.39171 | FAIL | 900-600 | -0.587 | -0.487 | -0.488 | -0.498 |  | -0.429 | -0.41389 | -0.557 | -0.519 | -0.40466 | -0.60772 | PASS
195 | 0.414 | [7 empty] | 0.353 | 0.48124 | 0.4108 | FAIL | 910-900 | 0.008 | 0.003 | 0.007 | 0.004 |  | 0.01 | 0.019444 | 0.004 | 0.0080001 | 0.020512 | -0.0029701 | PASS
200 | 0.57 | [8 empty] | 0.6702 | 0.56523 | No data | 920-900 | 0.458 | 0.25 | 0.248 | 0.253 |  | 0.421 | 0.19167 | 0.264 | 0.26 | 0.47132 | 0.17835 | PASS
210 | 0.162 | 0.613 |  |  |  |  | 0.6679 | 0.641 |  | 0.69319 | 0.1367 | No data | 930-920 | 0.047 | 0.029 | 0.027 | 0.029 |  | 0.035 | 0.036111 |  | 0.028 | 0.048322 | 0.019243 | PASS
215 | 0.639 | [8 empty] | 0.72277 | 0.63501 | No data | 940-900 | 1.13 | 1.575 | 2.108 | 2.356 |  | 2.509 | 1.6056 | 2.631 | 2.074 | 2.706 | 1.0549 | PASS
220 | 0.186 | 0.701 | 0.399 | 0.827 | 0.835 | 0.734 | 0.7368 | 0.683 | 0.558 | 0.86745 | 0.15355 | PASS | 960-900 | -0.44 | -0.702 | -0.83 | -0.897 |  | -0.756 | -0.99467 | -1.018 | -0.645 | -0.4111 | -1.0453 | PASS
230 | 0.454 | 0.976 | 0.692 | 1.131 | 1.139 | 1.02 | 1.04 | 0.985 | 0.861 | 1.1732 | 0.41975 | PASS | PEAK COOLING [KW]
240 | 0.415 | 1.072 | 0.66 | 1.239 | 1.246 | 1.108 | 1.114 | 1.045 | 0.878 | 1.2875 | 0.37345 | PASS |  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | ACCEPTANCE RANGE
250 | 3.213 | 2.545 | 2.177 | 2.924 | 2.931 | 2.486 | 2.684 | 3.38 | 4.284 | 3.7383 | 2.1027 | FAIL | CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | Max | Min | Result
270 | 7.528 | 8.67 |  | 9.828 | 10.35 |  | 8.764 | 8.714 |  | 10.4911 | 7.3869 | No data | 900-600 | -3.306 | -2.81 | -3.198 | -2.956 |  | -2.952 | -2.9194 | -3.355 | -3.187 | -2.7822 | -3.3948 | PASS
280 | 4.873 | 5.895 |  | 6.511 | 7.114 |  | 5.761 | 6.257 |  | 7.226 | 4.761 | No data | 910-900 | -0.992 | -0.655 | -1.122 | -0.594 |  | -0.548 | -0.775 | -0.31 | -1.075 | -0.2694 | -1.1626 | PASS
290 | 5.204 | 7.011 |  | 7.871 | 8.089 |  | 6.699 | 7.431 |  | 8.2332 | 5.0598 | No data | 920-900 | -0.503 | -0.222 | -0.349 | -0.384 |  | -0.263 | -0.51667 | 0.048 | -0.436 | 0.076233 | -0.5449 | PASS
300 | 4.302 | 5.836 |  | 6.665 | 7.1 |  | 5.721 | 5.781 |  | 7.1927 | 4.1621 | No data | 930-920 | -0.512 | -0.387 | -0.721 | -0.407 |  | -0.585 | -0.55167 |  | -0.704 | -0.3703 | -0.7377 | PASS
310 | 2.732 | 4.57 |  | 5.245 | 5.471 |  | 3.727 |  |  | 5.608 | 2.5951 | No data | 940-900 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
320 | 5.061 | 5.906 |  | 6.725 | 7.304 |  | 5.956 | 5.663 |  | 7.4162 | 4.9575 | No data | 950-900 | -0.855 | -0.534 | -0.794 | -0.701 |  | -0.657 | -0.88056 | -0.59 | -0.861 | -0.51667 | -0.89788 | PASS
395 | 0 | 0.011 | 0 | 0.016 | 0.014 | 0.01 | 0.01029 | 0.011 | 0.001 | 0.0168 | -0.0008 | PASS | 960-900 | -1.935 | -2.011 | -2.401 | -2.501 |  | -2.155 | -2.1887 | -2.054 | -2.37 | -1.9067 | -2.5293 | PASS
400 | 0 | 0.04 | 0.002 | 0.061 | 0.058 | 0.042 | 0.04468 | 0.044 | 0.016 | 0.06405 | -0.00305 | PASS
410 | 0 | 0.059 | 0.01 | 0.084 | 0.084 | 0.063 | 0.06707 | 0.065 | 0.035 | 0.0882 | -0.0042 | PASS
420 | 0.011 | 0.147 | 0.051 | 0.189 | 0.188 | 0.154 | 0.1575 | 0.143 | 0.105 | 0.1979 | 0.0021 | PASS
430 | 0.542 | 0.617 | 0.422 | 0.704 | 0.684 | 0.563 | 0.6174 | 0.875 | 1.106 | 0.89765 | 0.39935 | FAIL
440 | 3.967 | 4.172 |  | 4.674 | 5.204 |  | 3.975 | 4.684 |  | 5.4492 | 0.054044 | No data
800 | 0.113 | 0.224 | 0.055 | 0.272 | 0.222 | 0.195 | 0.2073 | 0.325 | 0.323 | 4.7771 | -0.16986 | PASS
810 | 1.052 | 1.405 |  | 1.711 | 1.708 |  | 1.191 | 1.624 |  | 1.744 | 1.0377 | No data | LOW MASS IN-DEPTH (CASES 195 THRU 320) SENSITIVITY TESTS
ANNUAL HEATING [MWH]
[14 empty] | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | ACCEPTANCE RANGE
[13 empty] | CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | Max | Min | Result
ANNUAL HOURLY INTEGRATED PEAK HEATING LOADS | [12 empty] | 200-195 | 1.085
CODENAME: | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | ACCEPTANCE RANGE |  |  | 210-200 | 1.204
COUNTRY: | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | MAX | MIN | Test | 220-215 | 1.397
CASE# | KW | KW | KW | KW | KW | KW | KW | KW | KW | kW | kW | Result | 215-200 | 0.295
600 | 3.437 | 3.94 | 4.045 | 4.258 |  | 4.037 | 3.9306 | 4.354 | 3.767 | 4.3998 | 3.3911 | PASS | 220-210 | 0.488 | 0.656 |  |  |  |  | 0.743 | 0.47 |  | 0.75665 | 0.45635 | No data
610 | 3.437 | 3.941 | 4.034 | 4.258 |  | 4.037 | 3.9222 | 4.354 | 3.755 | 4.3998 | 3.3911 | PASS | 230-220 | 3.432 | 3.525 | 3.456 | 3.531 | 3.522 | 3.615 | 3.543 | 3.527 | 3.411 | 3.8062 | 3.4257 | FAIL
620 | 3.591 | 3.941 | 4.046 | 4.277 |  | 4.277 | 3.9222 | 4.379 | 3.785 | 4.385 | 3.5516 | PASS | 240-220 | -1.295 | -1.206 | -1.339 | -1.333 | -1.341 | -1.228 | -1.221 | -1.203 | -1.281 | -1.1996 | -1.3479 | PASS
630 | 3.592 | 3.941 | 4.025 | 4.28 |  | 4.278 | 3.9222 |  | 3.762 | 4.3144 | 3.5576 | PASS | 250-220 | -2.193 | -1.476 | -1.763 | -1.494 | -1.474 | -1.448 | -1.533 | -1.699 | -1.9 | -1.4108 | -2.2302 | PASS
640 | 5.232 | 5.486 | 5.943 | 6.53 |  | 6.347 | 5.7222 | 6.954 | 5.656 | 7.411 | 5.1282 | PASS | 270-220 | -2.434 | -2.285 |  | -2.761 | -2.207 |  | -2.25 | -1.948 |  | -1.9073 | -2.8017 | No data
650 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 280-270 | 0.165 | 0.195 |  | 0.596 | 0.228 |  | 0.232 | 0.352 |  | 0.61755 | 0.14345 | No data
900 | 2.85 | 3.453 | 3.557 | 3.76 |  | 3.608 | 3.5167 | 3.797 | 3.248 | 3.8444 | 2.8026 | PASS | 320-270 | -0.651 | -0.721 |  | -0.714 | -0.779 |  | -0.699 | -0.649 |  | -0.6425 | -0.77929 | No data
910 | 2.858 | 3.456 | 3.564 | 3.764 |  | 3.618 | 3.5361 | 3.801 | 3.256 | 3.8482 | 2.8108 | PASS | 290-270 | 0.067 | 0.029 |  | 0.065 | 0.022 |  | 0.085 | 0.02 |  | 0.08825 | 0.01675 | No data
920 | 3.308 | 3.703 | 3.805 | 4.013 |  | 4.029 | 3.7083 | 4.061 | 3.508 | 4.0986 | 3.2703 | PASS | 300-270 | 0.251 | 0.147 |  | 0.246 | 0.044 |  | 0.077 | 0.297 |  | 0.30965 | 0.03135 | No data
930 | 3.355 | 3.732 | 3.832 | 4.042 |  | 4.064 | 3.7444 |  | 3.536 | 4.0995 | 3.3196 | PASS | 310-300 | 0.46 | 0.25 |  | 0.263 | 0.201 |  | 0.486 |  |  | 0.50025 | 0.18675 | No data
940 | 3.98 | 5.028 | 5.665 | 6.116 |  | 6.117 | 5.1222 | 6.428 | 5.322 | 6.5504 | 3.8576 | PASS | ANNUAL COOLING [MWH]
950 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | N/A |  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | ACCEPTANCE RANGE
960 | 2.41 | 2.751 | 2.727 | 2.863 |  | 2.852 | 2.522 | 2.779 | 2.603 | 2.8856 | 2.3874 | PASS | CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | Max | Min | Result
195 | 2.004 | [7 empty] | 2.294 | 2.0575 | 2.0015 | FAIL | 200-195 | 0.156
200 | 2.651 | [8 empty] | 2.7701 | 2.6453 | No data | 210-200 | -0.408
210 | 2.701 | 2.973 |  |  |  |  | 2.9806 | 3.325 |  | 3.3562 | 2.6698 | No data | 220-215 | -0.453
215 | 2.787 | [8 empty] | 2.9409 | 2.7797 | No data | 215-200 | 0.069
220 | 2.867 | 3.28 | 3.465 | 3.695 |  | 3.348 | 3.3361 | 3.52 | 3.245 | 3.7364 | 2.8256 | PASS | 220-210 | 0.024 | 0.088 |  |  |  |  | 0.0689 | 0.042 |  | 0.0912 | 0.0208 | No data
230 | 4.386 | 4.984 | 4.994 | 5.279 |  | 5.159 | 4.8917 | 5.107 | 4.743 | 5.3236 | 4.3414 | PASS | 230-220 | 0.268 | 0.275 | 0.293 | 0.304 | 0.304 | 0.286 | 0.3032 | 0.302 | 0.303 | 0.3058 | 0.2662 | PASS
240 | 2.685 | 3.1 | 3.282 | 3.495 |  | 3.159 | 3.1528 | 3.333 | 3.062 | 3.5355 | 2.6445 | PASS | 240-220 | 0.229 | 0.371 | 0.261 | 0.412 | 0.411 | 0.374 | 0.3772 | 0.362 | 0.32 | 0.42115 | 0.21985 | PASS
250 | 2.866 | 3.279 | 3.465 | 3.695 |  | 3.341 | 3.3361 | 3.525 | 3.245 | 3.7364 | 2.8245 | PASS | 250-220 | 3.027 | 1.844 | 1.778 | 2.097 | 2.096 | 1.752 | 1.9472 | 2.697 | 3.726 | 3.3582 | 1.6755 | FAIL
270 | 2.863 | 3.277 |  | 3.661 |  |  | 3.3361 | 3.738 |  | 3.7817 | 2.8193 | No data | 270-220 | 7.342 | 7.969 |  | 9.001 | 9.515 |  | 8.0272 | 8.031 |  | 9.6236 | 7.2333 | No data
280 | 2.864 | 3.278 |  | 3.685 |  |  | 3.3361 | 3.759 |  | 3.8038 | 2.8193 | No data | 280-270 | -2.655 | -2.775 |  | -3.317 | -3.236 |  | -3.003 | -2.457 |  | -2.4502 | -3.36 | No data
290 | 2.863 | 3.277 |  | 3.661 |  |  | 3.3278 | 3.738 |  | 3.7817 | 2.8193 | No data | 320-270 | -2.467 | -2.764 |  | -3.103 | -3.046 |  | -2.808 | -3.051 |  | -2.4352 | -3.1348 | No data
300 | 3.014 | 3.276 |  | 3.681 |  |  | 3.3278 | 3.77 |  | 3.8078 | 2.9762 | No data | 290-270 | -2.324 | -1.659 |  | -1.957 | -2.261 |  | -2.065 | -1.283 |  | -1.2309 | -2.376 | No data
310 | 3.015 | 3.277 |  | 3.669 |  |  | 3.3278 |  |  | 3.7017 | 2.9823 | No data | 300-270 | -3.226 | -2.834 |  | -3.163 | -3.25 |  | -3.043 | -2.933 |  | -2.8132 | -3.2708 | No data
320 | 2.861 | 3.275 |  | 3.651 |  |  | 3.3361 | 3.735 |  | 3.7787 | 2.8173 | No data | 310-300 | -1.57 | -1.266 |  | -1.42 | -1.629 |  | -1.994 |  |  | -1.2296 | -2.0304 | No data
395 | 2.062 | 2.209 | 2.328 | 2.385 |  | 2.263 | 2.2211 | 2.27 | 2.301 | 2.4011 | 2.0459 | PASS | PEAK HEATING [KW]
400 | 2.867 | 3.28 | 3.476 | 3.695 |  | 3.342 | 3.3361 | 3.52 | 3.255 | 3.7364 | 2.8256 | PASS |  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | ACCEPTANCE RANGE
410 | 3.625 | 4.124 | 4.233 | 4.487 |  | 4.227 | 4.1139 | 4.314 | 4.002 | 4.5301 | 3.5819 | PASS | CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | Max | Min | Result
420 | 3.443 | 3.944 | 4.05 | 4.287 |  | 4.044 | 3.9306 | 4.126 | 3.819 | 4.2954 | 3.4008 | PASS | 200-195 | 0.647
430 | 3.442 | 3.944 | 4.05 | 4.287 |  | 4.044 | 3.9306 | 4.137 | 3.819 | 4.2984 | 3.3997 | PASS | 210-200 | 0.05
440 | 3.439 | 3.942 |  | 4.277 |  |  | 3.9306 | 4.376 |  | 4.4229 | 3.3921 | No data | 220-215 | 0.08
800 | 3.227 | 3.793 | 3.909 | 4.138 |  | 3.902 | 3.7861 | 3.939 | 3.634 | 4.1637 | 3.1814 | PASS | 215-200 | 0.136
810 | 2.979 | 3.566 |  | 3.915 |  |  | 3.6056 | 3.963 |  | 4.0122 | 2.9298 | No data | 220-210 | 0.166 | 0.307 |  |  |  |  | 0.35556 | 0.195 |  | 1.9145 | 0.082739 | No data
[13 empty] | 230-220 | 1.519 | 1.704 | 1.529 | 1.584 |  | 1.811 | 1.5556 | 1.587 | 1.498 | 1.9107 | -0.28365 | PASS
[13 empty] | 240-220 | -0.182 | -0.18 | -0.183 | -0.2 |  | -0.189 | -0.18333 | -0.187 | -0.183 | -0.179 | -0.201 | PASS
[13 empty] | 250-220 | -0.001 | -0.001 | 0 | 0 |  | -0.007 | 0 | 0.005 | 0 | 0.0056 | -0.0076 | PASS
[13 empty] | 270-220 | -0.004 | -0.003 |  | -0.034 |  |  | 0 | 0.218 |  | 0.2306 | -0.0466 | No data
[13 empty] | 280-270 | 0.001 | 0.001 |  | 0.024 |  |  | 0 | 0.021 |  | 0.0252 | -0.0012 | No data
[13 empty] | 320-270 | -0.002 | -0.002 |  | -0.01 |  |  | 0 | -0.003 |  | 0.0005 | -0.0105 | No data
[13 empty] | 290-270 | 0 | 0 |  | 0 |  |  | -0.0083333 | 0 |  |  |  | N/A
[13 empty] | 300-270 | 0.151 | -0.001 |  | 0.02 |  |  | -0.0083333 | 0.032 |  | 0.15897 | -0.0163 | No data
[13 empty] | 310-300 | 0.001 | 0.001 |  | -0.012 |  |  | 0 |  |  | 0.0023396 | -0.027131 | No data
PEAK COOLING [KW]
[14 empty] | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | ACCEPTANCE RANGE
[13 empty] | CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | Max | Min | Result
[13 empty] | 200-195 | 0.212 | [8 empty] | 0.24585 | 0.21039 | No data
[13 empty] | 210-200 | -0.387 | [8 empty] | -0.22696 | -0.39462 | No data
ANNUAL HOURLY INTEGRATED PEAK COOLING LOADS | [12 empty] | 220-215 | -0.447 | [8 empty] | -0.22355 | -0.45764 | No data
CODENAME: | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | ACCEPTANCE RANGE |  |  | 215-200 | 0.144 | [8 empty] | 0.14666 | 0.08805 | No data
COUNTRY: | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | MAX | MIN | Test | 220-210 | 0.084 | 0.149 |  |  |  |  | 0.11111 | 0.071 |  | 0.1529 | 0.0671 | No data
CASE# | kW | kW | kW | kW | kW | kW | kW | kW | KW | kW | kW | Result | 230-220 | 0.499 | 0.48 | 0.518 | 0.535 |  | 0.485 | 0.52889 | 0.536 | 0.513 | 0.5388 | 0.4772 | PASS
600 | 6.194 | 5.965 | 6.656 | 6.827 |  | 6.286 | 6.4861 | 6.812 | 6.965 | 6.8701 | 5.9219 | FAIL | 240-220 | 0.179 | 0.181 | 0.182 | 0.2 |  | 0.183 | 0.1825 | 0.184 | 0.182 | 0.20105 | 0.17795 | PASS
610 | 5.669 | 5.824 | 6.064 | 6.371 |  | 6.17 | 5.675 | 6.146 | 6.482 | 6.3918 | 5.6655 | FAIL | 250-220 | 2.8 | 1.87 | 1.668 | 1.25 |  | 1.043 | 2.0489 | 3.699 | 2.141 | 3.8318 | 0.92752 | PASS
620 | 3.634 | 4.075 | 4.43 | 4.593 |  | 4.297 | 4.275 | 5.096 | 4.679 | 5.1691 | 3.5609 | PASS | 270-220 | 5.796 | 5.475 |  | 5.894 |  |  | 5.585 | 5.654 |  | 6.0644 | 5.4469 | No data
630 | 3.072 | 3.704 | 3.588 | 4.116 |  | 3.665 | 3.6083 |  | 3.834 | 4.1682 | 3.0198 | PASS | 280-270 | -1.912 | -2.01 |  | -2.014 |  |  | -1.9778 | -1.631 |  | -1.6054 | -2.1682 | No data
640 | 6.161 | 5.892 | 6.576 | 6.776 |  | 6.25 | 6.4417 | 6.771 | 6.903 | 6.8202 | 5.8478 | FAIL | 320-270 | -0.655 | -0.695 |  | -0.681 |  |  | -0.58611 | -0.726 |  | -0.5855 | -0.73299 | No data
650 | 6.031 | 5.831 | 6.516 | 6.671 |  | 6.143 | 6.3778 | 6.679 | 6.843 | 6.7214 | 5.7886 | FAIL | 290-270 | -0.087 | -0.086 |  | -0.258 |  |  | -0.56111 | -0.246 |  | -0.062244 | -0.58487 | No data
900 | 2.888 | 3.155 | 3.458 | 3.871 |  | 3.334 | 3.5667 | 3.457 | 3.778 | 3.9202 | 2.8389 | PASS | 300-270 | -2.952 | -2.548 |  | -2.577 |  |  | -2.4861 | -1.938 |  | -1.8933 | -3.0439 | No data
910 | 1.896 | 2.5 | 2.336 | 3.277 |  | 2.786 | 2.7917 | 3.147 | 2.703 | 3.3461 | 1.8269 | PASS | 310-300 | -0.556 | -0.344 |  | -0.493 |  |  | -0.68889 |  |  | -0.32676 | -0.70613 | No data
920 | 2.385 | 2.933 | 3.109 | 3.487 |  | 3.071 | 3.05 | 3.505 | 3.342 | 3.523 | 2.329 | PASS
930 | 1.873 | 2.546 | 2.388 | 3.08 |  | 2.486 | 2.4983 |  | 2.638 | 3.1404 | 1.8126 | PASS
940 | 2.888 | 3.155 | 3.458 | 3.871 |  | 3.334 | 3.5667 | 3.457 | 3.778 | 3.9202 | 2.8389 | PASS
950 | 2.033 | 2.621 | 2.664 | 3.17 |  | 2.677 | 2.6861 | 2.867 | 2.917 | 3.2269 | 1.9762 | PASS | LOW MASS IN-DEPTH (CASES 395 THRU 440) SENSITIVITY TESTS
960 | 0.953 | 1.144 | 1.057 | 1.37 |  | 1.179 | 1.378 | 1.403 | 1.408 | 1.4255 | 0.9305 | PASS | ANNUAL HEATING [MWH]
195 | 0.651 | [7 empty] | 0.689 | 0.79043 | 0.64436 | PASS |  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | ACCEPTANCE RANGE
200 | 0.863 | [8 empty] | 1.0363 | 0.85475 | No data | CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | Max | Min | Result
210 | 0.476 | 1.017 |  |  |  |  | 1.0678 | 1.142 |  | 1.1753 | 0.4427 | No data | 400-395 | 1.916 | 2.276 | 2.935 | 2.767 | 2.772 | 2.32 | 2.311 | 2.487 | 2.187 | 2.9859 | 1.865 | PASS
215 | 1.007 | [8 empty] | 1.1243 | 1.0014 | No data | 410-400 | 1.696 | 1.798 | 1.736 | 1.76 | 1.761 | 1.732 | 1.77 | 1.759 | 1.721 | 1.8958 | 1.6865 | PASS
220 | 0.56 | 1.166 | 0.937 | 1.34 |  | 1.215 | 1.1789 | 1.213 | 1.032 | 1.379 | 0.521 | PASS | 420-410 | -1.298 | -1.263 | -1.355 | -1.361 | -1.361 | -1.245 | -1.239 | -1.222 | -1.306 | -1.215 | -1.3679 | PASS
230 | 1.059 | 1.646 | 1.455 | 1.875 |  | 1.7 | 1.7078 | 1.749 | 1.545 | 1.9158 | 1.0182 | PASS | 430-420 | -1.869 | -1.122 | -1.324 | -1.187 | -1.187 | -1.112 | -1.197 | -1.353 | -1.765 | -1.0741 | -1.9068 | PASS
240 | 0.739 | 1.347 | 1.119 | 1.54 |  | 1.398 | 1.3614 | 1.397 | 1.214 | 1.58 | 0.69895 | PASS | 600-430 | -1.133 | -1.715 | -2.118 | -1.952 | -1.59 | -1.78 | -1.628 | -1.148 | -1.315 | -1.0838 | -2.1672 | PASS
250 | 3.36 | 3.036 | 2.605 | 2.59 |  | 2.258 | 3.2278 | 4.912 | 3.173 | 5.0447 | 2.1253 | PASS | 440-600 | 0.153 | 0.214 |  | 0.426 | 0.215 |  | 0.226 | 0.28 |  | 0.43965 | 0.13935 | No data
270 | 6.356 | 6.641 |  | 7.234 |  |  | 6.7639 | 6.867 |  | 7.2779 | 6.3121 | No data | ANNUAL COOLING [MWH]
280 | 4.444 | 4.631 |  | 5.22 |  |  | 4.7861 | 5.236 |  | 5.2756 | 4.4044 | No data |  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | ACCEPTANCE RANGE
290 | 6.269 | 6.555 |  | 6.976 |  |  | 6.2028 | 6.621 |  | 7.0147 | 6.1641 | No data | CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | Max | Min | Result
300 | 3.404 | 4.093 |  | 4.657 |  |  | 4.2778 | 4.929 |  | 5.0052 | 3.3277 | No data | 400-395 | 0 | 0.029 | 0.002 | 0.045 | 0.044 | 0.032 | 0.03439 | 0.033 | 0.015 | 0.04725 | -0.00225 | PASS
310 | 2.848 | 3.749 |  | 4.164 |  |  | 3.5889 |  |  | 4.2298 | 2.7822 | No data | 410-400 | 0 | 0.019 | 0.008 | 0.023 | 0.026 | 0.021 | 0.02239 | 0.021 | 0.019 | 0.0273 | -0.0013 | PASS
320 | 5.701 | 5.946 |  | 6.553 |  |  | 6.1778 | 6.141 |  | 6.5956 | 5.6584 | No data | 420-410 | 0.011 | 0.088 | 0.041 | 0.105 | 0.104 | 0.091 | 0.09043 | 0.078 | 0.07 | 0.1097 | 0.0063 | PASS
395 | 0 | 0.362 | 0 | 0.394 |  | 0.356 | 0.3625 | 0.345 | 0.175 | 0.4137 | -0.0197 | PASS | 430-420 | 0.531 | 0.47 | 0.371 | 0.515 | 0.496 | 0.409 | 0.4599 | 0.732 | 1.001 | 0.75005 | 0.35295 | FAIL
400 | 0 | 0.581 | 0.265 | 0.666 |  | 0.612 | 0.61333 | 0.572 | 0.407 | 0.6993 | -0.0333 | PASS | 600-430 | 5.595 | 5.816 | 6.657 | 6.574 | 7.28 | 5.929 | 5.8746 | 5.903 | 6.948 | 7.3643 | 5.576 | PASS
410 | 0.035 | 0.699 | 0.413 | 0.814 |  | 0.724 | 0.74306 | 0.71 | 0.559 | 0.85295 | -0.00395 | PASS | 440-600 | -2.17 | -2.261 |  | -2.604 | -2.76 |  | -2.517 | -2.094 |  | -2.0607 | -2.7879 | No data
420 | 0.258 | 0.923 | 0.631 | 1.047 |  | 0.938 | 0.93778 | 0.921 | 0.792 | 1.0864 | 0.21855 | PASS | PEAK HEATING [KW]
430 | 1.493 | 1.772 | 1.427 | 1.762 |  | 1.575 | 1.7983 | 2.578 | 2.113 | 2.6356 | 1.3694 | PASS |  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | ACCEPTANCE RANGE
440 | 4.546 | 4.424 |  | 5.053 |  |  | 4.6861 | 5.278 |  | 5.4867 | 0.89448 | No data | CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | Max | Min | Result
800 | 0.585 | 0.967 | 0.743 | 1.352 |  | 1.028 | 0.98278 | 1.358 | 1.267 | 5.0447 | 0.37263 | PASS | 400-395 | 0.805 | 1.071 | 1.148 | 1.31 |  | 1.079 | 1.115 | 1.25 | 0.954 | 1.3353 | 0.77975 | PASS
810 | 1.852 | 2.357 |  | 2.991 |  |  | 2.3436 | 2.862 |  | 3.048 | 1.7951 | No data | 410-400 | 0.758 | 0.844 | 0.757 | 0.792 |  | 0.885 | 0.77778 | 0.794 | 0.747 | 0.91887 | 0.74929 | FAIL
[13 empty] | 420-410 | -0.182 | -0.18 | -0.183 | -0.2 |  | -0.183 | -0.18333 | -0.188 | -0.183 | -0.179 | -0.201 | PASS
[13 empty] | 430-420 | -0.001 | 0 | 0 | 0 |  | 0 | 0 | 0.011 | 0 | 0.0116 | -0.0016 | PASS
[13 empty] | 600-430 | -0.005 | -0.004 | -0.005 | -0.029 |  | -0.007 | 0 | 0.217 | -0.052 | 0.23401 | -0.13808 | PASS
[13 empty] | 440-600 | 0.002 | 0.002 |  | 0.019 |  |  | 0 | 0.022 |  | 0.0231 | -0.0011 | No data
PEAK COOLING [KW]
[14 empty] | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | ACCEPTANCE RANGE
[13 empty] | CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | Max | Min | Result
[13 empty] | 400-395 | 0 | 0.219 | 0.265 | 0.272 |  | 0.256 | 0.25083 | 0.227 | 0.232 | 0.2856 | -0.0136 | PASS
[13 empty] | 410-400 | 0.035 | 0.118 | 0.148 | 0.148 |  | 0.112 | 0.12972 | 0.138 | 0.152 | 0.15365 | 0.02935 | PASS
[13 empty] | 420-410 | 0.223 | 0.224 | 0.218 | 0.233 |  | 0.214 | 0.19472 | 0.211 | 0.233 | 0.2577 | 0.19172 | PASS
[13 empty] | 430-420 | 1.235 | 0.849 | 0.796 | 0.715 |  | 0.637 | 0.86056 | 1.657 | 1.321 | 1.708 | 0.586 | PASS
[13 empty] | 600-430 | 4.701 | 4.193 | 5.229 | 5.065 |  | 4.711 | 4.6878 | 4.234 | 4.852 | 5.2808 | 4.1412 | PASS
[13 empty] | 440-600 | -1.648 | -1.541 |  | -1.774 |  |  | -1.8 | -1.534 |  | -1.518 | -1.8692 | No data
HIGH MASS BASIC AND IN-DEPTH SENSITIVITY TESTS
FREE-FLOAT TEMPERATURE OUTPUT | [12 empty] | ANNUAL HEATING [MWH]
MAXIMUM ANNUAL HOURLY ZONE TEMPERATURE (C) | [13 empty] | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | ACCEPTANCE RANGE
CODENAME: | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | ACCEPTANCE RANGE |  |  | CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | Max | Min | Result
COUNTRY: | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | MAX | MIN | Test | 800-430 | -0.561 | -0.535 | -0.599 | -0.567 | -0.586 | -0.501 | -0.56 | -0.649 | -0.956 | -0.49233 | -0.68307 | FAIL
CASE# | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | C | C | Result | 900-800 | -3.698 | -4.343 | -5.356 | -4.714 | -4.612 | -4.431 | -4.285 | -3.82 | -4.052 | -3.6151 | -5.4389 | PASS
600FF | 64.929 | 65.11 | 69.5 | 68.6 |  | 64.9 | 65.25 | 65.25 | 73.4 | 69.73 | 64.67 | FAIL | 900-810 | -0.669 | -0.836 |  | -1.107 | -0.84 |  | -0.912 | -0.921 |  | -0.6471 | -1.1289 | No data
900FF | 41.812 | 43.44 | 42.7 | 44.8 |  | 43 | 42.46 | 43.17 | 45.5 | 44.9494 | 41.6626 | FAIL | 910-610 | -2.78 | -2.944 | -3.532 | -3.106 | -3.338 | -2.908 | -2.873 | -3.163 | -3.483 | -2.7424 | -3.5696 | PASS
650FF | 63.236 | 63.45 | 68.2 | 67 |  | 63.3 | 63.74 | 63.82 | 71.7 | 68.4557 | 62.8298 | FAIL | 920-620 | -1.3 | -1.297 | -1.689 | -1.461 | -1.676 | -1.329 | -1.297 | -1.428 | -1.832 | -1.2774 | -1.7086 | FAIL
950FF | 35.54 | 36.23 | 35.9 | 38.5 |  | 36.1 | 35.67 | 37.58 | 37.1 | 38.648 | 35.392 | PASS | 930-630 | -0.907 | -1.012 | -1.134 | -1.128 | -1.273 | -0.927 | -0.884 |  | -1.259 | -0.86455 | -1.2924 | PASS
960 | 48.943 | 48.88 | 49 | 51 |  | 50.2 | 55.34 | 48.92 | 51.6 | 55.663 | 48.557 | PASS | 940-640 | -1.958 | -1.867 | -2.304 | -2.024 | -2.392 | -1.886 | -1.963 | -1.986 | -2.157 | -1.8407 | -2.4183 | PASS
MINIMUM ANNUAL HOURLY ZONE TEMPERATURE (C) | [12 empty] | ANNUAL COOLING [MWH]
CODENAME: | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | ACCEPTANCE RANGE |  |  |  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | ACCEPTANCE RANGE
COUNTRY: | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | MAX | MIN | Test | CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | Max | Min | Result
CASE# | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | C | C | Result | 800-430 | -0.429 | -0.393 | -0.367 | -0.432 | -0.462 | -0.368 | -0.4101 | -0.55 | -0.783 | -0.36283 | -0.55915 | FAIL
600FF | -15.565 | -17.05 | -18.8 | -18 |  | -17.8 | -17.81 | -18.47 | -17.7 | -15.4032 | -18.9591 | PASS | 900-800 | 2.019 | 2.376 | 2.4 | 2.893 | 3.193 | 2.377 | 2.2777 | 2.274 | 3.067 | 3.2517 | 1.9603 | PASS
900FF | -1.647 | -3.15 | -4.3 | -4.5 |  | -4 | -6.38 | -5.64 | -2 | -1.4103 | -6.6167 | PASS | 900-810 | 1.08 | 1.195 |  | 1.454 | 1.707 |  | 1.294 | 0.975 |  | 1.7436 | 0.9384 | No data
650FF | -22.564 | -22.96 | -21.6 | -23 |  | -22.9 | -22.83 | -22.91 | -21 | -21.5246 | -23.1831 | FAIL | 910-610 | -3.094 | -3.318 | -3.876 | -3.576 | -3.924 | -3.336 | -3.275 | -3.739 | -4.136 | -3.0525 | -3.9655 | FAIL
950FF | -19.484 | -20.04 | -18.6 | -19.7 |  | -20.2 | -19.34 | -19.96 | -17.8 | -18.5125 | -20.4366 | FAIL | 920-620 | -1.577 | -1.476 | -1.894 | -1.69 | -1.912 | -1.554 | -1.483 | -1.738 | -2.087 | -1.4542 | -1.9338 | FAIL
960 | 2.729 | 1.63 | 3.9 | 3.1 |  | 1.4 | -2.82 | -0.39 | 6 | 4.236 | -3.156 | FAIL | 930-630 | -1.09 | -1.174 | -1.223 | -1.32 | -1.463 | -1.05 | -1 |  | -1.412 | -0.99353 | -1.4862 | PASS
AVERAGE ANNUAL HOURLY ZONE TEMPERATURE (C) | [12 empty] | 940-640 | -3.873 | -3.647 | -4.419 | -3.99 | -4.57 | -3.758 | -3.863 | -3.992 | -4.441 | -3.6009 | -4.6161 | PASS
CODENAME: | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | ACCEPTANCE RANGE |  |  | 950-650 | -4.429 | -4.614 | -5.257 | -4.973 | -5.956 | -4.537 | -4.5584 | -4.685 | -5.929 | -4.3527 | -6.0324 | PASS
COUNTRY: | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | MAX | MIN | Test | PEAK HEATING [KW]
CASE# | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | C | C | Result |  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | ACCEPTANCE RANGE
600FF | 25.126 | 25.43 | 24.6 | 25.48 | 25.93 | 25.2 | 24.49 | 24.22 | 26.993 | 26.0155 | 24.1345 | FAIL | CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | Max | Min | Result
900FF | 25.453 | 25.93 | 24.7 | 25.49 | 25.72 | 25.2 | 24.47 | 24.45 | 27.0563 | 25.9334 | 24.4198 | FAIL | 800-430 | -0.215 | -0.151 | -0.141 | -0.149 |  | -0.142 | -0.14444 | -0.198 | -0.185 | -0.1373 | -0.2187 | PASS
650FF | 18.234 | 18.69 | 19.1 | 18.96 | 19.62 | 18.4 | 17.99 | 18.36 | 20.4281 | 19.7015 | 17.9635 | FAIL | 900-800 | -0.377 | -0.34 | -0.352 | -0.378 |  | -0.294 | -0.26944 | -0.142 | -0.386 | -0.12027 | -0.59835 | PASS
950FF | 14.14 | 14.26 | 14.3 | 14.97 | 14.29 | 14 | 14.53 | 14.64 | 15.0742 | 15.0185 | 13.9827 | FAIL | 900-810 | -0.129 | -0.113 |  | -0.155 |  |  | -0.088889 | -0.166 |  | -0.085033 | -0.16986 | No data
960 | 27.49 | 27.72 | 28 | 28.69 | 28.54 | 28 | 28.96 | 26.43 | 30.0216 | 29.0378 | 26.3035 | FAIL | 910-610 | -0.579 | -0.485 | -0.47 | -0.494 |  | -0.419 | -0.38611 | -0.553 | -0.499 | -0.38055 | -0.58691 | PASS
[13 empty] | 920-620 | -0.283 | -0.238 | -0.241 | -0.264 |  | -0.248 | -0.21389 | -0.318 | -0.277 | -0.20868 | -0.32321 | PASS
[13 empty] | 930-630 | -0.237 | -0.209 | -0.193 | -0.238 |  | -0.214 | -0.17778 |  | -0.226 | -0.17477 | -0.24101 | PASS
[13 empty] | 940-640 | -1.252 | -0.458 | -0.278 | -0.414 |  | -0.23 | -0.6 | -0.526 | -0.334 | -0.16634 | -1.5669 | PASS
PEAK COOLING [KW]
[14 empty] | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | ACCEPTANCE RANGE
[13 empty] | CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | Max | Min | Result
[13 empty] | 800-430 | -0.908 | -0.805 | -0.684 | -0.41 |  | -0.547 | -0.81556 | -1.22 | -0.846 | -0.39821 | -1.528 | PASS
[13 empty] | 900-800 | 2.303 | 2.188 | 2.715 | 2.519 |  | 2.306 | 2.5839 | 2.099 | 2.511 | 2.7458 | 2.0808 | PASS
[13 empty] | 900-810 | 1.036 | 0.798 |  | 0.88 |  |  | 1.2231 | 0.595 |  | 1.2545 | 0.5636 | No data
SOLAR RADIATION | [12 empty] | 910-610 | -3.773 | -3.324 | -3.728 | -3.094 |  | -3.384 | -2.8833 | -2.999 | -3.779 | -2.8389 | -3.8175 | PASS
ANNUAL INCIDENT TOTAL | [12 empty] | 920-620 | -1.249 | -1.142 | -1.321 | -1.106 |  | -1.226 | -1.225 | -1.591 | -1.337 | -1.0818 | -1.6152 | PASS
CASE 600 | [12 empty] | 930-630 | -1.199 | -1.158 | -1.2 | -1.036 |  | -1.179 | -1.11 |  | -1.196 | -1.0278 | -1.2082 | PASS
[13 empty] | 940-640 | -3.273 | -2.737 | -3.118 | -2.905 |  | -2.916 | -2.875 | -3.314 | -3.125 | -2.7081 | -3.3428 | PASS
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR |  |  |  | 950-650 | -3.998 | -3.21 | -3.852 | -3.501 |  | -3.466 | -3.6917 | -3.812 | -3.926 | -3.1706 | -4.0374 | PASS
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA
SURFACE | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2
= | = | = | = | = | = | = | = | = | = |  |  |  |  | ANNUAL TRANSMISSIVITY COEFFICIENT OF WINDOWS
NORTH | 427 |  | 434 | 456 | 407.3 | 457 | 367.4 | 453 | 450.2906 |  |  |  | (ANNUAL UNSHADED TRANSMITTED SOLRAD)/(ANNUAL UNSHADED INCIDENT SOLRAD)
EAST | 959 |  | 1155 | 1083 | 1217.3 | 1082 | 1101 | 962 | 1165.8275
WEST | 1086 |  | 1079 | 1003 | 856.5 | 1002 | 1012 | 1090 | 1088.9381 |  |  |  | CODENAME: | ESP | BLAST | DOE2.1D | SUNCODE | SERIRES | S3PAS | TRNSYS | TASE | YOUR
SOUTH | 1456 |  | 1566 | 1476 | 1467.7 | 1474 | 1522 | 1468 | 1579.3093 |  |  |  | COUNTRY: | UK-DMU | US/IT | USA | USA | UK | SPAIN | BEL/UK | FINLAND | DATA
HORZ. | 1797 |  | 1831 | 1832 | 1831.8 | 1832 | 1832 | 1832 | 1830.85 |  |  |  | CASE#
= | = | = | = | = | = | = | = | = | =
[13 empty] | 620WEST | 0.67403 |  | 0.68119 | 0.68694 | 0.65728 | 0.64072 | 0.65382 | 0.64771 | 0.681
[13 empty] | 600SOUTH | 0.64973 |  | 0.67114 | 0.65176 | 0.6502 | 0.62822 | 0.64663 | 0.62262 | 0.672
SOLAR RADIATION
UNSHADED ANNUAL TRANSMITTED
ANNUAL SHADING COEFFICIENT OF WINDOW SHADING DEVICES: OVERHANGS & FINS
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR |  |  |  | (1-(ANNUAL SHADED TRANSMITTED SOLRAD)/(ANNUAL UNSHADED TRANSMITTED SOLRAD))
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA
CASE# | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 |  |  |  | CODENAME: | ESP | BLAST | DOE2.1D | SUNCODE | SERIRES | S3PAS | TRNSYS | TASE | YOUR
= | = | = | = | = | = | = | = | = | = |  |  |  | COUNTRY: | UK-DMU | US/IT | USA | USA | UK | SPAIN | BEL/UK | FINLAND | DATA
620WEST | 732 |  | 735 | 689 | 562.96 | 642 | 661.67 | 706 | 704.776 |  |  |  | CASE#
600SOUTH | 946 |  | 1051 | 962 | 954.3 | 926 | 984.17 | 914 | 1004.936
= | = | = | = | = | = | = | = | = | = |  |  |  | 630/620 W | 0.18169 |  | 0.34558 | 0.19594 | 0.21611 | 0.32866 | 0.33879 |  | 0.56
[13 empty] | 610/600 S | 0.17019 |  | 0.20932 | 0.16528 | 0.18803 | 0.18251 | 0.20542 | 0.11488 | 0.464
ANNUAL HOURLY INTEGRATED PEAK HEATING LOADS
[13 empty] | CODENAME: |  | ESP |  |  | BLAST |  |  | DOE2 |  |  | SRES/SUN |  |  |  | SERIRES |  |  | S3PAS |  |  | TRNSYS |  |  | TASE |  |  | YOUR
[13 empty] | COUNTRY: |  | UK-DMU |  |  | USA/ITALY |  |  | USA |  |  | USA |  |  |  | UK-BRE |  |  | SPAIN |  |  | BEL/UK |  |  | FINLAND |  |  | DATA
[13 empty] | CASE# | KW | DATE | HR | KW | DATE | HR | KW | DATE | HR | KW | DATE |  | HR | KW | DATE | HR | KW | DATE | HR | KW | DATE | HR | KW | DATE | HR | KW | DATE | HR | MIN | MAX
SOLAR RADIATION | [12 empty] | 600 | 3.437 | 1993-01-04 | 5 | 3.94 | JAN 04 | 5 | 4.045 | JAN 04 | 5 | 4.258 | JAN 04 |  | 2 |  |  |  | 4.037 | JAN 04 | 2 | 3.9306 | Jan-04 | 6 | 4.354 | JAN 04 | 2 | 3.767 | 2006-01-04 | 5 | 3.437 | 4.354
SHADED ANNUAL TRANSMITTED | [12 empty] | 610 | 3.437 | 1993-01-04 | 5 | 3.941 | JAN 04 | 5 | 4.034 | JAN 04 | 5 | 4.258 | JAN 04 |  | 2 |  |  |  | 4.037 | JAN 04 | 2 | 3.9222 | Jan-04 | 6 | 4.354 | JAN 04 | 2 | 3.755 | 2006-01-04 | 5 | 3.437 | 4.354
[13 empty] | 620 | 3.591 | 1993-01-04 | 6 | 3.941 | JAN 04 | 5 | 4.046 | JAN 04 | 5 | 4.277 | JAN 04 |  | 2 |  |  |  | 4.277 | JAN 04 | 2 | 3.9222 | Jan-04 | 6 | 4.379 | JAN 04 | 2 | 3.785 | 2006-01-04 | 5 | 3.591 | 4.379
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR |  |  |  | 630 | 3.592 | 1993-01-04 | 7 | 3.941 | JAN 04 | 5 | 4.025 | JAN 04 | 5 | 4.28 | JAN 04 |  | 2 |  |  |  | 4.278 | JAN 04 | 2 | 3.9222 | Jan-04 | 6 |  |  |  | 3.762 | 2006-01-04 | 5 | 3.592 | 4.28
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA |  |  |  | 640 | 5.232 | 1993-01-04 | 7 | 5.486 | JAN 04 | 8 | 5.943 | JAN 04 | 8 | 6.53 | JAN 04 |  | 8 |  |  |  | 6.347 | JAN 04 | 8 | 5.7222 | Jan-04 | 8 | 6.954 | JAN 04 | 8 | 5.656 | 2006-01-04 | 5 | 5.232 | 6.954
CASE# | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 |  |  |  | 650 | 0 |  |  | 0 |  |  | 0 |  |  | 0 | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0
= | = | = | = | = | = | = | = | = | = |  |  |  | 900 | 2.85 | 1993-01-04 | 7 | 3.453 | JAN 04 | 7 | 3.557 | JAN 04 | 7 | 3.76 | JAN 04 |  | 7 |  |  |  | 3.608 | JAN 04 | 8 | 3.5167 | Jan-04 | 7 | 3.797 | JAN 04 | 7 | 3.248 | 2006-01-04 | 7 | 2.85 | 3.797
630WEST | 599 |  | 481 | 554 | 441.3 | 431 | 437.5 |  | 462.231 |  |  |  | 910 | 2.858 | 1993-01-04 | 7 | 3.456 | JAN 04 | 7 | 3.564 | JAN 04 | 7 | 3.764 | JAN 04 |  | 7 |  |  |  | 3.618 | JAN 04 | 8 | 3.5361 | Jan-04 | 7 | 3.801 | JAN 04 | 7 | 3.256 | 2006-01-04 | 7 | 2.858 | 3.801
610SOUTH | 785 |  | 831 | 803 | 774.86 | 757 | 782 | 809 | 803.901 |  |  |  | 920 | 3.308 | 1993-01-04 | 7 | 3.703 | JAN 04 | 7 | 3.805 | JAN 04 | 7 | 4.013 | JAN 04 |  | 7 |  |  |  | 4.029 | JAN 04 | 7 | 3.7083 | Jan-04 | 7 | 4.061 | JAN 04 | 7 | 3.508 | 2006-01-04 | 7 | 3.308 | 4.061
= | = | = | = | = | = | = | = | = | = |  |  |  | 930 | 3.355 | 1993-01-04 | 7 | 3.732 | JAN 04 | 7 | 3.832 | JAN 04 | 7 | 4.042 | JAN 04 |  | 7 |  |  |  | 4.064 | JAN 04 | 7 | 3.7444 | Jan-04 | 7 |  |  |  | 3.536 | 2006-01-04 | 7 | 3.355 | 4.064
[13 empty] | 940 | 3.98 | 1993-01-04 | 7 | 5.028 | JAN 04 | 8 | 5.665 | JAN 04 | 8 | 6.116 | JAN 04 |  | 8 |  |  |  | 6.117 | JAN 04 | 8 | 5.1222 | Jan-03 | 9 | 6.428 | JAN 04 | 8 | 5.322 | 2006-01-04 | 8 | 3.98 | 6.428
[13 empty] | 950 | 0 |  |  | 0 |  |  | 0 |  |  | 0 | [6 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0
[13 empty] | 960 | 2.41 | 1993-01-04 | 7 | 2.751 | JAN 04 | 8 | 2.727 | JAN 04 | 8 | 2.863 | JAN 04 |  | 8 |  |  |  | 2.852 | JAN 04 | 8 | 2.522 | Jan-04 | 8 | 2.779 | JAN 04 | 8 | 2.603 | 2006-01-04 | 8 | 2.41 | 2.863
[13 empty] | 195 | 2.004 | 1993-01-04 | 2 | [22 empty] | 2.294 | 2006-01-04 | 3 | 2.004 | 2.004
[13 empty] | 200 | 2.651 | 1993-01-04 | 5 | [25 empty] | 2.651 | 2.651
HOURLY INCIDENT SOLAR RADIATION CLOUDY DAY, MARCH 5 | [12 empty] | 210 | 2.701 | 1993-01-04 | 5 | 2.973 | JAN 04 | 5 | [13 empty] | 2.9806 | Jan-04 | 5 | 3.325 | JAN 04 | 2 |  |  |  | 2.701 | 3.325
CASE 600 | [12 empty] | 215 | 2.787 | 1993-01-04 | 5 | [25 empty] | 2.787 | 2.787
SOUTH SURFACE | [12 empty] | 220 | 2.867 | 1993-01-04 | 5 | 3.28 | JAN 04 | 5 | 3.465 | JAN 04 | 5 | 3.695 | JAN 04 |  | 2 |  |  |  | 3.348 | JAN 04 | 8 | 3.3361 | Jan-04 | 6 | 3.52 | JAN 04 | 2 | 3.245 | 2006-01-04 | 5 | 2.867 | 3.695
[13 empty] | 230 | 4.386 | 1993-01-04 | 5 | 4.984 | JAN 04 | 2 | 4.994 | JAN 04 | 2 | 5.279 | JAN 04 |  | 2 |  |  |  | 5.159 | JAN 04 | 2 | 4.8917 | Jan-04 | 6 | 5.107 | JAN 04 | 2 | 4.743 | 2006-01-04 | 2 | 4.386 | 5.279
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR |  |  |  | 240 | 2.685 | 1993-01-04 | 5 | 3.1 | JAN 04 | 5 | 3.282 | JAN 04 | 5 | 3.495 | JAN 04 |  | 2 |  |  |  | 3.159 | JAN 04 | 8 | 3.1528 | Jan-04 | 6 | 3.333 | JAN 04 | 8 | 3.062 | 2006-01-04 | 5 | 2.685 | 3.495
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA |  |  |  | 250 | 2.866 | 1993-01-04 | 5 | 3.279 | JAN 04 | 5 | 3.465 | JAN 04 | 5 | 3.695 | JAN 04 |  | 2 |  |  |  | 3.341 | JAN 04 | 6 | 3.3361 | Jan-04 | 6 | 3.525 | JAN 04 | 2 | 3.245 | 2006-01-04 | 5 | 2.866 | 3.695
HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 |  |  |  | 270 | 2.863 | 1993-01-04 | 5 | 3.277 | JAN 04 | 5 |  |  |  | 3.661 | JAN 04 |  | 2 | [6 empty] | 3.3361 | Jan-04 | 6 | 3.738 | JAN 04 | 2 |  |  |  | 2.863 | 3.738
= | = | = | = | = | = | = | = | = | = |  |  |  | 280 | 2.864 | 1993-01-04 | 5 | 3.278 | JAN 04 | 5 |  |  |  | 3.685 | JAN 04 |  | 2 | [6 empty] | 3.3361 | Jan-04 | 6 | 3.759 | JAN 04 | 2 |  |  |  | 2.864 | 3.759
1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 290 | 2.863 | 1993-01-04 | 5 | 3.277 | JAN 04 | 5 |  |  |  | 3.661 | JAN 04 |  | 2 | [6 empty] | 3.3278 | Jan-04 | 6 | 3.738 | JAN 04 | 2 |  |  |  | 2.863 | 3.738
2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 300 | 3.014 | 1993-01-04 | 6 | 3.276 | JAN 04 | 5 |  |  |  | 3.681 | JAN 04 |  | 2 | [6 empty] | 3.3278 | Jan-04 | 6 | 3.77 | JAN 04 | 2 |  |  |  | 3.014 | 3.77
3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 310 | 3.015 | 1993-01-04 | 6 | 3.277 | JAN 04 | 5 |  |  |  | 3.669 | JAN 04 |  | 2 | [6 empty] | 3.3278 | Jan-04 | 6 | [6 empty] | 3.015 | 3.669
4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 320 | 2.861 | 1993-01-04 | 5 | 3.275 | JAN 04 | 5 |  |  |  | 3.651 | JAN 04 |  | 2 | [6 empty] | 3.3361 | Jan-04 | 6 | 3.735 | JAN 04 | 3 |  |  |  | 2.861 | 3.735
5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 395 | 2.062 | 1993-01-04 | 7 | 2.209 | JAN 04 | 8 | 2.328 | JAN 04 | 3 | 2.385 | JAN 04 |  | 3 |  |  |  | 2.263 | JAN 04 | 4 | 2.2211 | Jan-04 | 8 | 2.27 | JAN 04 | 3 | 2.301 | 2006-01-04 | 3 | 2.062 | 2.385
6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 400 | 2.867 | 1993-01-04 | 5 | 3.28 | JAN 04 | 5 | 3.476 | JAN 04 | 5 | 3.695 | JAN 04 |  | 2 |  |  |  | 3.342 | JAN 04 | 8 | 3.3361 | Jan-04 | 6 | 3.52 | JAN 04 | 2 | 3.255 | 2006-01-04 | 5 | 2.867 | 3.695
7 | 1.6 |  | 1.5 | 3.0447 | 3.02 | 3 | 3.05 | 3 | 1.49 |  |  |  | 410 | 3.625 | 1993-01-04 | 5 | 4.124 | JAN 04 | 5 | 4.233 | JAN 04 | 5 | 4.487 | JAN 04 |  | 2 |  |  |  | 4.227 | JAN 04 | 2 | 4.1139 | Jan-04 | 6 | 4.314 | JAN 04 | 2 | 4.002 | 2006-01-04 | 5 | 3.625 | 4.487
8 | 13.8 |  | 12.59 | 20.6464 | 20.59 | 21 | 20.69 | 20.68 | 12.47 |  |  |  | 420 | 3.443 | 1993-01-04 | 5 | 3.944 | JAN 04 | 5 | 4.05 | JAN 04 | 5 | 4.287 | JAN 04 |  | 2 |  |  |  | 4.044 | JAN 04 | 2 | 3.9306 | Jan-04 | 6 | 4.126 | JAN 04 | 2 | 3.819 | 2006-01-04 | 5 | 3.443 | 4.287
9 | 31.6 |  | 30.01 | 38.8836 | 38.83 | 39 | 38.94 | 38.94 | 29.43 |  |  |  | 430 | 3.442 | 1993-01-04 | 5 | 3.944 | JAN 04 | 5 | 4.05 | JAN 04 | 5 | 4.287 | JAN 04 |  | 2 |  |  |  | 4.044 | JAN 04 | 2 | 3.9306 | Jan-04 | 6 | 4.137 | JAN 04 | 2 | 3.819 | 2006-01-04 | 5 | 3.442 | 4.287
10 | 48.3 |  | 46.23 | 54.5664 | 54.53 | 55 | 54.67 | 54.56 | 45.63 |  |  |  | 440 | 3.439 | 1993-01-04 | 5 | 3.942 | JAN 04 | 5 |  |  |  | 4.277 | JAN 04 |  | 2 | [6 empty] | 3.9306 | Jan-04 | 6 | 4.376 | JAN 04 | 2 |  |  |  | 3.439 | 4.376
11 | 61.6 |  | 59.31 | 65.9733 | 54.77 | 66 | 66.08 | 65.99 | 58.57 |  |  |  | 800 | 3.227 | 1993-01-04 | 5 | 3.793 | JAN 04 | 7 | 3.909 | JAN 04 | 7 | 4.138 | JAN 04 |  | 2 |  |  |  | 3.902 | JAN 04 | 8 | 3.7861 | Jan-04 | 7 | 3.939 | JAN 04 | 7 | 3.634 | 2006-01-04 | 7 | 3.227 | 4.138
12 | 69.3 |  | 65.05 | 71.7839 | 59.65 | 72 | 71.92 | 71.74 | 64.28 |  |  |  | 810 | 2.979 | 1993-01-04 | 7 | 3.566 | JAN 04 | 7 |  |  |  | 3.915 | JAN 04 |  | 7 | [6 empty] | 3.6056 | Jan-04 | 7 | 3.963 | JAN 04 | 7 |  |  |  | 2.979 | 3.963
13 | 71.7 |  | 66.98 | 72.2839 | 60.1 | 72 | 72.42 | 72.3 | 66.18
14 | 68.1 |  | 63.11 | 66.4075 | 55.24 | 66 | 66.53 | 66.38 | 62.33
15 | 58.9 |  | 51.79 | 54.8997 | 45.68 | 55 | 55 | 54.8 | 51.13
16 | 44.4 |  | 37.13 | 38.8836 | 32.37 | 39 | 38.94 | 38.84 | 36.61
17 | 26.9 |  | 19.14 | 20.4797 | 17.06 | 20 | 20.52 | 20.46 | 18.91
18 | 8.7 |  | 4.62 | 3.0447 | 2.54 | 3 | 3.05 | 0 | 4.59
19 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
= | = | = | = | = | = | = | = | = | =
ANNUAL HOURLY INTEGRATED PEAK COOLING LOADS
[13 empty] | CODENAME: |  | ESP |  |  | BLAST |  |  | DOE2 |  |  | SRES/SUN |  |  |  | SERIRES |  |  | S3PAS |  |  | TRNSYS |  |  | TASE |  |  | YOUR
[13 empty] | COUNTRY: |  | UK-DMU |  |  | USA/ITALY |  |  | USA |  |  | USA |  |  |  | UK-BRE |  |  | SPAIN |  |  | BEL/UK |  |  | FINLAND |  |  | DATA
[13 empty] | CASE# | KW | DATE | HR | KW | DATE | HR | KW | DATE | HR | KW | DATE |  | HR | KW | DATE | HR | KW | DATE | HR | KW | DATE |  | KW | DATE | HR | KW | DATE | HR | MIN | MAX
[13 empty] | 600 | 6.194 | 1993-10-17 | 13 | 5.965 | OCT 16 | 14 | 6.656 | OCT 16 | 13 | 6.827 | OCT 16 |  | 14 |  |  |  | 6.286 | NOV 25 | -6.194 | 6.4861 | Oct-16 | 14 | 6.812 | OCT 17 | 14 | 6.965 | 2006-10-17 | 13 | 5.965 | 6.827
[13 empty] | 610 | 5.669 | 1993-11-25 | 13 | 5.824 | NOV 25 | 14 | 6.064 | JAN 13 | 14 | 6.371 | NOV 25 |  | 14 |  |  |  | 6.17 | NOV 25 | -5.669 | 5.675 | 1925-11-01 | 14 | 6.146 | OCT 17 | 14 | 6.482 | 2006-01-13 | 14 | 5.669 | 6.371
HOURLY INCIDENT SOLAR RADIATION CLOUDY DAY, MARCH 5 | [12 empty] | 620 | 3.634 | 1993-07-26 | 16 | 4.075 | JUL 26 | 17 | 4.43 | JUL 26 | 17 | 4.593 | JUL 26 |  | 17 |  |  |  | 4.297 | JUL 26 | -3.634 | 4.275 | 1926-07-01 | 17 | 5.096 | JUL 26 | 16 | 4.679 | 2006-07-26 | 17 | 3.634 | 5.096
CASE 600 | [12 empty] | 630 | 3.072 | 1993-07-26 | 16 | 3.704 | JUL 26 | 17 | 3.588 | JUL 26 | 17 | 4.116 | JUL 26 |  | 17 |  |  |  | 3.665 | JUL 26 | -3.072 | 3.6083 | 1926-07-01 | 17 |  |  |  | 3.834 | 2006-07-26 | 17 | 3.072 | 4.116
WEST SURFACE | [12 empty] | 640 | 6.161 | 1993-10-17 | 13 | 5.892 | OCT 16 | 14 | 6.576 | OCT 16 | 14 | 6.776 | OCT 16 |  | 14 |  |  |  | 6.25 | NOV 25 | -6.161 | 6.4417 | Oct-16 | 14 | 6.771 | OCT 17 | 14 | 6.903 | 2006-10-16 | 14 | 5.892 | 6.776
[13 empty] | 650 | 6.031 | 1993-10-17 | 13 | 5.831 | OCT 16 | 14 | 6.516 | OCT 16 | 14 | 6.671 | OCT 16 |  | 14 |  |  |  | 6.143 | NOV 25 | -6.031 | 6.3778 | Oct-17 | 14 | 6.679 | OCT 17 | 14 | 6.843 | 2006-10-16 | 14 | 5.831 | 6.679
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR |  |  |  | 900 | 2.888 | 1993-10-17 | 14 | 3.155 | OCT 06 | 15 | 3.458 | OCT 17 | 14 | 3.871 | OCT 17 |  | 14 |  |  |  | 3.334 | OCT 17 | -2.888 | 3.5667 | Oct-17 | 15 | 3.457 | OCT 17 | 15 | 3.778 | 2006-10-17 | 14 | 2.888 | 3.871
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA |  |  |  | 910 | 1.896 | 1993-10-17 | 15 | 2.5 | OCT 21 | 15 | 2.336 | OCT 17 | 15 | 3.277 | OCT 17 |  | 15 |  |  |  | 2.786 | OCT 17 | -1.896 | 2.7917 | Oct-17 | 15 | 3.147 | OCT 17 | 15 | 2.703 | 2006-10-17 | 15 | 1.896 | 3.277
HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 |  |  |  | 920 | 2.385 | 1993-07-26 | 16 | 2.933 | JUL 26 | 17 | 3.109 | JUL 26 | 17 | 3.487 | JUL 26 |  | 17 |  |  |  | 3.071 | JUL 26 | -2.385 | 3.05 | 1926-07-01 | 17 | 3.505 | JUL 26 | 17 | 3.342 | 2006-07-26 | 17 | 2.385 | 3.505
= | = | = | = | = | = | = | = | = | = |  |  |  | 930 | 1.873 | 1993-07-26 | 17 | 2.546 | JUL 26 | 17 | 2.388 | JUL 26 | 18 | 3.08 | JUL 26 |  | 17 |  |  |  | 2.486 | JUL 26 | -1.873 | 2.4983 | 1926-07-01 | 17 |  |  |  | 2.638 | 2006-07-26 | 17 | 1.873 | 3.08
1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 940 | 2.888 | 1993-10-17 | 14 | 3.155 | OCT 06 | 15 | 3.458 | OCT 17 | 14 | 3.871 | OCT 17 |  | 14 |  |  |  | 3.334 | OCT 17 | -2.888 | 3.5667 | Oct-17 | 15 | 3.457 | OCT 17 | 15 | 3.778 | 2006-10-17 | 14 | 2.888 | 3.871
2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 950 | 2.033 | 1993-09-02 | 14 | 2.621 | SEP 02 | 15 | 2.664 | SEP 2 | 15 | 3.17 | SEP 02 |  | 14 |  |  |  | 2.677 | SEP 02 | -2.033 | 2.6861 | Sep-02 | 15 | 2.867 | SEP 02 | 14 | 2.917 | 2006-09-02 | 15 | 2.033 | 3.17
3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 960 | 0.953 | 1993-08-16 | 16 | 1.144 | JUL 26 | 16 | 1.057 | JUL 26 | 16 | 1.37 | JUL 26 |  | 16 |  |  |  | 1.179 | JUL 26 | 16 | 1.378 | 1926-07-01 | 16 | 1.403 | JUL 26 | 16 | 1.408 | 2006-07-26 | 16 | 0.953 | 1.403
4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 195 | 0.651 | 1993-07-26 | 15 | [22 empty] | 0.689 | 2006-07-27 | 15 | 0.651 | 0.651
5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 200 | 0.863 | 1993-08-16 | 14 | [25 empty] | 0.863 | 0.863
6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 210 | 0.476 | 1993-08-16 | 16 | 1.017 | JUL 26 | 15 | [13 empty] | 1.0678 | 1926-07-01 | 16 | 1.142 | JUL 26 | 15 |  |  |  | 0.476 | 1.142
7 | 1.6 |  | 1.8 | 2.9967 | 3 | 3 | 2.99 | 3 | 1.8 |  |  |  | 215 | 1.007 | 1993-08-11 | 14 | [25 empty] | 1.007 | 1.007
8 | 13.5 |  | 13.92 | 20.1831 | 20.24 | 20 | 20.17 | 20.15 | 14.01 |  |  |  | 220 | 0.56 | 1993-07-27 | 15 | 1.166 | JUL 26 | 15 | 0.937 | JUL 27 | 14 | 1.34 | JUL 26 |  | 15 |  |  |  | 1.215 | JUL 26 | -0.56 | 1.1789 | 1926-07-01 | 16 | 1.213 | JUL 26 | 15 | 1.032 | 2006-07-27 | 15 | 0.56 | 1.34
9 | 31 |  | 31.75 | 37.955 | 38.01 | 38 | 37.92 | 37.9 | 32.07 |  |  |  | 230 | 1.059 | 1993-07-27 | 15 | 1.646 | JUL 26 | 15 | 1.455 | JUL 27 | 14 | 1.875 | JUL 26 |  | 15 |  |  |  | 1.7 | JUL 26 | -1.059 | 1.7078 | 1926-07-01 | 16 | 1.749 | JUL 26 | 15 | 1.545 | 2006-07-27 | 15 | 1.059 | 1.875
10 | 47.1 |  | 45.24 | 53.2444 | 53.27 | 53 | 53.17 | 53.15 | 45.58 |  |  |  | 240 | 0.739 | 1993-07-27 | 15 | 1.347 | JUL 26 | 15 | 1.119 | JUL 27 | 14 | 1.54 | JUL 26 |  | 15 |  |  |  | 1.398 | JUL 26 | -0.739 | 1.3614 | 1926-07-01 | 16 | 1.397 | JUL 26 | 15 | 1.214 | 2006-07-27 | 15 | 0.739 | 1.54
11 | 59.7 |  | 56.63 | 64.4672 | 53.37 | 64 | 64.39 | 64.4 | 57.08 |  |  |  | 250 | 3.36 | 1993-09-05 | 12 | 3.036 | SEP 05 | 12 | 2.605 | SEP 5 | 11 | 2.59 | AUG 26 |  | 14 |  |  |  | 2.258 | AUG 26 | -3.36 | 3.2278 | Sep-05 | 13 | 4.912 | SEP 05 | 12 | 3.173 | 2006-08-26 | 14 | 2.258 | 4.912
12 | 67.4 |  | 61.58 | 69.9819 | 57.91 | 70 | 69.89 | 69.95 | 62 |  |  |  | 270 | 6.356 | 1993-11-25 | 13 | 6.641 | NOV 25 | 14 |  |  |  | 7.234 | OCT 16 |  | 14 | [6 empty] | 6.7639 | Oct-17 | 14 | 6.867 | OCT 16 | 14 |  |  |  | 6.356 | 7.234
13 | 70.1 |  | 63.7 | 70.8061 | 58.3 | 71 | 70.75 | 71.16 | 63.93 |  |  |  | 280 | 4.444 | 1993-10-17 | 13 | 4.631 | NOV 25 | 13 |  |  |  | 5.22 | OCT 16 |  | 14 | [6 empty] | 4.7861 | Oct-16 | 14 | 5.236 | OCT 16 | 14 |  |  |  | 4.444 | 5.236
14 | 67.3 |  | 61.46 | 65.6633 | 54.15 | 66 | 65.69 | 66.02 | 61.32 |  |  |  | 290 | 6.269 | 1993-01-13 | 13 | 6.555 | NOV 25 | 14 |  |  |  | 6.976 | NOV 25 |  | 14 | [6 empty] | 6.2028 | 1925-11-01 | 14 | 6.621 | NOV 25 | 14 |  |  |  | 6.2028 | 6.976
15 | 58.9 |  | 51.67 | 54.9214 | 45.38 | 55 | 55.03 | 55.16 | 51.08 |  |  |  | 300 | 3.404 | 1993-07-26 | 16 | 4.093 | JUL 26 | 17 |  |  |  | 4.657 | JUL 26 |  | 17 | [6 empty] | 4.2778 | 1926-07-01 | 17 | 4.929 | JUL 26 | 17 |  |  |  | 3.404 | 4.929
16 | 44.9 |  | 37.2 | 39.4869 | 32.7 | 40 | 39.61 | 39.73 | 36.25 |  |  |  | 310 | 2.848 | 1993-07-26 | 16 | 3.749 | JUN 30 | 17 |  |  |  | 4.164 | JUL 26 |  | 17 | [6 empty] | 3.5889 | 1926-07-01 | 17 | [6 empty] | 2.848 | 4.164
17 | 27.6 |  | 16.72 | 21.2906 | 17.7 | 21 | 21.42 | 21.6 | 15.95 |  |  |  | 320 | 5.701 | 1993-11-25 | 13 | 5.946 | NOV 25 | 14 |  |  |  | 6.553 | OCT 16 |  | 14 | [6 empty] | 6.1778 | Oct-17 | 14 | 6.141 | OCT 16 | 14 |  |  |  | 5.701 | 6.553
18 | 9 |  | 2.52 | 3.27 | 2.73 | 3 | 3.28 | 0 | 2.32 |  |  |  | 395 | 0 |  |  | 0.362 | JUL 26 | 18 | 0 |  |  | 0.394 | JUL 26 |  | 17 |  |  |  | 0.356 | JUL 26 | 18 | 0.3625 | 1926-07-01 | 18 | 0.345 | JUL 26 | 18 | 0.175 | 2006-07-27 | 17 | 0 | 0.394
19 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 400 | 0 |  |  | 0.581 | JUL 26 | 17 | 0.265 | JUL 27 | 17 | 0.666 | JUL 26 |  | 16 |  |  |  | 0.612 | JUL 26 | 17 | 0.61333 | 1926-07-01 | 17 | 0.572 | JUL 26 | 17 | 0.407 | 2006-07-27 | 16 | 0 | 0.666
20 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 410 | 0.035 | 1993-07-27 | 16 | 0.699 | JUL 26 | 17 | 0.413 | JUL 27 | 17 | 0.814 | JUL 26 |  | 15 |  |  |  | 0.724 | JUL 26 | -0.035 | 0.74306 | 1926-07-01 | 17 | 0.71 | JUL 26 | 17 | 0.559 | 2006-07-27 | 16 | 0.035 | 0.814
21 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 420 | 0.258 | 1993-07-27 | 15 | 0.923 | JUL 26 | 15 | 0.631 | JUL 27 | 15 | 1.047 | JUL 26 |  | 15 |  |  |  | 0.938 | JUL 26 | -0.258 | 0.93778 | 1926-07-01 | 16 | 0.921 | JUL 26 | 15 | 0.792 | 2006-07-27 | 15 | 0.258 | 1.047
22 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 430 | 1.493 | 1993-08-16 | 14 | 1.772 | AUG 26 | 14 | 1.427 | AUG 16 | 14 | 1.762 | JUL 26 |  | 15 |  |  |  | 1.575 | JUL 26 | -1.493 | 1.7983 | 1905-09-01 | 13 | 2.578 | SEP 05 | 12 | 2.113 | 2006-08-26 | 14 | 1.427 | 2.578
23 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 440 | 4.546 | 1993-10-17 | 13 | 4.424 | OCT 16 | 14 |  |  |  | 5.053 | OCT 16 |  | 14 | [6 empty] | 4.6861 | Oct-16 | 14 | 5.278 | OCT 17 | 14 |  |  |  | 4.424 | 5.278
24 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 800 | 0.585 | 1993-07-27 | 14 | 0.967 | AUG 16 | 14 | 0.743 | JUL 28 | 14 | 1.352 | JUL 27 |  | 14 |  |  |  | 1.028 | JUL 27 | -0.585 | 0.98278 | Aug-16 | 14 | 1.358 | SEP 05 | 12 | 1.267 | 2006-08-16 | 14 | 0.585 | 1.358
= | = | = | = | = | = | = | = | = | = |  |  |  | 810 | 1.852 | 1993-09-02 | 14 | 2.357 | AUG 26 | 14 |  |  |  | 2.991 | SEP 02 |  | 14 | [6 empty] | 2.3436 | Sep-02 | 14 | 2.862 | SEP 02 | 14 |  |  |  | 1.852 | 2.991
HOURLY INCIDENT SOLAR RADIATION, CLEAR DAY, JULY 27
CASE 600
SOUTH SURFACE
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA
HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
= | = | = | = | = | = | = | = | = | =
1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | FREE-FLOAT TEMPERATURE OUTPUT
2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | MAXIMUM ANNUAL HOURLY ZONE TEMPERATURE (C)
3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | CODENAME: |  | ESP |  |  | BLAST |  |  | DOE2 |  |  | SRES/SUN |  |  |  | SERIRES |  |  | S3PAS |  |  | TRNSYS |  |  | TASE |  |  | YOUR
4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | COUNTRY: |  | UK-DMU |  |  | USA/ITALY |  |  | USA |  |  | USA |  |  |  | UK-BRE |  |  | SPAIN |  |  | BEL/UK |  |  | FINLAND |  |  | DATA
5 | 0.5 |  | 0 | 0.16667 | 0.14 | 0 | 0.17 | 0.2 | 0 |  |  |  | CASE# | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE |  | HR | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE |  | TMP (C) | DATE | HR | TMP (C) | DATE | HR | MIN | MAX
6 | 17.9 |  | 20.11 | 27.8275 | 29.94 | 28 | 27.01 | 25.7 | 21.25 |  |  |  | 600FF | 64.929 | 1993-10-17 | 15 | 65.11 | OCT 16 | 15 | 69.5 | OCT 17 | 15 | 68.6 | OCT 16 |  | 15 |  |  |  | 64.9 | OCT 16 | 16 | 65.25 | Oct-17 | 16 | 65.25 | OCT 15 | 16 | 75.4 | 2012-10-17 | 15 | 64.9 | 69.5
7 | 58.6 |  | 70.22 | 77.3025 | 89.2 | 80 | 63 | 62.1 | 73.53 |  |  |  | 900FF | 41.812 | 1993-10-17 | 15 | 43.44 | SEP 02 | 16 | 42.7 | SEP 02 | 15 | 44.8 | SEP 02 |  | 15 |  |  |  | 43 | SEP 02 | 15 | 42.46 | Oct-17 | 15 | 43.17 | SEP 15 | 15 | 45.5 | 2012-10-17 | 15 | 41.812 | 44.8
8 | 100.4 |  | 108.13 | 99.9892 | 112.85 | 104 | 71.22 | 107.47 | 110.86 |  |  |  | 650FF | 63.236 | 1993-10-17 | 15 | 63.45 | OCT 16 | 15 | 68.2 | OCT 17 | 15 | 67 | OCT 16 |  | 15 |  |  |  | 63.3 | OCT 16 | 16 | 63.74 | Oct-17 | 16 | 63.82 | OCT 16 | 16 | 71.7 | 2012-10-17 | 15 | 63.236 | 68.2
9 | 205.9 |  | 219.58 | 211.0064 | 164.86 | 217 | 187.72 | 232.33 | 212.63 |  |  |  | 950FF | 35.54 | 1993-09-02 | 16 | 36.23 | SEP 02 | 16 | 35.9 | SEP 02 | 16 | 38.5 | SEP 02 |  | 15 |  |  |  | 36.1 | SEP 02 | 16 | 35.67 | Sep-02 | 15 | 37.58 | SEP 15 | 16 | 31.1 | 2012-09-02 | 15 | 35.54 | 38.5
10 | 326 |  | 343.67 | 331.0058 | 291.84 | 336 | 314.17 | 349.16 | 334.38 |  |  |  | 960 | 48.943 | 1993-10-17 | 15 | 48.88 | OCT 06 | 15 | 49 | OCT 17 | 15 | 51 | OCT 17 |  | 15 |  |  |  | 50.2 | OCT 17 | 15 | 55.34 | Oct-17 | 15 | 48.92 | OCT 15 | 15 | 51.6 | 2012-10-17 |  | 48.88 | 55.34
11 | 415.1 |  | 435.54 | 418.1717 | 389.26 | 423 | 404.44 | 430.22 | 425.82 |  |  |  | MINIMUM ANNUAL HOURLY ZONE TEMPERATURE (C)
12 | 454.8 |  | 475.37 | 454.9942 | 437.2 | 459 | 443.61 | 459.85 | 465.2 |  |  |  | CODENAME: |  | ESP |  |  | BLAST |  |  | DOE2 |  |  | SRES/SUN |  |  |  | SERIRES |  |  | S3PAS |  |  | TRNSYS |  |  | TASE |  |  | YOUR
13 | 455.6 |  | 488.49 | 464.5689 | 455.75 | 469 | 452.5 | 462.28 | 478.4 |  |  |  | COUNTRY: |  | UK-DMU |  |  | USA/ITALY |  |  | USA |  |  | USA |  |  |  | UK-BRE |  |  | SPAIN |  |  | BEL/UK |  |  | FINLAND |  |  | DATA
14 | 408.6 |  | 443.66 | 413.6364 | 413.67 | 418 | 400.56 | 404.57 | 433.75 |  |  |  | CASE# | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE |  | HR | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE |  | TMP (C) | DATE | HR | TMP (C) | DATE | HR | MIN | MAX
15 | 321.2 |  | 367.07 | 334.2839 | 341.53 | 340 | 316.94 | 319.26 | 357.6 |  |  |  | 600FF | -15.565 | 1993-01-04 | 7 | -17.05 | JAN 04 | 8 | -18.8 | JAN 04 | 8 | -18 | JAN 04 |  | 7 |  |  |  | -17.8 | JAN 04 | 8 | -17.81 | Jan-04 | 7 | -18.47 | JAN 08 | 9 | -17.7 | 2006-01-04 | 8 | -18.8 | -15.565
16 | 200.6 |  | 246.71 | 211.9439 | 223.71 | 218 | 188.89 | 193.61 | 238.77 |  |  |  | 900FF | -1.647 | 1993-01-04 | 8 | -3.15 | JAN 04 | 8 | -4.3 | JAN 04 | 8 | -4.5 | JAN 04 |  | 8 |  |  |  | -4 | JAN 04 | 8 | -6.38 | Jan-04 | 8 | -5.64 | JAN 08 | 9 | -2 | 2006-01-04 | 8 | -6.38 | -1.647
17 | 102.3 |  | 119.19 | 111.7408 | 105.72 | 115 | 86.03 | 132.3 | 121.87 |  |  |  | 650FF | -22.564 | 1993-01-04 | 6 | -22.96 | JAN 04 | 7 | -21.6 | JAN 04 | 2 | -23 | JAN 04 |  | 2 |  |  |  | -22.9 | JAN 04 | 2 | -22.83 | Jan-04 | 7 | -22.91 | JAN 02 | 23 | -21 | 2006-01-04 | 2 | -23 | -21.6
18 | 78.8 |  | 68.86 | 73.0792 | 68.47 | 74 | 69.78 | 76.6 | 71.71 |  |  |  | 950FF | -19.484 | 1993-01-04 | 6 | -20.04 | JAN 04 | 7 | -18.6 | JAN 04 | 7 | -19.7 | JAN 04 |  | 7 |  |  |  | -20.2 | JAN 04 | 7 | -19.34 | Jan-04 | 7 | -19.96 | JAN 07 | 22 | -17.8 | 2006-01-04 | 7 | -20.2 | -18.6
19 | 37.1 |  | 19.75 | 17.7025 | 14.35 | 18 | 17.61 | 18.05 | 20.51 |  |  |  | 960 | 2.729 | 1993-02-06 | 6 | 1.63 | FEB 06 | 7 | 3.9 | FEB 06 | 7 | 3.1 | FEB 06 |  | 7 |  |  |  | 1.4 | FEB 06 | 6 | -2.82 | Jan-04 | 8 | -0.39 | FEB 05 | 7 | 6 | 2006-02-06 | 7 | -2.82 | 3.9
20 | 1.1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | AVERAGE ANNUAL HOURLY ZONE TEMPERATURE (C)
21 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | CODENAME: |  | ESP |  |  | BLAST |  |  | DOE2 |  |  | SRES/SUN |  |  |  | SERIRES |  |  | S3PAS |  |  | TRNSYS |  |  | TASE |  |  | YOUR
22 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | COUNTRY: |  | UK-DMU |  |  | USA/ITALY |  |  | USA |  |  | USA |  |  |  | UK-BRE |  |  | SPAIN |  |  | BEL/UK |  |  | FINLAND |  |  | DATA
23 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | CASE# | TMP (C) |  |  | TMP (C) |  |  | TMP (C) |  |  | TMP (C) |  |  |  | TMP (C) |  |  | TMP (C) |  |  | TMP (C) |  |  | TMP (C) |  |  | TMP (C) | DATE | HR | MIN | MAX
24 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 600FF | 25.126 |  |  | 25.43 |  |  | 24.6 |  |  | 25.48 |  |  |  | 25.93 |  |  | 25.2 |  |  | 24.49 |  |  | 24.22 |  |  | 26.993 |  |  | 24.22 | 25.93
= | = | = | = | = | = | = | = | = | = |  |  |  | 900FF | 25.453 |  |  | 25.93 |  |  | 24.7 |  |  | 25.49 |  |  |  | 25.72 |  |  | 25.2 |  |  | 24.47 |  |  | 24.45 |  |  | 27.0563 |  |  | 24.45 | 25.93
[13 empty] | 650FF | 18.234 |  |  | 18.69 |  |  | 19.1 |  |  | 18.96 |  |  |  | 19.62 |  |  | 18.4 |  |  | 17.99 |  |  | 18.36 |  |  | 20.4281 |  |  | 17.99 | 19.62
[13 empty] | 950FF | 14.14 |  |  | 14.26 |  |  | 14.3 |  |  | 14.97 |  |  |  | 14.29 |  |  | 14 |  |  | 14.53 |  |  | 14.64 |  |  | 15.0742 |  |  | 14 | 14.97
[13 empty] | 960 | 27.49 |  |  | 27.72 |  |  | 28 |  |  | 28.69 |  |  |  | 28.54 |  |  | 28 |  |  | 28.96 |  |  | 26.43 |  |  | 30.0216 |  |  | 26.43 | 28.96
HOURLY INCIDENT SOLAR RADIATION, CLEAR DAY, JULY 27
CASE 600
WEST SURFACE
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA
HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
= | = | = | = | = | = | = | = | = | =
1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0.4 |  | 0 | 0.16667 | 0.14 | 0 | 0.17 | 0.2 | 0
6 | 17.9 |  | 19.96 | 27.8275 | 29.94 | 28 | 27.01 | 25.7 | 21.16
7 | 58.5 |  | 65.86 | 77.3025 | 89.2 | 80 | 63 | 62.1 | 69.31
8 | 91.8 |  | 97.11 | 99.9892 | 112.85 | 104 | 71.22 | 72 | 100.74
9 | 113.7 |  | 116.89 | 120.0506 | 121.41 | 125 | 85.58 | 92.6 | 119.05
10 | 131.2 |  | 128.97 | 134.9631 | 123.51 | 140 | 98.03 | 112.8 | 130.25
11 | 145.7 |  | 138.05 | 149.5847 | 125.06 | 154 | 109.14 | 136.75 | 139.62
12 | 153.8 |  | 141.34 | 153.1336 | 121.07 | 157 | 113.06 | 150.9 | 142.54
13 | 267.7 |  | 243.51 | 266.4489 | 117.94 | 270 | 235.17 | 382.5 | 244.31
14 | 464.8 |  | 462.83 | 461.2772 | 333.68 | 463 | 453.89 | 576.81 | 461.98
15 | 635.1 |  | 664.62 | 635.5103 | 525.35 | 635 | 652.5 | 744.52 | 662.1
16 | 738.3 |  | 786.35 | 719.3256 | 634.59 | 715 | 762.78 | 807.29 | 782.66
17 | 623.9 |  | 649.05 | 502.7889 | 478.44 | 497 | 568.33 | 541.68 | 651.77
18 | 296.9 |  | 243.11 | 141.2425 | 140.3 | 139 | 158 | 145.25 | 231.93
19 | 68.8 |  | 43.19 | 25.2472 | 21.96 | 24 | 26.6 | 24.9 | 38.33
20 | 1.6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
= | = | = | = | = | = | = | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 600FF JAN 4
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA
HOUR | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C)
= | = | = | = | = | = | = | = | = | =
1 | -8.88 | -12.0409 | -12.3 | -12.21 |  | -12.1 | -12.02 | -13.04 | -10.4
2 | -10.48 | -13.523 | -14.1 | -13.8 |  | -13.7 | -13.5 | -14.59 | -12.4
3 | -11.76 | -14.4018 | -15.4 | -14.9 |  | -14.7 | -14.7 | -15.65 | -13.8
4 | -12.75 | -15.2598 | -16.3 | -15.79 |  | -15.6 | -15.65 | -16.46 | -14.9
5 | -13.69 | -15.9988 | -17.1 | -16.55 |  | -16.4 | -16.47 | -17.16 | -15.8
6 | -14.49 | -16.3983 | -17.9 | -17.2 |  | -17 | -17.14 | -17.79 | -16.7
7 | -15.15 | -17.0108 | -18.5 | -17.74 |  | -17.6 | -17.7 | -18.32 | -17.4
8 | -15.63 | -17.0531 | -18.8 | -17.85 |  | -17.8 | -17.59 | -18.47 | -17.7
9 | -14.63 | -13.7364 | -14.7 | -14.88 |  | -14.6 | -13.46 | -15.47 | -13.3
10 | -10.03 | -7.9937 | -7.8 | -9.07 |  | -8.9 | -7.099 | -9.56 | -5.7
11 | -2.2 | 2.6043 | 3.2 | 1.01 |  | 1 | 3.657 | 0.49 | 6.1
12 | 8.84 | 12.2151 | 13.4 | 11.21 |  | 10.7 | 13.49 | 10.39 | 17.2
13 | 18.96 | 20.8602 | 22.3 | 20.03 |  | 19.2 | 21.77 | 18.75 | 26.8
14 | 27.19 | 27.532 | 29.5 | 27.27 |  | 26.1 | 28.26 | 25.48 | 34.6
15 | 33.22 | 31.3289 | 33.8 | 31.34 |  | 29.8 | 32.09 | 29.21 | 39.4
16 | 35.51 | 31.0594 | 33.5 | 31.47 |  | 29.7 | 32.16 | 28.97 | 39.4
17 | 31.46 | 24.2801 | 27 | 25.96 |  | 23.9 | 25.71 | 22.58 | 32.5
18 | 23.99 | 17.4634 | 19.7 | 18.96 |  | 17.6 | 18.84 | 15.59 | 24.8
19 | 18.08 | 12.0529 | 13.7 | 13.04 |  | 12.2 | 13.1 | 10.2 | 18.4
20 | 13.02 | 7.5727 | 8.7 | 8.31 |  | 7.8 | 8.408 | 6.02 | 13
21 | 8.87 | 3.5981 | 4.4 | 4.27 |  | 4 | 4.387 | 2.39 | 8.3
22 | 5.12 | 0.51861 | 1 | 0.99 |  | 0.9 | 0.9659 | -0.59 | 4.5
23 | 2.03 | -1.9381 | -1.9 | -1.66 |  | -1.7 | -1.781 | -3.04 | 1.2
24 | -1.03 | -4.0741 | -4.4 | -3.92 |  | -3.9 | -4.032 | -5.14 | -1.5
= | = | = | = | = | = | = | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 900FF JAN 4
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA
HOUR | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C)
= | = | = | = | = | = | = | = | = | =
1 | 1.61 | -0.17002 | -0.9 | -1.31 |  | -0.7 | -3.455 | -2.68 | 1.5
2 | 0.93 | -0.79333 | -1.6 | -1.97 |  | -1.4 | -3.986 | -3.33 | 0.8
3 | 0.49 | -1.0908 | -2 | -2.37 |  | -1.8 | -4.395 | -3.72 | 0.3
4 | 0.07 | -1.6745 | -2.5 | -2.81 |  | -2.3 | -4.8 | -4.1 | -0.1
5 | -0.41 | -2.0414 | -2.9 | -3.25 |  | -2.7 | -5.216 | -4.51 | -0.6
6 | -0.87 | -2.4328 | -3.4 | -3.68 |  | -3.2 | -5.604 | -4.93 | -1.1
7 | -1.27 | -2.9702 | -3.9 | -4.1 |  | -3.6 | -5.984 | -5.34 | -1.6
8 | -1.64 | -3.1541 | -4.3 | -4.4 |  | -4 | -6.078 | -5.64 | -2
9 | -1.54 | -2.3938 | -3.3 | -3.45 |  | -3.2 | -4.717 | -4.59 | -0.9
10 | -0.4 | -1.0924 | -1.6 | -1.6 |  | -1.7 | -2.977 | -2.64 | 0.9
11 | 1.59 | 1.5953 | 1.2 | 1.66 |  | 0.9 | 0.2494 | 0.75 | 3.9
12 | 4.4 | 3.6249 | 3.5 | 4.4 |  | 3.1 | 2.539 | 3.26 | 6.3
13 | 6.72 | 5.6203 | 5.5 | 6.56 |  | 5.1 | 4.382 | 4.99 | 8.5
14 | 8.66 | 7.3237 | 7.2 | 8.39 |  | 6.8 | 5.853 | 6.51 | 10.3
15 | 10.02 | 8.2691 | 8 | 9.04 |  | 7.6 | 6.614 | 7.11 | 11.2
16 | 10.4 | 8.1513 | 7.9 | 8.58 |  | 7.4 | 6.333 | 6.68 | 11
17 | 9.41 | 6.5309 | 6.2 | 6.44 |  | 5.8 | 4.204 | 4.24 | 9.2
18 | 7.66 | 5.2506 | 4.7 | 4.43 |  | 4.4 | 2.869 | 2.45 | 7.7
19 | 6.74 | 4.5191 | 3.8 | 3.37 |  | 3.6 | 2.107 | 1.71 | 6.8
20 | 6 | 3.8832 | 3.2 | 2.73 |  | 3 | 1.581 | 1.32 | 6.1
21 | 5.41 | 3.2206 | 2.7 | 2.11 |  | 2.4 | 1.047 | 0.82 | 5.5
22 | 4.74 | 2.8485 | 2.2 | 1.66 |  | 1.9 | 0.5504 | 0.42 | 5
23 | 4.2 | 2.4745 | 1.7 | 1.26 |  | 1.5 | 0.1517 | 0.05 | 4.5
24 | 3.66 | 1.8994 | 1.2 | 0.83 |  | 1 | -0.238 | -0.34 | 4
= | = | = | = | = | = | = | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 650FF JULY 27
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA
HOUR | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C)
= | = | = | = | = | = | = | = | = | =
1 | 22.58 | 22.223 | 21.8 | 22.37 |  | 22.4 | 22.69 | 22.26 | 22
2 | 21.15 | 21.1546 | 20.8 | 21.19 |  | 21.2 | 21.33 | 21.11 | 21
3 | 20.23 | 20.3068 | 19.9 | 20.33 |  | 20.4 | 20.41 | 20.28 | 20.1
4 | 19.45 | 19.5218 | 19.1 | 19.54 |  | 19.5 | 19.61 | 19.49 | 19.3
5 | 18.95 | 19.295 | 18.8 | 19.21 |  | 19.2 | 19.16 | 19.14 | 19
6 | 19.24 | 19.9144 | 19.5 | 19.86 |  | 19.9 | 19.6 | 19.81 | 19.7
7 | 21.16 | 22.5284 | 22.2 | 22.51 |  | 22.5 | 21.68 | 22.49 | 22.4
8 | 23.56 | 25.0275 | 24 | 24.89 |  | 24.7 | 23.47 | 24.81 | 24.8
9 | 25.67 | 28.3327 | 27.3 | 28.29 |  | 27.9 | 26.38 | 28.04 | 28.5
10 | 28.91 | 31.8311 | 31.5 | 32.42 |  | 31.7 | 30.35 | 32.11 | 32.8
11 | 32.8 | 35.825 | 36.2 | 37.12 |  | 36.2 | 34.82 | 36.54 | 37.6
12 | 37.49 | 40.1973 | 41.1 | 42.08 |  | 40.8 | 39.38 | 41.15 | 42.6
13 | 41.94 | 43.9026 | 45.4 | 46.46 |  | 45 | 43.48 | 45.03 | 46.8
14 | 45.43 | 46.3464 | 48.4 | 49.69 |  | 48.1 | 46.14 | 47.65 | 49.8
15 | 47.41 | 47.6362 | 50.1 | 51.3 |  | 49.6 | 47.4 | 49.04 | 51.6
16 | 47.84 | 47.6029 | 50.1 | 51.28 |  | 49.7 | 47.33 | 49.28 | 51.9
17 | 47.01 | 47.3406 | 49.1 | 50.46 |  | 49.1 | 46.71 | 48.73 | 51.1
18 | 45.53 | 45.3964 | 46.8 | 48.37 |  | 47.2 | 45.28 | 46.58 | 48.8
19 | 37.37 | 33.7034 | 34 | 35.39 |  | 35.1 | 33.1 | 34.91 | 34.7
20 | 31.57 | 30.8664 | 30.9 | 31.63 |  | 31.6 | 30.49 | 30.69 | 31.4
21 | 29.05 | 28.695 | 28.5 | 29.12 |  | 29.2 | 28.55 | 28.81 | 28.9
22 | 26.92 | 26.4968 | 26.3 | 26.83 |  | 26.9 | 26.66 | 26.66 | 26.6
23 | 25.52 | 25.6844 | 25.4 | 25.87 |  | 25.9 | 25.55 | 25.69 | 25.6
24 | 23.84 | 24.0543 | 23.7 | 24.19 |  | 24.2 | 24.26 | 24.1 | 23.9
= | = | = | = | = | = | = | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 950FF JULY 27
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA
HOUR | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C)
= | = | = | = | = | = | = | = | = | =
1 | 24.36 | 24.5601 | 24.2 | 24.52 |  | 24.6 | 25.28 | 24.53 | 24.6
2 | 23.46 | 23.8963 | 23.5 | 23.81 |  | 23.9 | 24.47 | 23.8 | 23.9
3 | 22.86 | 23.3126 | 22.9 | 23.22 |  | 23.3 | 23.87 | 23.23 | 23.3
4 | 22.27 | 22.6823 | 22.3 | 22.6 |  | 22.7 | 23.26 | 22.6 | 22.7
5 | 21.86 | 22.4527 | 22 | 22.32 |  | 22.4 | 22.87 | 22.27 | 22.4
6 | 22.01 | 22.8128 | 22.5 | 22.77 |  | 22.8 | 23.06 | 22.67 | 22.8
7 | 23.32 | 24.6678 | 24.3 | 24.73 |  | 24.6 | 24.38 | 24.55 | 24.6
8 | 25.62 | 27.3586 | 26.5 | 27.59 |  | 27.1 | 27.21 | 27.57 | 27.2
9 | 27.59 | 28.3229 | 27.5 | 29.09 |  | 28.2 | 27.98 | 29.42 | 28.3
10 | 28.82 | 29.2074 | 28.6 | 30.5 |  | 29.3 | 29.11 | 30.68 | 29.4
11 | 29.84 | 30.1901 | 29.8 | 31.98 |  | 30.5 | 30.31 | 31.91 | 30.7
12 | 30.98 | 31.3352 | 31.1 | 33.56 |  | 31.7 | 31.53 | 33.27 | 32
13 | 32.08 | 32.1879 | 32.2 | 34.79 |  | 32.8 | 32.55 | 34.27 | 33.1
14 | 32.85 | 32.845 | 33 | 35.65 |  | 33.6 | 33.15 | 34.9 | 33.9
15 | 33.33 | 33.1198 | 33.4 | 35.96 |  | 34 | 33.37 | 35.19 | 34.3
16 | 33.55 | 33.2478 | 33.5 | 35.82 |  | 34.1 | 33.38 | 35.28 | 34.5
17 | 33.44 | 33.3523 | 33.5 | 35.61 |  | 34.1 | 33.37 | 35.3 | 34.5
18 | 33.23 | 32.996 | 33.1 | 34.93 |  | 33.7 | 33.16 | 34.71 | 34
19 | 30.92 | 30.203 | 30 | 30.96 |  | 30.6 | 30.43 | 30.74 | 30.4
20 | 29.17 | 29.3534 | 29.1 | 29.79 |  | 29.6 | 29.61 | 29.38 | 29.5
21 | 28.31 | 28.5416 | 28.2 | 28.83 |  | 28.7 | 28.89 | 27.64 | 28.6
22 | 27.27 | 27.3759 | 27.1 | 27.59 |  | 27.5 | 27.93 | 27.46 | 27.5
23 | 26.62 | 27.174 | 26.8 | 27.28 |  | 27.3 | 27.42 | 27.1 | 27.2
24 | 25.54 | 25.9805 | 25.7 | 26.1 |  | 26.1 | 26.59 | 26.02 | 26
= | = | = | = | = | = | = | = | = | =
HOURLY HEATING & COOLING LOAD DATA
CASE 600 JAN 4
[USE (-) FOR COOLING]
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA
HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | =
1 | 3.25 | 3.8018 | 3.926 | 4.127 |  | 3.925 | 3.7667 | 4.225 | 3.645
2 | 3.409 | 3.9109 | 4.035 | 4.258 |  | 4.037 | 3.8667 | 4.354 | 3.75
3 | 3.392 | 3.8658 | 4.013 | 4.229 |  | 4.003 | 3.9028 | 4.321 | 3.74
4 | 3.381 | 3.9196 | 4.041 | 4.22 |  | 4.001 | 3.8944 | 4.308 | 3.765
5 | 3.417 | 3.9401 | 4.045 | 4.22 |  | 4.001 | 3.9167 | 4.303 | 3.767
6 | 3.432 | 3.9258 | 4.036 | 4.221 |  | 4.001 | 3.9306 | 4.307 | 3.758
7 | 3.421 | 3.937 | 4.045 | 4.222 |  | 4.001 | 3.9306 | 4.307 | 3.764
8 | 3.337 | 3.7023 | 3.857 | 4.09 |  | 3.898 | 3.7528 | 4.167 | 3.558
9 | 2.767 | 2.6752 | 2.559 | 2.902 |  | 2.706 | 2.4228 | 2.912 | 2.157
10 | 1.497 | 1.3833 | 0.843 | 1.275 |  | 1.151 | 0.79667 | 1.466 | 0.335
11 | 0.151 | 0 | 0 | 0 |  | 0 | -0.034833 | 0 | -0.194
12 | -0.771 | -1.2242 | -1.552 | -1.066 |  | -1.036 | -1.435 | -0.424 | -2.459
13 | -2.66 | -2.4871 | -2.854 | -2.586 |  | -2.498 | -2.7203 | -2.364 | -3.689
14 | -3.575 | -2.9579 | -3.398 | -3.225 |  | -3.085 | -3.1556 | -2.759 | -4.172
15 | -3.527 | -2.631 | -3.116 | -2.826 |  | -2.637 | -2.8444 | -2.431 | -3.874
16 | -2.435 | -1.3491 | -1.82 | -1.552 |  | -1.345 | -1.7158 | -1.14 | -2.522
17 | -0.356 | 0 | 0 | -0.001 |  | 0 | 0 | 0 | 0
18 | 0.243 | 0.95017 | 0.775 | 0.8 |  | 0.88 | 0.77306 | 1.292 | 0.203
19 | 1.53 | 2.3779 | 2.232 | 2.34 |  | 2.331 | 2.3014 | 2.445 | 1.823
20 | 2.321 | 2.8665 | 2.933 | 2.988 |  | 2.949 | 2.9667 | 2.941 | 2.603
21 | 2.641 | 3.2126 | 3.323 | 3.365 |  | 3.309 | 3.2778 | 3.405 | 3.029
22 | 2.899 | 3.2845 | 3.487 | 3.532 |  | 3.347 | 3.4611 | 3.594 | 3.214
23 | 3.017 | 3.3307 | 3.514 | 3.605 |  | 3.494 | 3.5 | 3.696 | 3.256
24 | 3.008 | 3.388 | 3.561 | 3.663 |  | 3.527 | 3.4722 | 3.769 | 3.304
= | = | = | = | = | = | = | = | = | =
HOURLY HEATING & COOLING LOAD DATA
CASE 900 JAN 4
[USE (-) FOR COOLING]
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA
HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | = | = | = | = | = | = | = | = | =
1 | 2.441 | 3.1039 | 3.101 | 3.394 |  | 3.208 | 3.0806 | 3.4 | 2.774
2 | 2.606 | 3.1986 | 3.237 | 3.54 |  | 3.349 | 3.2028 | 3.547 | 2.912
3 | 2.623 | 3.2044 | 3.279 | 3.557 |  | 3.382 | 3.2778 | 3.573 | 2.968
4 | 2.667 | 3.3056 | 3.377 | 3.613 |  | 3.447 | 3.3306 | 3.629 | 3.064
5 | 2.744 | 3.3669 | 3.446 | 3.666 |  | 3.506 | 3.4167 | 3.687 | 3.132
6 | 2.8 | 3.3993 | 3.498 | 3.715 |  | 3.558 | 3.4694 | 3.747 | 3.187
7 | 2.834 | 3.4532 | 3.557 | 3.76 |  | 3.605 | 3.5167 | 3.797 | 3.248
8 | 2.837 | 3.376 | 3.516 | 3.749 |  | 3.608 | 3.4639 | 3.794 | 3.21
9 | 2.641 | 2.8981 | 2.974 | 3.17 |  | 3.08 | 2.8333 | 3.168 | 2.636
10 | 2.12 | 2.3463 | 2.202 | 2.32 |  | 2.348 | 2.0561 | 2.449 | 1.828
11 | 1.502 | 1.3981 | 1.034 | 0.949 |  | 1.117 | 0.79333 | 1.293 | 0.588
12 | 0.676 | 0.37698 | 0.232 | 0.101 |  | 0.3 | 0.037278 | 0.619 | 0
13 | 0.074 | 0 | 0 | 0 |  | 0 | 0 | 0.136 | 0
14 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
15 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
16 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0.088 | 0
17 | 0.027 | 0.12409 | 0 | 0.277 |  | 0.143 | 0.13494 | 1.198 | 0
18 | 0.413 | 0.76691 | 0.739 | 1.216 |  | 0.91 | 0.76444 | 1.602 | 0.036
19 | 0.804 | 1.3064 | 1.14 | 1.608 |  | 1.281 | 1.1986 | 1.805 | 0.52
20 | 1.068 | 1.613 | 1.429 | 1.816 |  | 1.543 | 1.4589 | 1.943 | 0.858
21 | 1.269 | 1.9255 | 1.7 | 2.038 |  | 1.81 | 1.7008 | 2.121 | 1.158
22 | 1.502 | 2.1361 | 1.894 | 2.174 |  | 1.995 | 1.9342 | 2.227 | 1.38
23 | 1.658 | 2.2208 | 2.028 | 2.293 |  | 2.154 | 2.0922 | 2.338 | 1.547
24 | 1.749 | 2.3111 | 2.193 | 2.423 |  | 2.311 | 2.2267 | 2.458 | 1.735
= | = | = | = | = | = | = | = | = | =
FREE-FLOAT CASES
HOURLY ANNUAL ZONE TEMPERATURE BIN DATA
CASE 900FF
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA
TEMP (C) | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS
= | = | = | = | = | = | = | = | = | =
-50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
-6 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 | 0
-5 | 0 | 0 | 1 | 2 | 0 | 0 | 3 | 4 | 0
-4 | 0 | 1 | 3 | 3 | 4 | 4 | 6 | 5 | 0
-3 | 0 | 3 | 7 | 5 | 2 | 3 | 6 | 7 | 0
-2 | 3 | 5 | 5 | 7 | 7 | 8 | 12 | 10 | 3
-1 | 3 | 6 | 10 | 7 | 5 | 5 | 13 | 18 | 7
0 | 8 | 10 | 18 | 19 | 18 | 18 | 12 | 20 | 6
1 | 6 | 17 | 17 | 19 | 10 | 20 | 12 | 12 | 8
2 | 18 | 14 | 18 | 13 | 20 | 14 | 20 | 16 | 15
3 | 18 | 19 | 19 | 15 | 15 | 19 | 18 | 25 | 16
4 | 17 | 14 | 20 | 23 | 20 | 21 | 20 | 24 | 19
5 | 18 | 25 | 30 | 28 | 24 | 27 | 26 | 27 | 17
6 | 22 | 19 | 25 | 29 | 27 | 30 | 34 | 35 | 19
7 | 31 | 33 | 37 | 28 | 28 | 33 | 29 | 45 | 29
8 | 30 | 34 | 51 | 46 | 33 | 46 | 44 | 59 | 26
9 | 42 | 42 | 59 | 62 | 57 | 61 | 55 | 73 | 29
10 | 51 | 54 | 84 | 69 | 53 | 71 | 57 | 118 | 50
11 | 67 | 72 | 107 | 111 | 89 | 116 | 95 | 134 | 57
12 | 90 | 115 | 139 | 137 | 112 | 127 | 127 | 138 | 75
13 | 115 | 137 | 153 | 141 | 142 | 157 | 143 | 173 | 95
14 | 156 | 159 | 158 | 154 | 151 | 160 | 162 | 183 | 120
15 | 172 | 165 | 206 | 188 | 178 | 207 | 183 | 234 | 140
16 | 215 | 198 | 239 | 232 | 195 | 224 | 234 | 274 | 154
17 | 244 | 245 | 274 | 253 | 248 | 255 | 273 | 298 | 188
18 | 293 | 277 | 350 | 301 | 266 | 315 | 296 | 342 | 226
19 | 338 | 317 | 322 | 336 | 332 | 347 | 356 | 352 | 252
20 | 387 | 365 | 375 | 342 | 344 | 352 | 346 | 331 | 324
21 | 398 | 358 | 392 | 362 | 361 | 366 | 388 | 334 | 336
22 | 385 | 372 | 364 | 329 | 376 | 349 | 380 | 343 | 335
23 | 396 | 341 | 370 | 348 | 366 | 357 | 366 | 349 | 375
24 | 380 | 368 | 381 | 352 | 341 | 341 | 401 | 338 | 414
25 | 417 | 357 | 432 | 361 | 397 | 392 | 404 | 404 | 362
26 | 455 | 389 | 431 | 373 | 426 | 399 | 436 | 393 | 402
27 | 459 | 420 | 415 | 415 | 418 | 403 | 465 | 396 | 400
28 | 445 | 463 | 452 | 390 | 446 | 440 | 412 | 411 | 430
29 | 459 | 419 | 410 | 405 | 432 | 396 | 408 | 391 | 441
30 | 415 | 396 | 404 | 418 | 422 | 395 | 398 | 362 | 427
31 | 406 | 393 | 342 | 401 | 389 | 360 | 335 | 342 | 448
32 | 369 | 348 | 349 | 341 | 334 | 337 | 348 | 322 | 404
33 | 339 | 315 | 309 | 330 | 338 | 306 | 310 | 291 | 370
34 | 277 | 321 | 242 | 285 | 311 | 306 | 297 | 266 | 342
35 | 230 | 303 | 197 | 246 | 262 | 256 | 202 | 210 | 318
36 | 191 | 254 | 185 | 213 | 203 | 217 | 197 | 169 | 275
37 | 164 | 195 | 136 | 156 | 189 | 166 | 161 | 151 | 189
38 | 108 | 175 | 92 | 146 | 137 | 138 | 97 | 132 | 189
39 | 71 | 99 | 74 | 112 | 103 | 97 | 86 | 85 | 154
40 | 37 | 66 | 35 | 90 | 71 | 57 | 48 | 59 | 109
41 | 15 | 32 | 16 | 58 | 35 | 31 | 22 | 32 | 80
42 | 0 | 25 | 5 | 36 | 18 | 10 | 11 | 20 | 47
43 | 0 | 5 | 0 | 18 | 5 | 1 | 2 | 1 | 23
44 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 13
45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
= | = | = | = | = | ======== | = | = | = | =
= | = | = | = | = | ======== | = | = | = | =
= | = | = | = | = | = | = | = | = | =
= | = | = | = | = | = | = | = | = | =