## A
RESULTS5-4.XLS |  |  |  | INSTRUCTIONS
Output spreadsheet for HVAC BESTEST |  |  |  | Import data so that Cell A1 of Sec5-4out.XLS is in A1 of Sheet "YD" (your data)
Check that the first value (TOTAL FURNACE LOAD GJ for HE100) lands in YD!B20.
Data should land in "YD" cells as tabulated below. Your data will then appear in columns E, I and M of Sheet A
and in rightmost column of each table on sheet Q. Chart update of "your data" is not automated.
See RESULTS5-4.DOC for spreadsheet navigation.
Cases | FURNACE LOAD | FURNACE INPUT | FUEL CONSUMPTION | FAN ENERGY | MEAN TEMP. | MAX TEMP. | MIN TEMP.
CASE HE100 | #VALUE! | #VALUE! | #VALUE! | - | - | - | -
CASE HE110 | #VALUE! | #VALUE! | #VALUE! | - | - | - | -
CASE HE120 | #VALUE! | #VALUE! | #VALUE! | - | - | - | -
CASE HE130 | #VALUE! | #VALUE! | #VALUE! | - | - | - | -
CASE HE140 | #VALUE! | #VALUE! | #VALUE! | - | - | - | -
CASE HE150 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | -
CASE HE160 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | -
CASE HE170 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | - | - | -
CASE HE210 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
CASE HE220 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
CASE HE230 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
| TOTAL FURNACE LOAD |  |  |  | TOTAL FURNACE INPUT |  |  |  | FUEL CONSUMPTION
| GJ |  |  |  | GJ |  |  |  | m3/s
Cases | ESP-r /HOT3000 | EnergyPlus | DOE-2.1E | Your | ESP-r /HOT3000 | EnergyPlus | DOE-2.1E | Your | ESP-r /HOT3000 | EnergyPlus | DOE-2.1E | Your
| NRCAN | NRCAN | NRCAN | Software | NRCAN | NRCAN | NRCAN | Software | NRCAN | NRCAN | NRCAN | Software
CASE HE100 | 77.94 | 77.75 | 77.73 | 76.0297 | 77.74 | 77.7133 | 78.3043 | 76.6269 | 0.000263 | 0.000263 | 0.000265 | 0.00025932
CASE HE110 | 77.94 | 77.75 | 77.73 | 76.0297 | 96.9201 | 97.2156 | 97.8065 | 95.7836 | 0.000328 | 0.000329 | 0.000331 | 0.00032415
CASE HE120 | 31.25 | 31.1 | 31.12 | 30.2887 | 38.4134 | 38.2657 | 38.4134 | 37.5032 | 0.00013 | 0.0001295 | 0.00013 | 0.00012692
CASE HE130 | 0 | 0 | 0.15804 | 0.12028 | 0 | 0 | 0.14479 | 0.099176 | 0 | 0 | 4.9e-07 | 3.3563e-07
CASE HE140 | 31.26 | 31.1 | 31.07 | 30.5303 | 39.0044 | 39.0044 | 38.7089 | 38.0128 | 0.000132 | 0.000132 | 0.000131 | 0.00012864
CASE HE150 | 29.88 | 29.59 | 29.55 | 28.993 | 37.2315 | 36.936 | 36.6405 | 36.0957 | 0.000126 | 0.000125 | 0.000124 | 0.00012216
CASE HE160 | 31.26 | 30.46 | 30.48 | 29.9247 | 38.118 | 38.118 | 37.8225 | 37.2457 | 0.000129 | 0.000129 | 0.000128 | 0.00012605
CASE HE170 | 29.88 | 29.59 | 29.55 | 28.993 | 37.2315 | 36.936 | 36.6405 | 36.0957 | 0.000126 | 0.000125 | 0.000124 | 0.00012216
CASE HE210 | 41.36 | 42.04 | 42.08 | 41.1695 | 50.5284 | 52.0059 | 52.3014 | 51.2474 | 0.000171 | 0.000176 | 0.000177 | 0.00017343
CASE HE220 | 39.41 | 39.87 | 39.87 | 38.9169 | 47.8691 | 49.3465 | 49.3465 | 48.4051 | 0.000162 | 0.000167 | 0.000167 | 0.00016381
CASE HE230 | 34.32 | 34.59 | 34.49 | 33.9518 | 41.3683 | 42.5503 | 43.1412 | 42.6793 | 0.00014 | 0.000144 | 0.000146 | 0.00014444
FAN ENERGY (BOTH FANS)
kWh
Cases | ESP-r /HOT3000 | EnergyPlus | DOE-2.1E | Your
| NRCAN | NRCAN | NRCAN | Software
CASE HE150 | 432 | 433.3 | 432.1 | 432
CASE HE160 | 170.2 | 172.2 | 172.3 | 169
CASE HE170 | 473.4 | 473.1 | 473.3 | 472
CASE HE210 | 281.6 | 291.4 | 299.2 | 293
CASE HE220 | 268.3 | 276.1 | 282.2 | 275
CASE HE230 | 458.3 | 431.4 | 480 | 474
| MEAN ZONE TEMPERATURE |  |  |  | MAXIMUM ZONE TEMPERATURE |  |  |  | MINIMUM ZONE TEMPERATURE
| °C |  |  |  | °C |  |  |  | °C
Cases | ESP-r /HOT3000 | EnergyPlus | DOE-2.1E | Your | ESP-r /HOT3000 | EnergyPlus | DOE-2.1E | Your | ESP-r /HOT3000 | EnergyPlus | DOE-2.1E | Your
| NRCAN | NRCAN | NRCAN | Software | NRCAN | NRCAN | NRCAN | Software | NRCAN | NRCAN | NRCAN | Software
CASE HE210 | 20.01 | 20 | 19.96 | 19.988 | 21.45 | 20 | 20.05 | 20.111 | 20 | 20 | 19.83 | 19.888
CASE HE220 | 18.75 | 18.53 | 18.5 | 18.538 | 22.7 | 20 | 20.05 | 20.111 | 15 | 15 | 14.88 | 14.944
CASE HE230 | 15.48 | 15.17 | 15.46 | 15.838 | 20.14 | 20 | 20.05 | 20.055 | 1.45 | 4.48 | 5.33 | 3.666

## YD
RESULTS5-4.XLS
Output spreadsheet for FURNACE BESTEST
INSTRUCTIONS:
1) PLEASE USE SPECIFIED UNITS
2) DATA ENTRY IS RESTRICTED TO THE SPECIFIED CELLS.
NOTE THAT WE HAVE USED THE PROTECTION OPTION IN THIS WORKSHEET TO
HELP ASSURE THAT DATA IS INPUT IN THE CORRECT CELLS.
THIS WAS DONE TO HELP EASE DATA HANDLING ON OUR END. IF YOU THINK WE
HAVE ACCIDENTALLY LEFT AN AREA PROTECTED THAT SHOULD HAVE BEEN
UNPROTECTED THEN DISABLE THE WORKSHEET PROTECTION TO INPUT YOUR DATA.
TOTAL FURNACE LOAD
CODENAME:
COUNTRY:
GJ
CASE HE100 | 76.0297
CASE HE110 | 76.0297
CASE HE120 | 30.2887
CASE HE130 | 0.12028
CASE HE140 | 30.5303
CASE HE150 | 28.993
CASE HE160 | 29.9247
CASE HE170 | 28.993
CASE HE210 | 41.1695
CASE HE220 | 38.9169
CASE HE230 | 33.9518
TOTAL FURNACE INPUT
CODENAME:
COUNTRY:
GJ
CASE HE100 | 76.6269
CASE HE110 | 95.7836
CASE HE120 | 37.5032
CASE HE130 | 0.099176
CASE HE140 | 38.0128
CASE HE150 | 36.0957
CASE HE160 | 37.2457
CASE HE170 | 36.0957
CASE HE210 | 51.2474
CASE HE220 | 48.4051
CASE HE230 | 42.6793
FUEL CONSUMPTION
CODENAME:
COUNTRY:
m3/s
CASE HE100 | 0.00025932
CASE HE110 | 0.00032415
CASE HE120 | 0.00012692
CASE HE130 | 3.3563e-07
CASE HE140 | 0.00012864
CASE HE150 | 0.00012216
CASE HE160 | 0.00012605
CASE HE170 | 0.00012216
CASE HE210 | 0.00017343
CASE HE220 | 0.00016381
CASE HE230 | 0.00014444
FAN ENERGY (BOTH FANS)
CODENAME:
COUNTRY:
kWh
CASE HE150 | 432
CASE HE160 | 169
CASE HE170 | 472
CASE HE210 | 293
CASE HE220 | 275
CASE HE230 | 474
MEAN ZONE TEMPERATURE
CODENAME:
COUNTRY:
°C
CASE HE210 | 19.988
CASE HE220 | 18.538
CASE HE230 | 15.838
MAXIMUM ZONE TEMPERATURE
CODENAME:
COUNTRY:
°C
CASE HE210 | 20.111
CASE HE220 | 20.111
CASE HE230 | 20.055
MINIMUM ZONE TEMPERATURE
CODENAME:
COUNTRY:
°C
CASE HE210 | 19.888
CASE HE220 | 14.944
CASE HE230 | 3.666

## B
Output spreadsheet for Furnace BESTEST
ESP-r /HOT3000 by NRCAN
INSTRUCTIONS:
1) PLEASE USE SPECIFIED UNITS
2) DATA ENTRY IS RESTRICTED TO THE SPECIFIED CELLS.
NOTE THAT WE HAVE USED THE PROTECTION OPTION IN THIS WORKSHEET TO
HELP ASSURE THAT DATA IS INPUT IN THE CORRECT CELLS.
THIS WAS DONE TO HELP EASE DATA HANDLING ON OUR END. IF YOU THINK WE
HAVE ACCIDENTALLY LEFT AN AREA PROTECTED THAT SHOULD HAVE BEEN
UNPROTECTED THEN DISABLE THE WORKSHEET PROTECTION TO INPUT YOUR DATA.
TOTAL FURNACE LOAD
CODENAME:
COUNTRY:
GJ
CASE HE100 | 77.94
CASE HE110 | 77.94
CASE HE120 | 31.25
CASE HE130 | 0
CASE HE140 | 31.26
CASE HE150 | 29.88
CASE HE160 | 31.26
CASE HE170 | 29.88
CASE HE210 | 41.36
CASE HE220 | 39.41
CASE HE230 | 34.32
TOTAL FURNACE INPUT
CODENAME:
COUNTRY:
GJ
CASE HE100 | 77.74
CASE HE110 | 96.9201
CASE HE120 | 38.4134
CASE HE130 | 0
CASE HE140 | 39.0044
CASE HE150 | 37.2315
CASE HE160 | 38.118
CASE HE170 | 37.2315
CASE HE210 | 50.5284
CASE HE220 | 47.8691
CASE HE230 | 41.3683
FUEL CONSUMPTION
CODENAME:
COUNTRY:
m3/s
CASE HE100 | 0.000263
CASE HE110 | 0.000328
CASE HE120 | 0.00013
CASE HE130 | 0
CASE HE140 | 0.000132
CASE HE150 | 0.000126
CASE HE160 | 0.000129
CASE HE170 | 0.000126
CASE HE210 | 0.000171
CASE HE220 | 0.000162
CASE HE230 | 0.00014
FAN ENERGY (BOTH FANS)
CODENAME:
COUNTRY:
kWh
CASE HE150 | 432
CASE HE160 | 170.2
CASE HE170 | 473.4
CASE HE210 | 281.6
CASE HE220 | 268.3
CASE HE230 | 458.3
MEAN ZONE TEMPERATURE
CODENAME:
COUNTRY:
°C
CASE HE210 | 20.01
CASE HE220 | 18.75
CASE HE230 | 15.48
MAXIMUM ZONE TEMPERATURE
CODENAME:
COUNTRY:
°C
CASE HE210 | 21.45
CASE HE220 | 22.7
CASE HE230 | 20.14
MINIMUM ZONE TEMPERATURE
CODENAME:
COUNTRY:
°C
CASE HE210 | 20
CASE HE220 | 15
CASE HE230 | 1.45

## C
Output spreadsheet for Furnace BESTEST
EnergyPlus by NRCAN
INSTRUCTIONS:
1) PLEASE USE SPECIFIED UNITS
2) DATA ENTRY IS RESTRICTED TO THE SPECIFIED CELLS.
NOTE THAT WE HAVE USED THE PROTECTION OPTION IN THIS WORKSHEET TO
HELP ASSURE THAT DATA IS INPUT IN THE CORRECT CELLS.
THIS WAS DONE TO HELP EASE DATA HANDLING ON OUR END. IF YOU THINK WE
HAVE ACCIDENTALLY LEFT AN AREA PROTECTED THAT SHOULD HAVE BEEN
UNPROTECTED THEN DISABLE THE WORKSHEET PROTECTION TO INPUT YOUR DATA.
TOTAL FURNACE LOAD
CODENAME:
COUNTRY:
GJ
CASE HE100 | 77.75
CASE HE110 | 77.75
CASE HE120 | 31.1
CASE HE130 | 0
CASE HE140 | 31.1
CASE HE150 | 29.59
CASE HE160 | 30.46
CASE HE170 | 29.59
CASE HE210 | 42.04
CASE HE220 | 39.87
CASE HE230 | 34.59
TOTAL FURNACE INPUT
CODENAME:
COUNTRY:
GJ
CASE HE100 | 77.7133
CASE HE110 | 97.2156
CASE HE120 | 38.2657
CASE HE130 | 0
CASE HE140 | 39.0044
CASE HE150 | 36.936
CASE HE160 | 38.118
CASE HE170 | 36.936
CASE HE210 | 52.0059
CASE HE220 | 49.3465
CASE HE230 | 42.5503
FUEL CONSUMPTION
CODENAME:
COUNTRY:
m3/s
CASE HE100 | 0.000263
CASE HE110 | 0.000329
CASE HE120 | 0.0001295
CASE HE130 | 0
CASE HE140 | 0.000132
CASE HE150 | 0.000125
CASE HE160 | 0.000129
CASE HE170 | 0.000125
CASE HE210 | 0.000176
CASE HE220 | 0.000167
CASE HE230 | 0.000144
FAN ENERGY (BOTH FANS)
CODENAME:
COUNTRY:
kWh
CASE HE150 | 433.3
CASE HE160 | 172.2
CASE HE170 | 473.1
CASE HE210 | 291.4
CASE HE220 | 276.1
CASE HE230 | 431.4
MEAN ZONE TEMPERATURE
CODENAME:
COUNTRY:
°C
CASE HE210 | 20
CASE HE220 | 18.53
CASE HE230 | 15.17
MAXIMUM ZONE TEMPERATURE
CODENAME:
COUNTRY:
°C
CASE HE210 | 20
CASE HE220 | 20
CASE HE230 | 20
MINIMUM ZONE TEMPERATURE
CODENAME:
COUNTRY:
°C
CASE HE210 | 20
CASE HE220 | 15
CASE HE230 | 4.48

## D
Output spreadsheet for Furnace BESTEST
DOE-2.1E by NRCAN
INSTRUCTIONS:
1) PLEASE USE SPECIFIED UNITS
2) DATA ENTRY IS RESTRICTED TO THE SPECIFIED CELLS.
NOTE THAT WE HAVE USED THE PROTECTION OPTION IN THIS WORKSHEET TO
HELP ASSURE THAT DATA IS INPUT IN THE CORRECT CELLS.
THIS WAS DONE TO HELP EASE DATA HANDLING ON OUR END. IF YOU THINK WE
HAVE ACCIDENTALLY LEFT AN AREA PROTECTED THAT SHOULD HAVE BEEN
UNPROTECTED THEN DISABLE THE WORKSHEET PROTECTION TO INPUT YOUR DATA.
TOTAL FURNACE LOAD
CODENAME:
COUNTRY:
GJ
CASE HE100 | 77.73
CASE HE110 | 77.73
CASE HE120 | 31.12
CASE HE130 | 0.15804
CASE HE140 | 31.07
CASE HE150 | 29.55
CASE HE160 | 30.48
CASE HE170 | 29.55
CASE HE210 | 42.08
CASE HE220 | 39.87
CASE HE230 | 34.49
TOTAL FURNACE INPUT
CODENAME:
COUNTRY:
GJ
CASE HE100 | 78.3043
CASE HE110 | 97.8065
CASE HE120 | 38.4134
CASE HE130 | 0.14479
CASE HE140 | 38.7089
CASE HE150 | 36.6405
CASE HE160 | 37.8225
CASE HE170 | 36.6405
CASE HE210 | 52.3014
CASE HE220 | 49.3465
CASE HE230 | 43.1412
FUEL CONSUMPTION
CODENAME:
COUNTRY:
m3/s
CASE HE100 | 0.000265
CASE HE110 | 0.000331
CASE HE120 | 0.00013
CASE HE130 | 4.9e-07
CASE HE140 | 0.000131
CASE HE150 | 0.000124
CASE HE160 | 0.000128
CASE HE170 | 0.000124
CASE HE210 | 0.000177
CASE HE220 | 0.000167
CASE HE230 | 0.000146
FAN ENERGY (BOTH FANS)
CODENAME:
COUNTRY:
kWh
CASE HE150 | 432.1
CASE HE160 | 172.3
CASE HE170 | 473.3
CASE HE210 | 299.2
CASE HE220 | 282.2
CASE HE230 | 480
MEAN ZONE TEMPERATURE
CODENAME:
COUNTRY:
°C
CASE HE210 | 19.96
CASE HE220 | 18.5
CASE HE230 | 15.46
MAXIMUM ZONE TEMPERATURE
CODENAME:
COUNTRY:
°C
CASE HE210 | 20.05
CASE HE220 | 20.05
CASE HE230 | 20.05
MINIMUM ZONE TEMPERATURE
CODENAME:
COUNTRY:
°C
CASE HE210 | 19.83
CASE HE220 | 14.88
CASE HE230 | 5.33

## Q
RESULTS.XLS5-4, Jan 27, 2005 |  |  | SEE SHEET 'A' FOR INSTRUCTIONS
NB: (Max-Min)/Analytical is replaced with (Max-Min)/Average for cases 2A,2B and 2C
TOTAL FURNACE LOAD |  | GJ
|  |  |  | Statistics, All Results |  |  | Analytical/semi-analytical |  | Your
Cases | ESP-r /HOT3000 | EnergyPlus | DOE-2.1E |  |  | (Max-Min) | Heat transfer surf | Infiltration | Software | Acceptance Criteria
|  |  |  | Min | Max | /Analytical | method | method |  | Max | Min
CASE HE100 | 77.94 | 77.75 | 77.73 | 77.73 | 77.94 | 0.2701% | 77.74 | 77.77 | 76.0297 | 77.9505 | 77.7195 | FAIL
CASE HE110 | 77.94 | 77.75 | 77.73 | 77.73 | 77.94 | 0.2701% | 77.74 | 77.77 | 76.0297 | 77.9505 | 77.7195 | FAIL
CASE HE120 | 31.25 | 31.1 | 31.12 | 31.1 | 31.25 | 0.4823% | 31.1 | 31.11 | 30.2887 | 31.2575 | 31.0925 | FAIL
CASE HE130 | 0 | 0 | 0.15804 | 0 | 0.15804 | 0% | 0 | 0 | 0.12028
CASE HE140 | 31.26 | 31.1 | 31.07 | 31.07 | 31.26 | 0.6109% | 31.1 | 31.11 | 30.5303 | 31.2695 | 31.0605 | FAIL
CASE HE150 | 29.88 | 29.59 | 29.55 | 29.55 | 29.88 | 1.113% | 29.65 | 29.66 | 28.993 | 29.8965 | 29.5335 | FAIL
CASE HE160 | 31.26 | 30.46 | 30.48 | 30.46 | 31.26 | 2.572% | 31.1 | 31.11 | 29.9247 | 31.3 | 30.42 | FAIL
CASE HE170 | 29.88 | 29.59 | 29.55 | 29.55 | 29.88 | 1.113% | 29.65 | 29.66 | 28.993 | 29.8965 | 29.5335 | FAIL
CASE HE210 | 41.36 | 42.04 | 42.08 | 41.36 | 42.08 | 1.726% | - | - | 41.1695 | 42.116 | 41.324 | FAIL
CASE HE220 | 39.41 | 39.87 | 39.87 | 39.41 | 39.87 | 1.16% | - | - | 38.9169 | 39.893 | 39.387 | FAIL
CASE HE230 | 34.32 | 34.59 | 34.49 | 34.32 | 34.59 | 0.7836% | - | - | 33.9518 | 34.6035 | 34.3065 | FAIL
TOTAL FURNACE INPUT |  | GJ
|  |  |  | Statistics, All Results |  |  | Analytical/semi-analytical |  | Your
Cases | ESP-r /HOT3000 | EnergyPlus | DOE-2.1E |  |  | (Max-Min) | Heat transfer surf | Infiltration | Software | Acceptance Criteria
|  |  |  | Min | Max | /Analytical | method | method |  | Max | Min
CASE HE100 | 77.74 | 77.7133 | 78.3043 | 77.7133 | 78.3043 | 0.7605% | 77.7133 | 77.7133 | 76.6269 | 78.3339 | 77.6838 | FAIL
CASE HE110 | 96.9201 | 97.2156 | 97.8065 | 96.9201 | 97.8065 | 0.9119% | 97.2156 | 97.2156 | 95.7836 | 97.8509 | 96.8757 | FAIL
CASE HE120 | 38.4134 | 38.2657 | 38.4134 | 38.2657 | 38.4134 | 0.3861% | 38.2657 | 38.2952 | 37.5032 | 38.4208 | 38.2583 | FAIL
CASE HE130 | 0 | 0 | 0.14479 | 0 | 0.14479 | 0% | 0 | 0 | 0.099176
CASE HE140 | 39.0044 | 39.0044 | 38.7089 | 38.7089 | 39.0044 | 0.7576% | 39.0044 | 39.0044 | 38.0128 | 39.0192 | 38.6942 | FAIL
CASE HE150 | 37.2315 | 36.936 | 36.6405 | 36.6405 | 37.2315 | 1.596% | 37.0246 | 37.0246 | 36.0957 | 37.261 | 36.611 | FAIL
CASE HE160 | 38.118 | 38.118 | 37.8225 | 37.8225 | 38.118 | 0.7758% | 38.0884 | 38.118 | 37.2457 | 38.1327 | 37.8077 | FAIL
CASE HE170 | 37.2315 | 36.936 | 36.6405 | 36.6405 | 37.2315 | 1.596% | 37.0246 | 37.0246 | 36.0957 | 37.261 | 36.611 | FAIL
CASE HE210 | 50.5284 | 52.0059 | 52.3014 | 50.5284 | 52.3014 | 3.448% | - | - | 51.2474 | 52.39 | 50.4398 | PASS
CASE HE220 | 47.8691 | 49.3465 | 49.3465 | 47.8691 | 49.3465 | 3.04% | - | - | 48.4051 | 49.4204 | 47.7952 | PASS
CASE HE230 | 41.3683 | 42.5503 | 43.1412 | 41.3683 | 43.1412 | 4.196% | - | - | 42.6793 | 43.2299 | 41.2797 | PASS
FUEL CONSUMPTION |  | m3/s
|  |  |  | Statistics, All Results |  |  | Analytical/semi-analytical |  | Your
Cases | ESP-r /HOT3000 | EnergyPlus | DOE-2.1E |  |  | (Max-Min) | Heat transfer surf | Infiltration | Software | Acceptance Criteria
|  |  |  | Min | Max | /Analytical | method | method |  | Max | Min
CASE HE100 | 0.000263 | 0.000263 | 0.000265 | 0.000263 | 0.000265 | 0.7605% | 0.000263 | 0.000263 | 0.00025932 | 0.0002651 | 0.0002629 | FAIL
CASE HE110 | 0.000328 | 0.000329 | 0.000331 | 0.000328 | 0.000331 | 0.9119% | 0.000329 | 0.000329 | 0.00032415 | 0.00033115 | 0.00032785 | FAIL
CASE HE120 | 0.00013 | 0.0001295 | 0.00013 | 0.0001295 | 0.00013 | 0.3861% | 0.0001295 | 0.0001296 | 0.00012692 | 0.00013003 | 0.00012947 | FAIL
CASE HE130 | 0 | 0 | 4.9e-07 | 0 | 4.9e-07 | 0% | 0 | 0 | 3.3563e-07
CASE HE140 | 0.000132 | 0.000132 | 0.000131 | 0.000131 | 0.000132 | 0.7576% | 0.000132 | 0.000132 | 0.00012864 | 0.00013205 | 0.00013095 | FAIL
CASE HE150 | 0.000126 | 0.000125 | 0.000124 | 0.000124 | 0.000126 | 1.596% | 0.0001253 | 0.0001253 | 0.00012216 | 0.0001261 | 0.0001239 | FAIL
CASE HE160 | 0.000129 | 0.000129 | 0.000128 | 0.000128 | 0.000129 | 0.7758% | 0.0001289 | 0.000129 | 0.00012605 | 0.00012905 | 0.00012795 | FAIL
CASE HE170 | 0.000126 | 0.000125 | 0.000124 | 0.000124 | 0.000126 | 1.596% | 0.0001253 | 0.0001253 | 0.00012216 | 0.0001261 | 0.0001239 | FAIL
CASE HE210 | 0.000171 | 0.000176 | 0.000177 | 0.000171 | 0.000177 | 3.448% | - | - | 0.00017343 | 0.0001773 | 0.0001707 | PASS
CASE HE220 | 0.000162 | 0.000167 | 0.000167 | 0.000162 | 0.000167 | 3.04% | - | - | 0.00016381 | 0.00016725 | 0.00016175 | PASS
CASE HE230 | 0.00014 | 0.000144 | 0.000146 | 0.00014 | 0.000146 | 4.196% | - | - | 0.00014444 | 0.0001463 | 0.0001397 | PASS
FAN ENERGY (BOTH FANS) |  | Kwh
|  |  |  | Statistics, All Results |  |  | Analytical | Your
Cases | ESP-r /HOT3000 | EnergyPlus | DOE-2.1E |  |  | (Max-Min) | /semi-analytical | Software | Acceptance Criteria
|  |  |  | Min | Max | /Analytical |  |  | Max | Min
CASE HE150 | 432 | 433.3 | 432.1 | 432 | 433.3 | 0.3009% | 432 | 432 | 433.365 | 431.935 | PASS
CASE HE160 | 170.2 | 172.2 | 172.3 | 170.2 | 172.3 | 1.216% | 172.76 | 169 | 172.405 | 170.095 | FAIL
CASE HE170 | 473.4 | 473.1 | 473.3 | 473.1 | 473.4 | 0.0634% | 473.18 | 472 | 473.415 | 473.085 | FAIL
CASE HE210 | 281.6 | 291.4 | 299.2 | 281.6 | 299.2 | 6.061% | - | 293 | 300.08 | 280.72 | PASS
CASE HE220 | 268.3 | 276.1 | 282.2 | 268.3 | 282.2 | 5.05% | - | 275 | 282.895 | 267.605 | PASS
CASE HE230 | 458.3 | 431.4 | 480 | 431.4 | 480 | 10.66% | - | 474 | 482.43 | 428.97 | PASS
MEAN ZONE TEMPERATURE |  | °C
|  |  |  | Statistics, All Results |  |  | Your
Cases | ESP-r /HOT3000 | EnergyPlus | DOE-2.1E |  |  | (Max-Min) | Software | Acceptance Criteria
|  |  |  | Min | Max | /Average |  | Max | Min
CASE HE210 | 20.01 | 20 | 19.96 | 19.96 | 20.01 | 0.2502% | 19.988 | 20.0125 | 19.9575 | PASS
CASE HE220 | 18.75 | 18.53 | 18.5 | 18.5 | 18.75 | 1.342% | 18.538 | 18.7625 | 18.4875 | PASS
CASE HE230 | 15.48 | 15.17 | 15.46 | 15.17 | 15.48 | 2.023% | 15.838 | 15.4955 | 15.1545 | FAIL
MAXIMUM ZONE TEMPERATURE |  | °C
|  |  |  | Statistics, All Results |  |  | Your
Cases | ESP-r /HOT3000 | EnergyPlus | DOE-2.1E |  |  | (Max-Min) | Software | Acceptance Criteria
|  |  |  | Min | Max | /Average |  | Max | Min
CASE HE210 | 21.45 | 20 | 20.05 | 20 | 21.45 | 6.996% | 20.111 | 21.5225 | 19.9275 | PASS
CASE HE220 | 22.7 | 20 | 20.05 | 20 | 22.7 | 12.65% | 20.111 | 22.835 | 19.865 | PASS
CASE HE230 | 20.14 | 20 | 20.05 | 20 | 20.14 | 0.6976% | 20.055 | 20.147 | 19.993 | PASS
MINIMUM ZONE TEMPERATURE |  | °C
|  |  |  | Statistics, All Results |  |  | Your
Cases | ESP-r /HOT3000 | EnergyPlus | DOE-2.1E |  |  | (Max-Min) | Software | Acceptance Criteria
|  |  |  | Min | Max | /Average |  | Max | Min
CASE HE210 | 20 | 20 | 19.83 | 19.83 | 20 | 0.8536% | 19.888 | 20.0085 | 19.8215 | PASS
CASE HE220 | 15 | 15 | 14.88 | 14.88 | 15 | 0.8032% | 14.944 | 15.006 | 14.874 | PASS
CASE HE230 | 1.45 | 4.48 | 5.33 | 1.45 | 5.33 | 114.5% | 3.666 | 5.524 | 1.256 | PASS