## A
RESULTS5-2.XLS |  | EnergyGauge Summit version 4.0 using DOE2.1E
This spreadsheet contains the IEA 12B/21C participant results which are
presented in the informational appendix containing example results.
This data is provided for the convenience of users who wish to plot
or tabulate their results along with the example results.
This speadsheet was originally created with Lotus 1-2-3 version 3.1 for DOS.
The spreadsheet contains only values and text (no formulas).
Various data can be found at the following addresses:
A61..L138 |  | Annual Loads (heating and sensible cooling)
A142..L180 |  | Annual Hourly Integrated Peak Heating Loads
A195..L233 |  | Annual Hourly Integrated Peak Sensible Cooling Loads
A249..L276 |  | Annual Free Float Temperature Output
A286..J335 |  | Various annual incident and annual transmitted solar
radiation outputs
A341..J901 |  | Various hourly incident solar, temperature, and load
output including temperature and bin frequency output
(this output was plotted in the example results appendix
but not presented in table format)
Q61..AB131 |  | Low Mass and High Mass Basic Sensitivity Tests
Q138..AB206 |  | In-Depth Sensitivity Tests, Cases 195 through 320
Q210..AB246 |  | In-Depth Sensitivity Tests, Cases 395 through 440
Q248..AB290 |  | High Mass Basic and In-Depth Sensitivity Tests
Q293..Z316 |  | Annual transmissivity and shading coefficients of windows
Q322..AT360 |  | Annual Hourly Integrated Peak Heating Loads
(including dates and hours)
Q375..AT413 |  | Annual Hourly Integrated Peak Sensible Cooling Loads
(including dates and hours)
Q429..AT456 |  | Annual Free Float Temperature Output
(including dates and hours)
A blank column with the header "YOUR DATA" has been provided with each
category of results. For data categories beginning in Column A, "YOUR
DATA" should be added to column J. For data categories beginning in
Column Q, "YOUR DATA" should be added to Column Z for Rows 65 to 316,
and to Columns AP through AR for Rows 326 to 456. This should
facilitate developing graphs and tables of your results which also
include the example results and/or ranges.
The Standard Output Report spreadsheet (Sec5-2out.XLS) has been designed
such that values input to Column B of Sec5-2out.XLS can be directly transferred to
Column J of this spreadsheet.
ANNUAL HEATING LOADS | [11 empty] | LOW MASS BASIC SENSITIVITY TESTS
| ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | SUMMARY |  | ANNUAL HEATING [MWH]
| UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | MIN | MAX |  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | SUMMARY
CASE | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh | CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | MIN | MAX
600 | 4.296 | 4.773 | 5.709 | 5.226 | 5.596 | 4.882 | 4.872 | 5.362 | 4.994 | 4.296 | 5.709 | 610-600 | 0.059 | 0.033 | 0.077 | 0.054 | 0.024 | 0.089 | 0.098 | 0.021 | 0.048 | 0.021 | 0.098
610 | 4.355 | 4.806 | 5.786 | 5.28 | 5.62 | 4.971 | 4.97 | 5.383 | 5.042 | 4.355 | 5.786 | 620-600 | 0.317 | 0.276 | 0.235 | 0.328 | 0.138 | 0.682 | 0.201 | 0.366 | 0.15 | 0.138 | 0.682
620 | 4.613 | 5.049 | 5.944 | 5.554 | 5.734 | 5.564 | 5.073 | 5.728 | 5.144 | 4.613 | 5.944 | 630-620 | 0.437 | 0.31 | 0.525 | 0.329 | 0.267 | 0.531 | 0.551 |  | 0.364 | 0.267 | 0.551
630 | 5.05 | 5.359 | 6.469 | 5.883 | 6.001 | 6.095 | 5.624 |  | 5.508 | 5.05 | 6.469 | 640-600 | -1.545 | -1.885 | -2.166 | -1.971 | -1.793 | -1.817 | -1.829 | -2.053 | -1.999 | -2.166 | -1.545
640 | 2.751 | 2.888 | 3.543 | 3.255 | 3.803 | 3.065 | 3.043 | 3.309 | 2.995 | 2.751 | 3.803 | ANNUAL COOLING [MWH]
650 | 0 | 0 | 0 | 0 | 0 | 0 | 4.171e-06 | 0 | 0 | 0 | 4.171e-06 |  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | SUMMARY
900 | 1.17 | 1.61 | 1.872 | 1.897 | 1.988 | 1.73 | 1.655 | 2.041 | 1.301 | 1.17 | 2.041 | CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | MIN | MAX
910 | 1.575 | 1.862 | 2.254 | 2.174 | 2.282 | 2.063 | 2.097 | 2.22 | 1.559 | 1.575 | 2.282 | 610-600 | -2.222 | -1.582 | -2.227 | -1.83 | -2.186 | -1.728 | -1.891 | -1.272 | -2.18 | -2.227 | -1.272
920 | 3.313 | 3.752 | 4.255 | 4.093 | 4.058 | 4.235 | 3.776 | 4.3 | 3.312 | 3.313 | 4.3 | 620-600 | -2.72 | -2.341 | -2.745 | -2.645 | -2.96 | -2.481 | -2.591 | -2.427 | -2.798 | -2.96 | -2.341
930 | 4.143 | 4.347 | 5.335 | 4.755 | 4.728 | 5.168 | 4.74 |  | 4.249 | 4.143 | 5.335 | 630-620 | -1.288 | -0.984 | -1.845 | -1.14 | -1.303 | -1.522 | -1.485 |  | -2.021 | -1.845 | -0.984
940 | 0.793 | 1.021 | 1.239 | 1.231 | 1.411 | 1.179 | 1.08 | 1.323 | 0.838 | 0.793 | 1.411 | 640-600 | -0.185 | -0.25 | -0.32 | -0.252 | -0.153 | -0.245 | -0.246 | -0.27 | -0.341 | -0.32 | -0.153
950 | 0 | 0 | 0 | 0 | 0 | 0 | 7.801e-06 | 0 | 0 | 0 | 7.801e-06 | 650-600 | -1.321 | -1.293 | -1.284 | -1.384 | -1.419 | -1.404 | -1.373 | -1.322 | -1.376 | -1.419 | -1.284
960 | 2.311 | 2.664 | 2.928 | 2.884 | 2.851 | 2.943 | 3.373 | 2.816 | 2.216 | 2.311 | 3.373 | PEAK HEATING [KW]
195 | 4.167 | [7 empty] | 5.536 | 4.167 | 4.167 |  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | SUMMARY
200 | 5.252 | [8 empty] | 5.252 | 5.252 | CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | MIN | MAX
210 | 6.456 | 6.559 |  |  |  |  | 6.554 | 6.967 |  | 6.456 | 6.967 | 610-600 | 0 | 0.001 | -0.011 | 0 |  | 0 | -0.0083333 | 0 | -0.012 | -0.011 | 0.001
215 | 5.547 | [8 empty] | 5.547 | 5.547 | 620-600 | 0.154 | 0.001 | 0.001 | 0.019 |  | 0.24 | -0.0083333 | 0.025 | 0.018 | -0.0083333 | 0.24
220 | 6.944 | 7.215 | 8.787 | 8.102 | 8.127 | 7.422 | 7.297 | 7.437 | 7.717 | 6.944 | 8.787 | 630-620 | 0.001 | 0 | -0.021 | 0.003 |  | 0.001 | 0 |  | -0.023 | -0.021 | 0.003
230 | 10.376 | 10.74 | 12.243 | 11.633 | 11.649 | 11.037 | 10.84 | 10.964 | 11.128 | 10.376 | 12.243 | 640-600 | 1.795 | 1.546 | 1.898 | 2.272 |  | 2.31 | 1.7917 | 2.6 | 1.889 | 1.546 | 2.6
240 | 5.649 | 6.009 | 7.448 | 6.769 | 6.786 | 6.194 | 6.076 | 6.234 | 6.436 | 5.649 | 7.448 | PEAK COOLING [KW]
250 | 4.751 | 5.739 | 7.024 | 6.608 | 6.653 | 5.974 | 5.764 | 5.738 | 5.817 | 4.751 | 7.024 |  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | SUMMARY
270 | 4.51 | 4.93 |  | 5.341 | 5.92 |  | 5.047 | 5.489 |  | 4.51 | 5.92 | CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | MIN | MAX
280 | 4.675 | 5.125 |  | 5.937 | 6.148 |  | 5.279 | 5.841 |  | 4.675 | 6.148 | 610-600 | -0.525 | -0.141 | -0.592 | -0.456 |  | -0.116 | -0.81111 | -0.666 | -0.483 | -0.81111 | -0.116
290 | 4.577 | 4.959 |  | 5.406 | 5.942 |  | 5.132 | 5.509 |  | 4.577 | 5.942 | 620-600 | -2.56 | -1.89 | -2.226 | -2.234 |  | -1.989 | -2.2111 | -1.716 | -2.286 | -2.56 | -1.716
300 | 4.761 | 5.077 |  | 5.587 | 5.964 |  | 5.124 | 5.786 |  | 4.761 | 5.964 | 630-620 | -0.562 | -0.371 | -0.842 | -0.477 |  | -0.632 | -0.66667 |  | -0.845 | -0.842 | -0.371
310 | 5.221 | 5.327 |  | 5.85 | 6.165 |  | 5.61 |  |  | 5.221 | 6.165 | 640-600 | -0.033 | -0.073 | -0.08 | -0.051 |  | -0.036 | -0.044444 | -0.041 | -0.062 | -0.08 | -0.033
320 | 3.859 | 4.209 |  | 4.627 | 5.141 |  | 4.348 | 4.84 |  | 3.859 | 5.141 | 650-600 | -0.163 | -0.134 | -0.14 | -0.156 |  | -0.143 | -0.10833 | -0.133 | -0.122 | -0.163 | -0.10833
395 | 4.984 | 4.799 | 5.835 | 5.199 | 5.201 | 4.967 | 4.855 | 4.839 | 5.472 | 4.799 | 5.835
400 | 6.9 | 7.075 | 8.77 | 7.966 | 7.973 | 7.287 | 7.166 | 7.326 | 7.659 | 6.9 | 8.77 | HIGH MASS BASIC SENSITIVITY TESTS
410 | 8.596 | 8.873 | 10.506 | 9.726 | 9.734 | 9.019 | 8.936 | 9.085 | 9.38 | 8.596 | 10.506 | ANNUAL HEATING [MWH]
420 | 7.298 | 7.61 | 9.151 | 8.365 | 8.373 | 7.774 | 7.697 | 7.863 | 8.074 | 7.298 | 9.151 |  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | SUMMARY
430 | 5.429 | 6.488 | 7.827 | 7.178 | 7.186 | 6.662 | 6.5 | 6.51 | 6.309 | 5.429 | 7.827 | CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | MIN | MAX
440 | 4.449 | 4.987 |  | 5.652 | 5.811 |  | 5.098 | 5.642 |  | 4.449 | 5.811 | 900-600 | -3.126 | -3.163 | -3.837 | -3.329 | -3.608 | -3.152 | -3.217 | -3.321 | -3.693 | -3.837 | -3.126
800 | 4.868 | 5.953 | 7.228 | 6.611 | 6.6 | 6.161 | 5.94 | 5.861 | 5.353 | 4.868 | 7.228 | 910-900 | 0.405 | 0.252 | 0.382 | 0.277 | 0.294 | 0.333 | 0.442 | 0.179 | 0.258 | 0.179 | 0.442
810 | 1.839 | 2.446 |  | 3.004 | 2.828 |  | 2.567 | 2.962 |  | 1.839 | 3.004 | 920-900 | 2.143 | 2.142 | 2.383 | 2.196 | 2.07 | 2.505 | 2.121 | 2.259 | 2.011 | 2.07 | 2.505
ANNUAL COOLING [MWH] | [11 empty] | 930-920 | 0.83 | 0.595 | 1.08 | 0.662 | 0.67 | 0.933 | 0.964 |  | 0.937 | 0.595 | 1.08
| ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | SUMMARY |  | 940-900 | -0.377 | -0.589 | -0.633 | -0.666 | -0.577 | -0.551 | -0.575 | -0.718 | -0.463 | -0.718 | -0.377
| UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | MIN | MAX | 960-900 | 1.141 | 1.054 | 1.056 | 0.987 | 0.863 | 1.213 | 1.718 | 0.775 | 0.915 | 0.775 | 1.718
CASE# | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh | MWh | ANNUAL COOLING [MWH]
600 | 6.137 | 6.433 | 7.079 | 7.278 | 7.964 | 6.492 | 6.492 | 6.778 | 8.054 | 6.137 | 7.964 |  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | SUMMARY
610 | 3.915 | 4.851 | 4.852 | 5.448 | 5.778 | 4.764 | 4.601 | 5.506 | 5.874 | 3.915 | 5.778 | CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | MIN | MAX
620 | 3.417 | 4.092 | 4.334 | 4.633 | 5.004 | 4.011 | 3.901 | 4.351 | 5.256 | 3.417 | 5.004 | 900-600 | -4.005 | -3.833 | -4.624 | -4.113 | -4.549 | -3.92 | -4.007 | -4.179 | -4.664 | -4.624 | -3.833
630 | 2.129 | 3.108 | 2.489 | 3.493 | 3.701 | 2.489 | 2.416 |  | 3.235 | 2.129 | 3.701 | 910-900 | -1.311 | -1.067 | -1.479 | -1.293 | -1.561 | -1.144 | -1.159 | -0.832 | -1.652 | -1.561 | -0.832
640 | 5.952 | 6.183 | 6.759 | 7.026 | 7.811 | 6.247 | 6.246 | 6.508 | 7.713 | 5.952 | 7.811 | 920-900 | -0.292 | 0.016 | -0.015 | -0.222 | -0.323 | -0.115 | -0.067 | 0.014 | -0.221 | -0.323 | 0.016
650 | 4.816 | 5.14 | 5.795 | 5.894 | 6.545 | 5.088 | 5.119 | 5.456 | 6.678 | 4.816 | 6.545 | 930-920 | -0.801 | -0.682 | -1.174 | -0.77 | -0.854 | -1.018 | -1.002 |  | -1.346 | -1.174 | -0.682
900 | 2.132 | 2.6 | 2.455 | 3.165 | 3.415 | 2.572 | 2.485 | 2.599 | 3.39 | 2.132 | 3.415 | 940-900 | -0.053 | -0.064 | -0.115 | -0.129 | -0.174 | -0.083 | -0.102 | -0.083 | -0.118 | -0.174 | -0.053
910 | 0.821 | 1.533 | 0.976 | 1.872 | 1.854 | 1.428 | 1.326 | 1.767 | 1.738 | 0.821 | 1.872 | 950-900 | -1.745 | -2.074 | -1.917 | -2.244 | -2.826 | -2.021 | -1.9244 | -1.828 | -2.641 | -2.826 | -1.745
920 | 1.84 | 2.616 | 2.44 | 2.943 | 3.092 | 2.457 | 2.418 | 2.613 | 3.169 | 1.84 | 3.092 | 960-900 | -1.644 | -1.934 | -2.027 | -2.362 | -2.697 | -1.929 | -2.0737 | -1.813 | -2.535 | -2.697 | -1.644
930 | 1.039 | 1.934 | 1.266 | 2.173 | 2.238 | 1.439 | 1.416 |  | 1.823 | 1.039 | 2.238 | PEAK HEATING [KW]
940 | 2.079 | 2.536 | 2.34 | 3.036 | 3.241 | 2.489 | 2.383 | 2.516 | 3.272 | 2.079 | 3.241 |  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | SUMMARY
950 | 0.387 | 0.526 | 0.538 | 0.921 | 0.589 | 0.551 | 0.5606 | 0.771 | 0.749 | 0.387 | 0.921 | CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | MIN | MAX
960 | 0.488 | 0.666 | 0.428 | 0.803 | 0.718 | 0.643 | 0.4113 | 0.786 | 0.855 | 0.4113 | 0.803 | 900-600 | -0.587 | -0.487 | -0.488 | -0.498 |  | -0.429 | -0.41389 | -0.557 | -0.519 | -0.587 | -0.41389
195 | 0.414 | [7 empty] | 0.353 | 0.414 | 0.414 | 910-900 | 0.008 | 0.003 | 0.007 | 0.004 |  | 0.01 | 0.019444 | 0.004 | 0.0080001 | 0.003 | 0.019444
200 | 0.57 | [8 empty] | 0.57 | 0.57 | 920-900 | 0.458 | 0.25 | 0.248 | 0.253 |  | 0.421 | 0.19167 | 0.264 | 0.26 | 0.19167 | 0.458
210 | 0.162 | 0.613 |  |  |  |  | 0.6679 | 0.641 |  | 0.162 | 0.6679 | 930-920 | 0.047 | 0.029 | 0.027 | 0.029 |  | 0.035 | 0.036111 |  | 0.028 | 0.027 | 0.047
215 | 0.639 | [8 empty] | 0.639 | 0.639 | 940-900 | 1.13 | 1.575 | 2.108 | 2.356 |  | 2.509 | 1.6056 | 2.631 | 2.074 | 1.13 | 2.631
220 | 0.186 | 0.701 | 0.399 | 0.827 | 0.835 | 0.734 | 0.7368 | 0.683 | 0.558 | 0.186 | 0.835 | 960-900 | -0.44 | -0.702 | -0.83 | -0.897 |  | -0.756 | -0.99467 | -1.018 | -0.645 | -1.018 | -0.44
230 | 0.454 | 0.976 | 0.692 | 1.131 | 1.139 | 1.02 | 1.04 | 0.985 | 0.861 | 0.454 | 1.139 | PEAK COOLING [KW]
240 | 0.415 | 1.072 | 0.66 | 1.239 | 1.246 | 1.108 | 1.114 | 1.045 | 0.878 | 0.415 | 1.246 |  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | SUMMARY
250 | 3.213 | 2.545 | 2.177 | 2.924 | 2.931 | 2.486 | 2.684 | 3.38 | 4.284 | 2.177 | 3.38 | CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | MIN | MAX
270 | 7.528 | 8.67 |  | 9.828 | 10.35 |  | 8.764 | 8.714 |  | 7.528 | 10.35 | 900-600 | -3.306 | -2.81 | -3.198 | -2.956 |  | -2.952 | -2.9194 | -3.355 | -3.187 | -3.355 | -2.81
280 | 4.873 | 5.895 |  | 6.511 | 7.114 |  | 5.761 | 6.257 |  | 4.873 | 7.114 | 910-900 | -0.992 | -0.655 | -1.122 | -0.594 |  | -0.548 | -0.775 | -0.31 | -1.075 | -1.122 | -0.31
290 | 5.204 | 7.011 |  | 7.871 | 8.089 |  | 6.699 | 7.431 |  | 5.204 | 8.089 | 920-900 | -0.503 | -0.222 | -0.349 | -0.384 |  | -0.263 | -0.51667 | 0.048 | -0.436 | -0.51667 | 0.048
300 | 4.302 | 5.836 |  | 6.665 | 7.1 |  | 5.721 | 5.781 |  | 4.302 | 7.1 | 930-920 | -0.512 | -0.387 | -0.721 | -0.407 |  | -0.585 | -0.55167 |  | -0.704 | -0.721 | -0.387
310 | 2.732 | 4.57 |  | 5.245 | 5.471 |  | 3.727 |  |  | 2.732 | 5.471 | 940-900 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
320 | 5.061 | 5.906 |  | 6.725 | 7.304 |  | 5.956 | 5.663 |  | 5.061 | 7.304 | 950-900 | -0.855 | -0.534 | -0.794 | -0.701 |  | -0.657 | -0.88056 | -0.59 | -0.861 | -0.88056 | -0.534
395 | 0 | 0.011 | 0 | 0.016 | 0.014 | 0.01 | 0.01029 | 0.011 | 0.001 | 0 | 0.016 | 960-900 | -1.935 | -2.011 | -2.401 | -2.501 |  | -2.155 | -2.1887 | -2.054 | -2.37 | -2.501 | -1.935
400 | 0 | 0.04 | 0.002 | 0.061 | 0.058 | 0.042 | 0.04468 | 0.044 | 0.016 | 0 | 0.061
410 | 0 | 0.059 | 0.01 | 0.084 | 0.084 | 0.063 | 0.06707 | 0.065 | 0.035 | 0 | 0.084
420 | 0.011 | 0.147 | 0.051 | 0.189 | 0.188 | 0.154 | 0.1575 | 0.143 | 0.105 | 0.011 | 0.189
430 | 0.542 | 0.617 | 0.422 | 0.704 | 0.684 | 0.563 | 0.6174 | 0.875 | 1.106 | 0.422 | 0.875
440 | 3.967 | 4.172 |  | 4.674 | 5.204 |  | 3.975 | 4.684 |  | 3.967 | 5.204
800 | 0.113 | 0.224 | 0.055 | 0.272 | 0.222 | 0.195 | 0.2073 | 0.325 | 0.323 | 0.055 | 0.325
810 | 1.052 | 1.405 |  | 1.711 | 1.708 |  | 1.191 | 1.624 |  | 1.052 | 1.711 | LOW MASS IN-DEPTH (CASES 195 THRU 320) SENSITIVITY TESTS
ANNUAL HEATING [MWH]
[13 empty] | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | SUMMARY
[12 empty] | CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | MIN | MAX
ANNUAL HOURLY INTEGRATED PEAK HEATING LOADS | [11 empty] | 200-195 | 1.085 | [8 empty] | 1.085 | 1.085
CODENAME: | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR |  |  | 210-200 | 1.204 | [8 empty] | 1.204 | 1.204
COUNTRY: | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | SUMMARY |  | 220-215 | 1.397 | [8 empty] | 1.397 | 1.397
CASE# | KW | KW | KW | KW | KW | KW | KW | KW | KW | MIN | MAX | 215-200 | 0.295 | [8 empty] | 0.295 | 0.295
600 | 3.437 | 3.94 | 4.045 | 4.258 |  | 4.037 | 3.9306 | 4.354 | 3.767 | 3.437 | 4.354 | 220-210 | 0.488 | 0.656 |  |  |  |  | 0.743 | 0.47 |  | 0.47 | 0.743
610 | 3.437 | 3.941 | 4.034 | 4.258 |  | 4.037 | 3.9222 | 4.354 | 3.755 | 3.437 | 4.354 | 230-220 | 3.432 | 3.525 | 3.456 | 3.531 | 3.522 | 3.615 | 3.543 | 3.527 | 3.411 | 3.432 | 3.615
620 | 3.591 | 3.941 | 4.046 | 4.277 |  | 4.277 | 3.9222 | 4.379 | 3.785 | 3.591 | 4.379 | 240-220 | -1.295 | -1.206 | -1.339 | -1.333 | -1.341 | -1.228 | -1.221 | -1.203 | -1.281 | -1.341 | -1.203
630 | 3.592 | 3.941 | 4.025 | 4.28 |  | 4.278 | 3.9222 |  | 3.762 | 3.592 | 4.28 | 250-220 | -2.193 | -1.476 | -1.763 | -1.494 | -1.474 | -1.448 | -1.533 | -1.699 | -1.9 | -2.193 | -1.448
640 | 5.232 | 5.486 | 5.943 | 6.53 |  | 6.347 | 5.7222 | 6.954 | 5.656 | 5.232 | 6.954 | 270-220 | -2.434 | -2.285 |  | -2.761 | -2.207 |  | -2.25 | -1.948 |  | -2.761 | -1.948
650 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 280-270 | 0.165 | 0.195 |  | 0.596 | 0.228 |  | 0.232 | 0.352 |  | 0.165 | 0.596
900 | 2.85 | 3.453 | 3.557 | 3.76 |  | 3.608 | 3.5167 | 3.797 | 3.248 | 2.85 | 3.797 | 320-270 | -0.651 | -0.721 |  | -0.714 | -0.779 |  | -0.699 | -0.649 |  | -0.779 | -0.649
910 | 2.858 | 3.456 | 3.564 | 3.764 |  | 3.618 | 3.5361 | 3.801 | 3.256 | 2.858 | 3.801 | 290-270 | 0.067 | 0.029 |  | 0.065 | 0.022 |  | 0.085 | 0.02 |  | 0.02 | 0.085
920 | 3.308 | 3.703 | 3.805 | 4.013 |  | 4.029 | 3.7083 | 4.061 | 3.508 | 3.308 | 4.061 | 300-270 | 0.251 | 0.147 |  | 0.246 | 0.044 |  | 0.077 | 0.297 |  | 0.044 | 0.297
930 | 3.355 | 3.732 | 3.832 | 4.042 |  | 4.064 | 3.7444 |  | 3.536 | 3.355 | 4.064 | 310-300 | 0.46 | 0.25 |  | 0.263 | 0.201 |  | 0.486 |  |  | 0.201 | 0.486
940 | 3.98 | 5.028 | 5.665 | 6.116 |  | 6.117 | 5.1222 | 6.428 | 5.322 | 3.98 | 6.428 | ANNUAL COOLING [MWH]
950 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | SUMMARY
960 | 2.41 | 2.751 | 2.727 | 2.863 |  | 2.852 | 2.522 | 2.779 | 2.603 | 2.41 | 2.863 | CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | MIN | MAX
195 | 2.004 | [7 empty] | 2.294 | 2.004 | 2.004 | 200-195 | 0.156 | [8 empty] | 0.156 | 0.156
200 | 2.651 | [8 empty] | 2.651 | 2.651 | 210-200 | -0.408 | [8 empty] | -0.408 | -0.408
210 | 2.701 | 2.973 |  |  |  |  | 2.9806 | 3.325 |  | 2.701 | 3.325 | 220-215 | -0.453 | [8 empty] | -0.453 | -0.453
215 | 2.787 | [8 empty] | 2.787 | 2.787 | 215-200 | 0.069 | [8 empty] | 0.069 | 0.069
220 | 2.867 | 3.28 | 3.465 | 3.695 |  | 3.348 | 3.3361 | 3.52 | 3.245 | 2.867 | 3.695 | 220-210 | 0.024 | 0.088 |  |  |  |  | 0.0689 | 0.042 |  | 0.024 | 0.088
230 | 4.386 | 4.984 | 4.994 | 5.279 |  | 5.159 | 4.8917 | 5.107 | 4.743 | 4.386 | 5.279 | 230-220 | 0.268 | 0.275 | 0.293 | 0.304 | 0.304 | 0.286 | 0.3032 | 0.302 | 0.303 | 0.268 | 0.304
240 | 2.685 | 3.1 | 3.282 | 3.495 |  | 3.159 | 3.1528 | 3.333 | 3.062 | 2.685 | 3.495 | 240-220 | 0.229 | 0.371 | 0.261 | 0.412 | 0.411 | 0.374 | 0.3772 | 0.362 | 0.32 | 0.229 | 0.412
250 | 2.866 | 3.279 | 3.465 | 3.695 |  | 3.341 | 3.3361 | 3.525 | 3.245 | 2.866 | 3.695 | 250-220 | 3.027 | 1.844 | 1.778 | 2.097 | 2.096 | 1.752 | 1.9472 | 2.697 | 3.726 | 1.752 | 3.027
270 | 2.863 | 3.277 |  | 3.661 |  |  | 3.3361 | 3.738 |  | 2.863 | 3.738 | 270-220 | 7.342 | 7.969 |  | 9.001 | 9.515 |  | 8.0272 | 8.031 |  | 7.342 | 9.515
280 | 2.864 | 3.278 |  | 3.685 |  |  | 3.3361 | 3.759 |  | 2.864 | 3.759 | 280-270 | -2.655 | -2.775 |  | -3.317 | -3.236 |  | -3.003 | -2.457 |  | -3.317 | -2.457
290 | 2.863 | 3.277 |  | 3.661 |  |  | 3.3278 | 3.738 |  | 2.863 | 3.738 | 320-270 | -2.467 | -2.764 |  | -3.103 | -3.046 |  | -2.808 | -3.051 |  | -3.103 | -2.467
300 | 3.014 | 3.276 |  | 3.681 |  |  | 3.3278 | 3.77 |  | 3.014 | 3.77 | 290-270 | -2.324 | -1.659 |  | -1.957 | -2.261 |  | -2.065 | -1.283 |  | -2.324 | -1.283
310 | 3.015 | 3.277 |  | 3.669 |  |  | 3.3278 |  |  | 3.015 | 3.669 | 300-270 | -3.226 | -2.834 |  | -3.163 | -3.25 |  | -3.043 | -2.933 |  | -3.25 | -2.834
320 | 2.861 | 3.275 |  | 3.651 |  |  | 3.3361 | 3.735 |  | 2.861 | 3.735 | 310-300 | -1.57 | -1.266 |  | -1.42 | -1.629 |  | -1.994 |  |  | -1.994 | -1.266
395 | 2.062 | 2.209 | 2.328 | 2.385 |  | 2.263 | 2.2211 | 2.27 | 2.301 | 2.062 | 2.385 | PEAK HEATING [KW]
400 | 2.867 | 3.28 | 3.476 | 3.695 |  | 3.342 | 3.3361 | 3.52 | 3.255 | 2.867 | 3.695 |  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | SUMMARY
410 | 3.625 | 4.124 | 4.233 | 4.487 |  | 4.227 | 4.1139 | 4.314 | 4.002 | 3.625 | 4.487 | CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | MIN | MAX
420 | 3.443 | 3.944 | 4.05 | 4.287 |  | 4.044 | 3.9306 | 4.126 | 3.819 | 3.443 | 4.287 | 200-195 | 0.647 | [8 empty] | 0.647 | 0.647
430 | 3.442 | 3.944 | 4.05 | 4.287 |  | 4.044 | 3.9306 | 4.137 | 3.819 | 3.442 | 4.287 | 210-200 | 0.05 | [8 empty] | 0.05 | 0.05
440 | 3.439 | 3.942 |  | 4.277 |  |  | 3.9306 | 4.376 |  | 3.439 | 4.376 | 220-215 | 0.08 | [8 empty] | 0.08 | 0.08
800 | 3.227 | 3.793 | 3.909 | 4.138 |  | 3.902 | 3.7861 | 3.939 | 3.634 | 3.227 | 4.138 | 215-200 | 0.136 | [8 empty] | 0.136 | 0.136
810 | 2.979 | 3.566 |  | 3.915 |  |  | 3.6056 | 3.963 |  | 2.979 | 3.963 | 220-210 | 0.166 | 0.307 |  |  |  |  | 0.35556 | 0.195 |  | 0.166 | 0.35556
[12 empty] | 230-220 | 1.519 | 1.704 | 1.529 | 1.584 |  | 1.811 | 1.5556 | 1.587 | 1.498 | 1.519 | 1.811
[12 empty] | 240-220 | -0.182 | -0.18 | -0.183 | -0.2 |  | -0.189 | -0.18333 | -0.187 | -0.183 | -0.2 | -0.18
[12 empty] | 250-220 | -0.001 | -0.001 | 0 | 0 |  | -0.007 | 0 | 0.005 | 0 | -0.007 | 0.005
[12 empty] | 270-220 | -0.004 | -0.003 |  | -0.034 |  |  | 0 | 0.218 |  | -0.034 | 0.218
[12 empty] | 280-270 | 0.001 | 0.001 |  | 0.024 |  |  | 0 | 0.021 |  | 0 | 0.024
[12 empty] | 320-270 | -0.002 | -0.002 |  | -0.01 |  |  | 0 | -0.003 |  | -0.01 | 0
[12 empty] | 290-270 | 0 | 0 |  | 0 |  |  | -0.0083333 | 0 |  | -0.0083333 | 0
[12 empty] | 300-270 | 0.151 | -0.001 |  | 0.02 |  |  | -0.0083333 | 0.032 |  | -0.0083333 | 0.151
[12 empty] | 310-300 | 0.001 | 0.001 |  | -0.012 |  |  | 0 |  |  | -0.012 | 0.001
PEAK COOLING [KW]
[13 empty] | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | SUMMARY
[12 empty] | CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | MIN | MAX
[12 empty] | 200-195 | 0.212 | [8 empty] | 0.212 | 0.212
[12 empty] | 210-200 | -0.387 | [8 empty] | -0.387 | -0.387
ANNUAL HOURLY INTEGRATED PEAK COOLING LOADS | [11 empty] | 220-215 | -0.447 | [8 empty] | -0.447 | -0.447
CODENAME: | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR |  |  | 215-200 | 0.144 | [8 empty] | 0.144 | 0.144
COUNTRY: | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | SUMMARY |  | 220-210 | 0.084 | 0.149 |  |  |  |  | 0.11111 | 0.071 |  | 0.071 | 0.149
CASE# | kW | kW | kW | kW | kW | kW | kW | kW | KW | MIN | MAX | 230-220 | 0.499 | 0.48 | 0.518 | 0.535 |  | 0.485 | 0.52889 | 0.536 | 0.513 | 0.48 | 0.536
600 | 6.194 | 5.965 | 6.656 | 6.827 |  | 6.286 | 6.4861 | 6.812 | 6.965 | 5.965 | 6.827 | 240-220 | 0.179 | 0.181 | 0.182 | 0.2 |  | 0.183 | 0.1825 | 0.184 | 0.182 | 0.179 | 0.2
610 | 5.669 | 5.824 | 6.064 | 6.371 |  | 6.17 | 5.675 | 6.146 | 6.482 | 5.669 | 6.371 | 250-220 | 2.8 | 1.87 | 1.668 | 1.25 |  | 1.043 | 2.0489 | 3.699 | 2.141 | 1.043 | 3.699
620 | 3.634 | 4.075 | 4.43 | 4.593 |  | 4.297 | 4.275 | 5.096 | 4.679 | 3.634 | 5.096 | 270-220 | 5.796 | 5.475 |  | 5.894 |  |  | 5.585 | 5.654 |  | 5.475 | 5.894
630 | 3.072 | 3.704 | 3.588 | 4.116 |  | 3.665 | 3.6083 |  | 3.834 | 3.072 | 4.116 | 280-270 | -1.912 | -2.01 |  | -2.014 |  |  | -1.9778 | -1.631 |  | -2.014 | -1.631
640 | 6.161 | 5.892 | 6.576 | 6.776 |  | 6.25 | 6.4417 | 6.771 | 6.903 | 5.892 | 6.776 | 320-270 | -0.655 | -0.695 |  | -0.681 |  |  | -0.58611 | -0.726 |  | -0.726 | -0.58611
650 | 6.031 | 5.831 | 6.516 | 6.671 |  | 6.143 | 6.3778 | 6.679 | 6.843 | 5.831 | 6.679 | 290-270 | -0.087 | -0.086 |  | -0.258 |  |  | -0.56111 | -0.246 |  | -0.56111 | -0.086
900 | 2.888 | 3.155 | 3.458 | 3.871 |  | 3.334 | 3.5667 | 3.457 | 3.778 | 2.888 | 3.871 | 300-270 | -2.952 | -2.548 |  | -2.577 |  |  | -2.4861 | -1.938 |  | -2.952 | -1.938
910 | 1.896 | 2.5 | 2.336 | 3.277 |  | 2.786 | 2.7917 | 3.147 | 2.703 | 1.896 | 3.277 | 310-300 | -0.556 | -0.344 |  | -0.493 |  |  | -0.68889 |  |  | -0.68889 | -0.344
920 | 2.385 | 2.933 | 3.109 | 3.487 |  | 3.071 | 3.05 | 3.505 | 3.342 | 2.385 | 3.505
930 | 1.873 | 2.546 | 2.388 | 3.08 |  | 2.486 | 2.4983 |  | 2.638 | 1.873 | 3.08
940 | 2.888 | 3.155 | 3.458 | 3.871 |  | 3.334 | 3.5667 | 3.457 | 3.778 | 2.888 | 3.871
950 | 2.033 | 2.621 | 2.664 | 3.17 |  | 2.677 | 2.6861 | 2.867 | 2.917 | 2.033 | 3.17 | LOW MASS IN-DEPTH (CASES 395 THRU 440) SENSITIVITY TESTS
960 | 0.953 | 1.144 | 1.057 | 1.37 |  | 1.179 | 1.378 | 1.403 | 1.408 | 0.953 | 1.403 | ANNUAL HEATING [MWH]
195 | kW: 0.651; KW: 0.689; MIN: 0.651; MAX: 0.651 |  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | SUMMARY
200 | kW: 0.863; MIN: 0.863; MAX: 0.863 | CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | MIN | MAX
210 | kW: 0.476; kW: 1.017; kW: 1.0678; kW: 1.142; MIN: 0.476; MAX: 1.142 | 400-395 | 1.916 | 2.276 | 2.935 | 2.767 | 2.772 | 2.32 | 2.311 | 2.487 | 2.187 | 1.916 | 2.935
215 | kW: 1.007; MIN: 1.007; MAX: 1.007 | 410-400 | 1.696 | 1.798 | 1.736 | 1.76 | 1.761 | 1.732 | 1.77 | 1.759 | 1.721 | 1.696 | 1.798
220 | 0.56 | 1.166 | 0.937 | 1.34 |  | 1.215 | 1.1789 | 1.213 | 1.032 | 0.56 | 1.34 | 420-410 | -1.298 | -1.263 | -1.355 | -1.361 | -1.361 | -1.245 | -1.239 | -1.222 | -1.306 | -1.361 | -1.222
230 | 1.059 | 1.646 | 1.455 | 1.875 |  | 1.7 | 1.7078 | 1.749 | 1.545 | 1.059 | 1.875 | 430-420 | -1.869 | -1.122 | -1.324 | -1.187 | -1.187 | -1.112 | -1.197 | -1.353 | -1.765 | -1.869 | -1.112
240 | 0.739 | 1.347 | 1.119 | 1.54 |  | 1.398 | 1.3614 | 1.397 | 1.214 | 0.739 | 1.54 | 600-430 | -1.133 | -1.715 | -2.118 | -1.952 | -1.59 | -1.78 | -1.628 | -1.148 | -1.315 | -2.118 | -1.133
250 | 3.36 | 3.036 | 2.605 | 2.59 |  | 2.258 | 3.2278 | 4.912 | 3.173 | 2.258 | 4.912 | 440-600 | 0.153 | 0.214 |  | 0.426 | 0.215 |  | 0.226 | 0.28 |  | 0.153 | 0.426
270 | 6.356 | 6.641 |  | 7.234 |  |  | 6.7639 | 6.867 |  | 6.356 | 7.234 | ANNUAL COOLING [MWH]
280 | 4.444 | 4.631 |  | 5.22 |  |  | 4.7861 | 5.236 |  | 4.444 | 5.236 |  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | SUMMARY
290 | 6.269 | 6.555 |  | 6.976 |  |  | 6.2028 | 6.621 |  | 6.2028 | 6.976 | CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | MIN | MAX
300 | 3.404 | 4.093 |  | 4.657 |  |  | 4.2778 | 4.929 |  | 3.404 | 4.929 | 400-395 | 0 | 0.029 | 0.002 | 0.045 | 0.044 | 0.032 | 0.03439 | 0.033 | 0.015 | 0 | 0.045
310 | kW: 2.848; kW: 3.749; kW: 4.164; kW: 3.5889; MIN: 2.848; MAX: 4.164 | 410-400 | 0 | 0.019 | 0.008 | 0.023 | 0.026 | 0.021 | 0.02239 | 0.021 | 0.019 | 0 | 0.026
320 | 5.701 | 5.946 |  | 6.553 |  |  | 6.1778 | 6.141 |  | 5.701 | 6.553 | 420-410 | 0.011 | 0.088 | 0.041 | 0.105 | 0.104 | 0.091 | 0.09043 | 0.078 | 0.07 | 0.011 | 0.105
395 | 0 | 0.362 | 0 | 0.394 |  | 0.356 | 0.3625 | 0.345 | 0.175 | 0 | 0.394 | 430-420 | 0.531 | 0.47 | 0.371 | 0.515 | 0.496 | 0.409 | 0.4599 | 0.732 | 1.001 | 0.371 | 0.732
400 | 0 | 0.581 | 0.265 | 0.666 |  | 0.612 | 0.61333 | 0.572 | 0.407 | 0 | 0.666 | 600-430 | 5.595 | 5.816 | 6.657 | 6.574 | 7.28 | 5.929 | 5.8746 | 5.903 | 6.948 | 5.595 | 7.28
410 | 0.035 | 0.699 | 0.413 | 0.814 |  | 0.724 | 0.74306 | 0.71 | 0.559 | 0.035 | 0.814 | 440-600 | -2.17 | -2.261 |  | -2.604 | -2.76 |  | -2.517 | -2.094 |  | -2.76 | -2.094
420 | 0.258 | 0.923 | 0.631 | 1.047 |  | 0.938 | 0.93778 | 0.921 | 0.792 | 0.258 | 1.047 | PEAK HEATING [KW]
430 | 1.493 | 1.772 | 1.427 | 1.762 |  | 1.575 | 1.7983 | 2.578 | 2.113 | 1.427 | 2.578 |  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | SUMMARY
440 | 4.546 | 4.424 |  | 5.053 |  |  | 4.6861 | 5.278 |  | 4.424 | 5.278 | CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | MIN | MAX
800 | 0.585 | 0.967 | 0.743 | 1.352 |  | 1.028 | 0.98278 | 1.358 | 1.267 | 0.585 | 1.358 | 400-395 | 0.805 | 1.071 | 1.148 | 1.31 |  | 1.079 | 1.115 | 1.25 | 0.954 | 0.805 | 1.31
810 | 1.852 | 2.357 |  | 2.991 |  |  | 2.3436 | 2.862 |  | 1.852 | 2.991 | 410-400 | 0.758 | 0.844 | 0.757 | 0.792 |  | 0.885 | 0.77778 | 0.794 | 0.747 | 0.757 | 0.885
[12 empty] | 420-410 | -0.182 | -0.18 | -0.183 | -0.2 |  | -0.183 | -0.18333 | -0.188 | -0.183 | -0.2 | -0.18
[12 empty] | 430-420 | -0.001 | 0 | 0 | 0 |  | 0 | 0 | 0.011 | 0 | -0.001 | 0.011
[12 empty] | 600-430 | -0.005 | -0.004 | -0.005 | -0.029 |  | -0.007 | 0 | 0.217 | -0.052 | -0.029 | 0.217
[12 empty] | 440-600 | 0.002 | 0.002 |  | 0.019 |  |  | 0 | 0.022 |  | 0 | 0.022
PEAK COOLING [KW]
[13 empty] | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | SUMMARY
[12 empty] | CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | MIN | MAX
[12 empty] | 400-395 | 0 | 0.219 | 0.265 | 0.272 |  | 0.256 | 0.25083 | 0.227 | 0.232 | 0 | 0.272
[12 empty] | 410-400 | 0.035 | 0.118 | 0.148 | 0.148 |  | 0.112 | 0.12972 | 0.138 | 0.152 | 0.035 | 0.148
[12 empty] | 420-410 | 0.223 | 0.224 | 0.218 | 0.233 |  | 0.214 | 0.19472 | 0.211 | 0.233 | 0.19472 | 0.233
[12 empty] | 430-420 | 1.235 | 0.849 | 0.796 | 0.715 |  | 0.637 | 0.86056 | 1.657 | 1.321 | 0.637 | 1.657
[12 empty] | 600-430 | 4.701 | 4.193 | 5.229 | 5.065 |  | 4.711 | 4.6878 | 4.234 | 4.852 | 4.193 | 5.229
[12 empty] | 440-600 | -1.648 | -1.541 |  | -1.774 |  |  | -1.8 | -1.534 |  | -1.8 | -1.534
HIGH MASS BASIC AND IN-DEPTH SENSITIVITY TESTS
FREE-FLOAT TEMPERATURE OUTPUT | [11 empty] | ANNUAL HEATING [MWH]
MAXIMUM ANNUAL HOURLY ZONE TEMPERATURE (C) | [12 empty] | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | SUMMARY
CODENAME: | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR |  |  | CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | MIN | MAX
COUNTRY: | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | SUMMARY |  | 800-430 | -0.561 | -0.535 | -0.599 | -0.567 | -0.586 | -0.501 | -0.56 | -0.649 | -0.956 | -0.649 | -0.501
CASE# | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | MIN | MAX | 900-800 | -3.698 | -4.343 | -5.356 | -4.714 | -4.612 | -4.431 | -4.285 | -3.82 | -4.052 | -5.356 | -3.698
600FF | 64.929 | 65.11 | 69.5 | 68.6 |  | 64.9 | 65.25 | 65.25 | 73.4 | 64.9 | 69.5 | 900-810 | -0.669 | -0.836 |  | -1.107 | -0.84 |  | -0.912 | -0.921 |  | -1.107 | -0.669
900FF | 41.812 | 43.44 | 42.7 | 44.8 |  | 43 | 42.46 | 43.17 | 45.5 | 41.812 | 44.8 | 910-610 | -2.78 | -2.944 | -3.532 | -3.106 | -3.338 | -2.908 | -2.873 | -3.163 | -3.483 | -3.532 | -2.78
650FF | 63.236 | 63.45 | 68.2 | 67 |  | 63.3 | 63.74 | 63.82 | 71.7 | 63.236 | 68.2 | 920-620 | -1.3 | -1.297 | -1.689 | -1.461 | -1.676 | -1.329 | -1.297 | -1.428 | -1.832 | -1.689 | -1.297
950FF | 35.54 | 36.23 | 35.9 | 38.5 |  | 36.1 | 35.67 | 37.58 | 37.1 | 35.54 | 38.5 | 930-630 | -0.907 | -1.012 | -1.134 | -1.128 | -1.273 | -0.927 | -0.884 |  | -1.259 | -1.273 | -0.884
960 | 48.943 | 48.88 | 49 | 51 |  | 50.2 | 55.34 | 48.92 | 51.6 | 48.88 | 55.34 | 940-640 | -1.958 | -1.867 | -2.304 | -2.024 | -2.392 | -1.886 | -1.963 | -1.986 | -2.157 | -2.392 | -1.867
MINIMUM ANNUAL HOURLY ZONE TEMPERATURE (C) | [11 empty] | ANNUAL COOLING [MWH]
CODENAME: | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR |  |  |  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | SUMMARY
COUNTRY: | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | SUMMARY |  | CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | MIN | MAX
CASE# | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | MIN | MAX | 800-430 | -0.429 | -0.393 | -0.367 | -0.432 | -0.462 | -0.368 | -0.4101 | -0.55 | -0.783 | -0.55 | -0.367
600FF | -15.565 | -17.05 | -18.8 | -18 |  | -17.8 | -17.81 | -18.47 | -17.7 | -18.8 | -15.565 | 900-800 | 2.019 | 2.376 | 2.4 | 2.893 | 3.193 | 2.377 | 2.2777 | 2.274 | 3.067 | 2.019 | 3.193
900FF | -1.647 | -3.15 | -4.3 | -4.5 |  | -4 | -6.38 | -5.64 | -2 | -6.38 | -1.647 | 900-810 | 1.08 | 1.195 |  | 1.454 | 1.707 |  | 1.294 | 0.975 |  | 0.975 | 1.707
650FF | -22.564 | -22.96 | -21.6 | -23 |  | -22.9 | -22.83 | -22.91 | -21 | -23 | -21.6 | 910-610 | -3.094 | -3.318 | -3.876 | -3.576 | -3.924 | -3.336 | -3.275 | -3.739 | -4.136 | -3.924 | -3.094
950FF | -19.484 | -20.04 | -18.6 | -19.7 |  | -20.2 | -19.34 | -19.96 | -17.8 | -20.2 | -18.6 | 920-620 | -1.577 | -1.476 | -1.894 | -1.69 | -1.912 | -1.554 | -1.483 | -1.738 | -2.087 | -1.912 | -1.476
960 | 2.729 | 1.63 | 3.9 | 3.1 |  | 1.4 | -2.82 | -0.39 | 6 | -2.82 | 3.9 | 930-630 | -1.09 | -1.174 | -1.223 | -1.32 | -1.463 | -1.05 | -1 |  | -1.412 | -1.463 | -1
AVERAGE ANNUAL HOURLY ZONE TEMPERATURE (C) | [11 empty] | 940-640 | -3.873 | -3.647 | -4.419 | -3.99 | -4.57 | -3.758 | -3.863 | -3.992 | -4.441 | -4.57 | -3.647
CODENAME: | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR |  |  | 950-650 | -4.429 | -4.614 | -5.257 | -4.973 | -5.956 | -4.537 | -4.5584 | -4.685 | -5.929 | -5.956 | -4.429
COUNTRY: | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | SUMMARY |  | PEAK HEATING [KW]
CASE# | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | MIN | MAX |  | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | SUMMARY
600FF | 25.126 | 25.43 | 24.6 | 25.48 | 25.93 | 25.2 | 24.49 | 24.22 | 26.993 | 24.22 | 25.93 | CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | MIN | MAX
900FF | 25.453 | 25.93 | 24.7 | 25.49 | 25.72 | 25.2 | 24.47 | 24.45 | 27.0563 | 24.45 | 25.93 | 800-430 | -0.215 | -0.151 | -0.141 | -0.149 |  | -0.142 | -0.14444 | -0.198 | -0.185 | -0.215 | -0.141
650FF | 18.234 | 18.69 | 19.1 | 18.96 | 19.62 | 18.4 | 17.99 | 18.36 | 20.4281 | 17.99 | 19.62 | 900-800 | -0.377 | -0.34 | -0.352 | -0.378 |  | -0.294 | -0.26944 | -0.142 | -0.386 | -0.378 | -0.142
950FF | 14.14 | 14.26 | 14.3 | 14.97 | 14.29 | 14 | 14.53 | 14.64 | 15.0742 | 14 | 14.97 | 900-810 | -0.129 | -0.113 |  | -0.155 |  |  | -0.088889 | -0.166 |  | -0.166 | -0.088889
960 | 27.49 | 27.72 | 28 | 28.69 | 28.54 | 28 | 28.96 | 26.43 | 30.0216 | 26.43 | 28.96 | 910-610 | -0.579 | -0.485 | -0.47 | -0.494 |  | -0.419 | -0.38611 | -0.553 | -0.499 | -0.579 | -0.38611
[12 empty] | 920-620 | -0.283 | -0.238 | -0.241 | -0.264 |  | -0.248 | -0.21389 | -0.318 | -0.277 | -0.318 | -0.21389
[12 empty] | 930-630 | -0.237 | -0.209 | -0.193 | -0.238 |  | -0.214 | -0.17778 |  | -0.226 | -0.238 | -0.17778
[12 empty] | 940-640 | -1.252 | -0.458 | -0.278 | -0.414 |  | -0.23 | -0.6 | -0.526 | -0.334 | -1.252 | -0.23
PEAK COOLING [KW]
[13 empty] | ESP | BLAST | DOE2 | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR | SUMMARY
[12 empty] | CASES | UK-DMU | US/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA | MIN | MAX
[12 empty] | 800-430 | -0.908 | -0.805 | -0.684 | -0.41 |  | -0.547 | -0.81556 | -1.22 | -0.846 | -1.22 | -0.41
[12 empty] | 900-800 | 2.303 | 2.188 | 2.715 | 2.519 |  | 2.306 | 2.5839 | 2.099 | 2.511 | 2.099 | 2.715
[12 empty] | 900-810 | 1.036 | 0.798 |  | 0.88 |  |  | 1.2231 | 0.595 |  | 0.595 | 1.2231
SOLAR RADIATION | [11 empty] | 910-610 | -3.773 | -3.324 | -3.728 | -3.094 |  | -3.384 | -2.8833 | -2.999 | -3.779 | -3.773 | -2.8833
ANNUAL INCIDENT TOTAL | [11 empty] | 920-620 | -1.249 | -1.142 | -1.321 | -1.106 |  | -1.226 | -1.225 | -1.591 | -1.337 | -1.591 | -1.106
CASE 600 | [11 empty] | 930-630 | -1.199 | -1.158 | -1.2 | -1.036 |  | -1.179 | -1.11 |  | -1.196 | -1.2 | -1.036
[12 empty] | 940-640 | -3.273 | -2.737 | -3.118 | -2.905 |  | -2.916 | -2.875 | -3.314 | -3.125 | -3.314 | -2.737
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR |  |  | 950-650 | -3.998 | -3.21 | -3.852 | -3.501 |  | -3.466 | -3.6917 | -3.812 | -3.926 | -3.998 | -3.21
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA
SURFACE | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2
= | [12 empty] | ANNUAL TRANSMISSIVITY COEFFICIENT OF WINDOWS | bar: kW to KW
NORTH | 427 |  | 434 | 456 | 407.3 | 457 | 367.4 | 453 | 450.2906 |  |  | (ANNUAL UNSHADED TRANSMITTED SOLRAD)/(ANNUAL UNSHADED INCIDENT SOLRAD)
EAST | 959 |  | 1155 | 1083 | 1217.3 | 1082 | 1101 | 962 | 1165.8275
WEST | 1086 |  | 1079 | 1003 | 856.5 | 1002 | 1012 | 1090 | 1088.9381 |  |  | CODENAME: | ESP | BLAST | DOE2.1D | SUNCODE | SERIRES | S3PAS | TRNSYS | TASE | YOUR
SOUTH | 1456 |  | 1566 | 1476 | 1467.7 | 1474 | 1522 | 1468 | 1579.3093 |  |  | COUNTRY: | UK-DMU | US/IT | USA | USA | UK | SPAIN | BEL/UK | FINLAND | DATA
HORZ. | 1797 |  | 1831 | 1832 | 1831.8 | 1832 | 1832 | 1832 | 1830.85 |  |  | CASE#
= | bar: kW to KW
[12 empty] | 920WEST | 0.67403 |  | 0.68119 | 0.68694 | 0.65728 | 0.64072 | 0.65382 | 0.64771 | 0.681
[12 empty] | 900SOUTH | 0.64973 |  | 0.67114 | 0.65176 | 0.6502 | 0.62822 | 0.64663 | 0.62262 | 0.672
SOLAR RADIATION
UNSHADED ANNUAL TRANSMITTED
ANNUAL SHADING COEFFICIENT OF WINDOW SHADING DEVICES: OVERHANGS & FINS
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR |  |  | (1-(ANNUAL SHADED TRANSMITTED SOLRAD)/(ANNUAL UNSHADED TRANSMITTED SOLRAD))
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA
CASE# | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 |  |  | CODENAME: | ESP | BLAST | DOE2.1D | SUNCODE | SERIRES | S3PAS | TRNSYS | TASE | YOUR
= | [11 empty] | COUNTRY: | UK-DMU | US/IT | USA | USA | UK | SPAIN | BEL/UK | FINLAND | DATA | bar: kW to KW
920WEST | 732 |  | 735 | 689 | 562.96 | 642 | 661.67 | 706 | 704.776 |  |  | CASE#
900SOUTH | 946 |  | 1051 | 962 | 954.3 | 926 | 984.17 | 914 | 1004.936
= | [11 empty] | 930/920 W | 0.18169 |  | 0.34558 | 0.19594 | 0.21611 | 0.32866 | 0.33879 |  | 0.56 | bar: kW to KW
[12 empty] | 910/900 S | 0.17019 |  | 0.20932 | 0.16528 | 0.18803 | 0.18251 | 0.20542 | 0.11488 | 0.464
ANNUAL HOURLY INTEGRATED PEAK HEATING LOADS
[12 empty] | CODENAME: |  | ESP |  |  | BLAST |  |  | DOE2 |  |  | SRES/SUN |  |  | SERIRES |  |  | S3PAS |  |  | TRNSYS |  |  | TASE |  |  | YOUR
[12 empty] | COUNTRY: |  | UK-DMU |  |  | USA/ITALY |  |  | USA |  |  | USA |  |  | UK-BRE |  |  | SPAIN |  |  | BEL/UK |  |  | FINLAND |  |  | DATA |  | SUMMARY
[12 empty] | CASE# | KW | DATE | HR | KW | DATE | HR | KW | DATE | HR | KW | DATE | HR | KW | DATE | HR | KW | DATE | HR | KW | DATE | HR | KW | DATE | HR | KW | DATE | HR | MIN | MAX
SOLAR RADIATION | [11 empty] | 600 | 3.437 | 1993-01-04 | 5 | 3.94 | JAN 04 | 5 | 4.045 | JAN 04 | 5 | 4.258 | JAN 04 | 2 |  |  |  | 4.037 | JAN 04 | 2 | 3.9306 | Jan-04 | 6 | 4.354 | JAN 04 | 2 | 3.767 | 2006-01-04 | 5 | 3.437 | 4.354
SHADED ANNUAL TRANSMITTED | [11 empty] | 610 | 3.437 | 1993-01-04 | 5 | 3.941 | JAN 04 | 5 | 4.034 | JAN 04 | 5 | 4.258 | JAN 04 | 2 |  |  |  | 4.037 | JAN 04 | 2 | 3.9222 | Jan-04 | 6 | 4.354 | JAN 04 | 2 | 3.755 | 2006-01-04 | 5 | 3.437 | 4.354
[12 empty] | 620 | 3.591 | 1993-01-04 | 6 | 3.941 | JAN 04 | 5 | 4.046 | JAN 04 | 5 | 4.277 | JAN 04 | 2 |  |  |  | 4.277 | JAN 04 | 2 | 3.9222 | Jan-04 | 6 | 4.379 | JAN 04 | 2 | 3.785 | 2006-01-04 | 5 | 3.591 | 4.379
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR |  |  | 630 | 3.592 | 1993-01-04 | 7 | 3.941 | JAN 04 | 5 | 4.025 | JAN 04 | 5 | 4.28 | JAN 04 | 2 |  |  |  | 4.278 | JAN 04 | 2 | 3.9222 | Jan-04 | 6 |  |  |  | 3.762 | 2006-01-04 | 5 | 3.592 | 4.28
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA |  |  | 640 | 5.232 | 1993-01-04 | 7 | 5.486 | JAN 04 | 8 | 5.943 | JAN 04 | 8 | 6.53 | JAN 04 | 8 |  |  |  | 6.347 | JAN 04 | 8 | 5.7222 | Jan-04 | 8 | 6.954 | JAN 04 | 8 | 5.656 | 2006-01-04 | 5 | 5.232 | 6.954
CASE# | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 | kWh/m2 |  |  | 650 | 0 |  |  | 0 |  |  | 0 |  |  | 0 | [5 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0
= | [11 empty] | 900 | 2.85 | 1993-01-04 | 7 | 3.453 | JAN 04 | 7 | 3.557 | JAN 04 | 7 | 3.76 | JAN 04 | 7 |  |  |  | 3.608 | JAN 04 | 8 | 3.5167 | Jan-04 | 7 | 3.797 | JAN 04 | 7 | 3.248 | 2006-01-04 | 7 | 2.85 | 3.797 | bar: kW to KW
930WEST | 599 |  | 481 | 554 | 441.3 | 431 | 437.5 |  | 462.231 |  |  | 910 | 2.858 | 1993-01-04 | 7 | 3.456 | JAN 04 | 7 | 3.564 | JAN 04 | 7 | 3.764 | JAN 04 | 7 |  |  |  | 3.618 | JAN 04 | 8 | 3.5361 | Jan-04 | 7 | 3.801 | JAN 04 | 7 | 3.256 | 2006-01-04 | 7 | 2.858 | 3.801
910SOUTH | 785 |  | 831 | 803 | 774.86 | 757 | 782 | 809 | 803.901 |  |  | 920 | 3.308 | 1993-01-04 | 7 | 3.703 | JAN 04 | 7 | 3.805 | JAN 04 | 7 | 4.013 | JAN 04 | 7 |  |  |  | 4.029 | JAN 04 | 7 | 3.7083 | Jan-04 | 7 | 4.061 | JAN 04 | 7 | 3.508 | 2006-01-04 | 7 | 3.308 | 4.061
= | [11 empty] | 930 | 3.355 | 1993-01-04 | 7 | 3.732 | JAN 04 | 7 | 3.832 | JAN 04 | 7 | 4.042 | JAN 04 | 7 |  |  |  | 4.064 | JAN 04 | 7 | 3.7444 | Jan-04 | 7 |  |  |  | 3.536 | 2006-01-04 | 7 | 3.355 | 4.064 | bar: kW to KW
[12 empty] | 940 | 3.98 | 1993-01-04 | 7 | 5.028 | JAN 04 | 8 | 5.665 | JAN 04 | 8 | 6.116 | JAN 04 | 8 |  |  |  | 6.117 | JAN 04 | 8 | 5.1222 | Jan-03 | 9 | 6.428 | JAN 04 | 8 | 5.322 | 2006-01-04 | 8 | 3.98 | 6.428
[12 empty] | 950 | 0 |  |  | 0 |  |  | 0 |  |  | 0 | [5 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0
[12 empty] | 960 | 2.41 | 1993-01-04 | 7 | 2.751 | JAN 04 | 8 | 2.727 | JAN 04 | 8 | 2.863 | JAN 04 | 8 |  |  |  | 2.852 | JAN 04 | 8 | 2.522 | Jan-04 | 8 | 2.779 | JAN 04 | 8 | 2.603 | 2006-01-04 | 8 | 2.41 | 2.863
[12 empty] | 195 | 2.004 | 1993-01-04 | 2 | [21 empty] | 2.294 | 2006-01-04 | 3 | 2.004 | 2.004
[12 empty] | 200 | 2.651 | 1993-01-04 | 5 | [24 empty] | 2.651 | 2.651
HOURLY INCIDENT SOLAR RADIATION CLOUDY DAY, MARCH 5 | [11 empty] | 210 | 2.701 | 1993-01-04 | 5 | 2.973 | JAN 04 | 5 | [12 empty] | 2.9806 | Jan-04 | 5 | 3.325 | JAN 04 | 2 |  |  |  | 2.701 | 3.325
CASE 600 OR 900 | [11 empty] | 215 | 2.787 | 1993-01-04 | 5 | [24 empty] | 2.787 | 2.787
SOUTH SURFACE | [11 empty] | 220 | 2.867 | 1993-01-04 | 5 | 3.28 | JAN 04 | 5 | 3.465 | JAN 04 | 5 | 3.695 | JAN 04 | 2 |  |  |  | 3.348 | JAN 04 | 8 | 3.3361 | Jan-04 | 6 | 3.52 | JAN 04 | 2 | 3.245 | 2006-01-04 | 5 | 2.867 | 3.695
[12 empty] | 230 | 4.386 | 1993-01-04 | 5 | 4.984 | JAN 04 | 2 | 4.994 | JAN 04 | 2 | 5.279 | JAN 04 | 2 |  |  |  | 5.159 | JAN 04 | 2 | 4.8917 | Jan-04 | 6 | 5.107 | JAN 04 | 2 | 4.743 | 2006-01-04 | 2 | 4.386 | 5.279
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR |  |  | 240 | 2.685 | 1993-01-04 | 5 | 3.1 | JAN 04 | 5 | 3.282 | JAN 04 | 5 | 3.495 | JAN 04 | 2 |  |  |  | 3.159 | JAN 04 | 8 | 3.1528 | Jan-04 | 6 | 3.333 | JAN 04 | 8 | 3.062 | 2006-01-04 | 5 | 2.685 | 3.495
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA |  |  | 250 | 2.866 | 1993-01-04 | 5 | 3.279 | JAN 04 | 5 | 3.465 | JAN 04 | 5 | 3.695 | JAN 04 | 2 |  |  |  | 3.341 | JAN 04 | 6 | 3.3361 | Jan-04 | 6 | 3.525 | JAN 04 | 2 | 3.245 | 2006-01-04 | 5 | 2.866 | 3.695
HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 |  |  | 270 | 2.863 | 1993-01-04 | 5 | 3.277 | JAN 04 | 5 |  |  |  | 3.661 | JAN 04 | 2 | [6 empty] | 3.3361 | Jan-04 | 6 | 3.738 | JAN 04 | 2 |  |  |  | 2.863 | 3.738
= | [11 empty] | 280 | 2.864 | 1993-01-04 | 5 | 3.278 | JAN 04 | 5 |  |  |  | 3.685 | JAN 04 | 2 | [6 empty] | 3.3361 | Jan-04 | 6 | 3.759 | JAN 04 | 2 |  |  |  | 2.864 | 3.759 | bar: kW to KW
1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 290 | 2.863 | 1993-01-04 | 5 | 3.277 | JAN 04 | 5 |  |  |  | 3.661 | JAN 04 | 2 | [6 empty] | 3.3278 | Jan-04 | 6 | 3.738 | JAN 04 | 2 |  |  |  | 2.863 | 3.738
2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 300 | 3.014 | 1993-01-04 | 6 | 3.276 | JAN 04 | 5 |  |  |  | 3.681 | JAN 04 | 2 | [6 empty] | 3.3278 | Jan-04 | 6 | 3.77 | JAN 04 | 2 |  |  |  | 3.014 | 3.77
3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 310 | 3.015 | 1993-01-04 | 6 | 3.277 | JAN 04 | 5 |  |  |  | 3.669 | JAN 04 | 2 | [6 empty] | 3.3278 | Jan-04 | 6 | [6 empty] | 3.015 | 3.669
4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 320 | 2.861 | 1993-01-04 | 5 | 3.275 | JAN 04 | 5 |  |  |  | 3.651 | JAN 04 | 2 | [6 empty] | 3.3361 | Jan-04 | 6 | 3.735 | JAN 04 | 3 |  |  |  | 2.861 | 3.735
5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 395 | 2.062 | 1993-01-04 | 7 | 2.209 | JAN 04 | 8 | 2.328 | JAN 04 | 3 | 2.385 | JAN 04 | 3 |  |  |  | 2.263 | JAN 04 | 4 | 2.2211 | Jan-04 | 8 | 2.27 | JAN 04 | 3 | 2.301 | 2006-01-04 | 3 | 2.062 | 2.385
6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 400 | 2.867 | 1993-01-04 | 5 | 3.28 | JAN 04 | 5 | 3.476 | JAN 04 | 5 | 3.695 | JAN 04 | 2 |  |  |  | 3.342 | JAN 04 | 8 | 3.3361 | Jan-04 | 6 | 3.52 | JAN 04 | 2 | 3.255 | 2006-01-04 | 5 | 2.867 | 3.695
7 | 1.6 |  | 1.5 | 3.0447 | 3.02 | 3 | 3.05 | 3 | 1.49 |  |  | 410 | 3.625 | 1993-01-04 | 5 | 4.124 | JAN 04 | 5 | 4.233 | JAN 04 | 5 | 4.487 | JAN 04 | 2 |  |  |  | 4.227 | JAN 04 | 2 | 4.1139 | Jan-04 | 6 | 4.314 | JAN 04 | 2 | 4.002 | 2006-01-04 | 5 | 3.625 | 4.487
8 | 13.8 |  | 12.59 | 20.6464 | 20.59 | 21 | 20.69 | 20.68 | 12.47 |  |  | 420 | 3.443 | 1993-01-04 | 5 | 3.944 | JAN 04 | 5 | 4.05 | JAN 04 | 5 | 4.287 | JAN 04 | 2 |  |  |  | 4.044 | JAN 04 | 2 | 3.9306 | Jan-04 | 6 | 4.126 | JAN 04 | 2 | 3.819 | 2006-01-04 | 5 | 3.443 | 4.287
9 | 31.6 |  | 30.01 | 38.8836 | 38.83 | 39 | 38.94 | 38.94 | 29.43 |  |  | 430 | 3.442 | 1993-01-04 | 5 | 3.944 | JAN 04 | 5 | 4.05 | JAN 04 | 5 | 4.287 | JAN 04 | 2 |  |  |  | 4.044 | JAN 04 | 2 | 3.9306 | Jan-04 | 6 | 4.137 | JAN 04 | 2 | 3.819 | 2006-01-04 | 5 | 3.442 | 4.287
10 | 48.3 |  | 46.23 | 54.5664 | 54.53 | 55 | 54.67 | 54.56 | 45.63 |  |  | 440 | 3.439 | 1993-01-04 | 5 | 3.942 | JAN 04 | 5 |  |  |  | 4.277 | JAN 04 | 2 | [6 empty] | 3.9306 | Jan-04 | 6 | 4.376 | JAN 04 | 2 |  |  |  | 3.439 | 4.376
11 | 61.6 |  | 59.31 | 65.9733 | 54.77 | 66 | 66.08 | 65.99 | 58.57 |  |  | 800 | 3.227 | 1993-01-04 | 5 | 3.793 | JAN 04 | 7 | 3.909 | JAN 04 | 7 | 4.138 | JAN 04 | 2 |  |  |  | 3.902 | JAN 04 | 8 | 3.7861 | Jan-04 | 7 | 3.939 | JAN 04 | 7 | 3.634 | 2006-01-04 | 7 | 3.227 | 4.138
12 | 69.3 |  | 65.05 | 71.7839 | 59.65 | 72 | 71.92 | 71.74 | 64.28 |  |  | 810 | 2.979 | 1993-01-04 | 7 | 3.566 | JAN 04 | 7 |  |  |  | 3.915 | JAN 04 | 7 | [6 empty] | 3.6056 | Jan-04 | 7 | 3.963 | JAN 04 | 7 |  |  |  | 2.979 | 3.963
13 | 71.7 |  | 66.98 | 72.2839 | 60.1 | 72 | 72.42 | 72.3 | 66.18
14 | 68.1 |  | 63.11 | 66.4075 | 55.24 | 66 | 66.53 | 66.38 | 62.33
15 | 58.9 |  | 51.79 | 54.8997 | 45.68 | 55 | 55 | 54.8 | 51.13
16 | 44.4 |  | 37.13 | 38.8836 | 32.37 | 39 | 38.94 | 38.84 | 36.61
17 | 26.9 |  | 19.14 | 20.4797 | 17.06 | 20 | 20.52 | 20.46 | 18.91
18 | 8.7 |  | 4.62 | 3.0447 | 2.54 | 3 | 3.05 | 0 | 4.59
19 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
= | bar: kW to KW
ANNUAL HOURLY INTEGRATED PEAK COOLING LOADS
[12 empty] | CODENAME: |  | ESP |  |  | BLAST |  |  | DOE2 |  |  | SRES/SUN |  |  | SERIRES |  |  | S3PAS |  |  | TRNSYS |  |  | TASE |  |  | YOUR
[12 empty] | COUNTRY: |  | UK-DMU |  |  | USA/ITALY |  |  | USA |  |  | USA |  |  | UK-BRE |  |  | SPAIN |  |  | BEL/UK |  |  | FINLAND |  |  | DATA |  | SUMMARY
[12 empty] | CASE# | KW | DATE | HR | KW | DATE | HR | KW | DATE | HR | KW | DATE | HR | KW | DATE | HR | KW | DATE | HR | KW | DATE |  | KW | DATE | HR | KW | DATE | HR | MIN | MAX
[12 empty] | 600 | 6.194 | 1993-10-17 | 13 | 5.965 | OCT 16 | 14 | 6.656 | OCT 16 | 13 | 6.827 | OCT 16 | 14 |  |  |  | 6.286 | NOV 25 | -6.194 | 6.4861 | Oct-16 | 14 | 6.812 | OCT 17 | 14 | 6.965 | 2006-10-17 | 13 | 5.965 | 6.827
[12 empty] | 610 | 5.669 | 1993-11-25 | 13 | 5.824 | NOV 25 | 14 | 6.064 | JAN 13 | 14 | 6.371 | NOV 25 | 14 |  |  |  | 6.17 | NOV 25 | -5.669 | 5.675 | 1925-11-01 | 14 | 6.146 | OCT 17 | 14 | 6.482 | 2006-01-13 | 14 | 5.669 | 6.371
HOURLY INCIDENT SOLAR RADIATION CLOUDY DAY, MARCH 5 | [11 empty] | 620 | 3.634 | 1993-07-26 | 16 | 4.075 | JUL 26 | 17 | 4.43 | JUL 26 | 17 | 4.593 | JUL 26 | 17 |  |  |  | 4.297 | JUL 26 | -3.634 | 4.275 | 1926-07-01 | 17 | 5.096 | JUL 26 | 16 | 4.679 | 2006-07-26 | 17 | 3.634 | 5.096
CASE 600 OR 900 | [11 empty] | 630 | 3.072 | 1993-07-26 | 16 | 3.704 | JUL 26 | 17 | 3.588 | JUL 26 | 17 | 4.116 | JUL 26 | 17 |  |  |  | 3.665 | JUL 26 | -3.072 | 3.6083 | 1926-07-01 | 17 |  |  |  | 3.834 | 2006-07-26 | 17 | 3.072 | 4.116
WEST SURFACE | [11 empty] | 640 | 6.161 | 1993-10-17 | 13 | 5.892 | OCT 16 | 14 | 6.576 | OCT 16 | 14 | 6.776 | OCT 16 | 14 |  |  |  | 6.25 | NOV 25 | -6.161 | 6.4417 | Oct-16 | 14 | 6.771 | OCT 17 | 14 | 6.903 | 2006-10-16 | 14 | 5.892 | 6.776
[12 empty] | 650 | 6.031 | 1993-10-17 | 13 | 5.831 | OCT 16 | 14 | 6.516 | OCT 16 | 14 | 6.671 | OCT 16 | 14 |  |  |  | 6.143 | NOV 25 | -6.031 | 6.3778 | Oct-17 | 14 | 6.679 | OCT 17 | 14 | 6.843 | 2006-10-16 | 14 | 5.831 | 6.679
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR |  |  | 900 | 2.888 | 1993-10-17 | 14 | 3.155 | OCT 06 | 15 | 3.458 | OCT 17 | 14 | 3.871 | OCT 17 | 14 |  |  |  | 3.334 | OCT 17 | -2.888 | 3.5667 | Oct-17 | 15 | 3.457 | OCT 17 | 15 | 3.778 | 2006-10-17 | 14 | 2.888 | 3.871
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA |  |  | 910 | 1.896 | 1993-10-17 | 15 | 2.5 | OCT 21 | 15 | 2.336 | OCT 17 | 15 | 3.277 | OCT 17 | 15 |  |  |  | 2.786 | OCT 17 | -1.896 | 2.7917 | Oct-17 | 15 | 3.147 | OCT 17 | 15 | 2.703 | 2006-10-17 | 15 | 1.896 | 3.277
HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 |  |  | 920 | 2.385 | 1993-07-26 | 16 | 2.933 | JUL 26 | 17 | 3.109 | JUL 26 | 17 | 3.487 | JUL 26 | 17 |  |  |  | 3.071 | JUL 26 | -2.385 | 3.05 | 1926-07-01 | 17 | 3.505 | JUL 26 | 17 | 3.342 | 2006-07-26 | 17 | 2.385 | 3.505
= | [11 empty] | 930 | 1.873 | 1993-07-26 | 17 | 2.546 | JUL 26 | 17 | 2.388 | JUL 26 | 18 | 3.08 | JUL 26 | 17 |  |  |  | 2.486 | JUL 26 | -1.873 | 2.4983 | 1926-07-01 | 17 |  |  |  | 2.638 | 2006-07-26 | 17 | 1.873 | 3.08 | bar: kW to KW
1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 940 | 2.888 | 1993-10-17 | 14 | 3.155 | OCT 06 | 15 | 3.458 | OCT 17 | 14 | 3.871 | OCT 17 | 14 |  |  |  | 3.334 | OCT 17 | -2.888 | 3.5667 | Oct-17 | 15 | 3.457 | OCT 17 | 15 | 3.778 | 2006-10-17 | 14 | 2.888 | 3.871
2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 950 | 2.033 | 1993-09-02 | 14 | 2.621 | SEP 02 | 15 | 2.664 | SEP 2 | 15 | 3.17 | SEP 02 | 14 |  |  |  | 2.677 | SEP 02 | -2.033 | 2.6861 | Sep-02 | 15 | 2.867 | SEP 02 | 14 | 2.917 | 2006-09-02 | 15 | 2.033 | 3.17
3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 960 | 0.953 | 1993-08-16 | 16 | 1.144 | JUL 26 | 16 | 1.057 | JUL 26 | 16 | 1.37 | JUL 26 | 16 |  |  |  | 1.179 | JUL 26 | 16 | 1.378 | 1926-07-01 | 16 | 1.403 | JUL 26 | 16 | 1.408 | 2006-07-26 | 16 | 0.953 | 1.403
4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 195 | 0.651 | 1993-07-26 | 15 | [21 empty] | 0.689 | 2006-07-27 | 15 | 0.651 | 0.651
5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 200 | 0.863 | 1993-08-16 | 14 | [24 empty] | 0.863 | 0.863
6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 210 | 0.476 | 1993-08-16 | 16 | 1.017 | JUL 26 | 15 | [12 empty] | 1.0678 | 1926-07-01 | 16 | 1.142 | JUL 26 | 15 |  |  |  | 0.476 | 1.142
7 | 1.6 |  | 1.8 | 2.9967 | 3 | 3 | 2.99 | 3 | 1.8 |  |  | 215 | 1.007 | 1993-08-11 | 14 | [24 empty] | 1.007 | 1.007
8 | 13.5 |  | 13.92 | 20.1831 | 20.24 | 20 | 20.17 | 20.15 | 14.01 |  |  | 220 | 0.56 | 1993-07-27 | 15 | 1.166 | JUL 26 | 15 | 0.937 | JUL 27 | 14 | 1.34 | JUL 26 | 15 |  |  |  | 1.215 | JUL 26 | -0.56 | 1.1789 | 1926-07-01 | 16 | 1.213 | JUL 26 | 15 | 1.032 | 2006-07-27 | 15 | 0.56 | 1.34
9 | 31 |  | 31.75 | 37.955 | 38.01 | 38 | 37.92 | 37.9 | 32.07 |  |  | 230 | 1.059 | 1993-07-27 | 15 | 1.646 | JUL 26 | 15 | 1.455 | JUL 27 | 14 | 1.875 | JUL 26 | 15 |  |  |  | 1.7 | JUL 26 | -1.059 | 1.7078 | 1926-07-01 | 16 | 1.749 | JUL 26 | 15 | 1.545 | 2006-07-27 | 15 | 1.059 | 1.875
10 | 47.1 |  | 45.24 | 53.2444 | 53.27 | 53 | 53.17 | 53.15 | 45.58 |  |  | 240 | 0.739 | 1993-07-27 | 15 | 1.347 | JUL 26 | 15 | 1.119 | JUL 27 | 14 | 1.54 | JUL 26 | 15 |  |  |  | 1.398 | JUL 26 | -0.739 | 1.3614 | 1926-07-01 | 16 | 1.397 | JUL 26 | 15 | 1.214 | 2006-07-27 | 15 | 0.739 | 1.54
11 | 59.7 |  | 56.63 | 64.4672 | 53.37 | 64 | 64.39 | 64.4 | 57.08 |  |  | 250 | 3.36 | 1993-09-05 | 12 | 3.036 | SEP 05 | 12 | 2.605 | SEP 5 | 11 | 2.59 | AUG 26 | 14 |  |  |  | 2.258 | AUG 26 | -3.36 | 3.2278 | Sep-05 | 13 | 4.912 | SEP 05 | 12 | 3.173 | 2006-08-26 | 14 | 2.258 | 4.912
12 | 67.4 |  | 61.58 | 69.9819 | 57.91 | 70 | 69.89 | 69.95 | 62 |  |  | 270 | 6.356 | 1993-11-25 | 13 | 6.641 | NOV 25 | 14 |  |  |  | 7.234 | OCT 16 | 14 | [6 empty] | 6.7639 | Oct-17 | 14 | 6.867 | OCT 16 | 14 |  |  |  | 6.356 | 7.234
13 | 70.1 |  | 63.7 | 70.8061 | 58.3 | 71 | 70.75 | 71.16 | 63.93 |  |  | 280 | 4.444 | 1993-10-17 | 13 | 4.631 | NOV 25 | 13 |  |  |  | 5.22 | OCT 16 | 14 | [6 empty] | 4.7861 | Oct-16 | 14 | 5.236 | OCT 16 | 14 |  |  |  | 4.444 | 5.236
14 | 67.3 |  | 61.46 | 65.6633 | 54.15 | 66 | 65.69 | 66.02 | 61.32 |  |  | 290 | 6.269 | 1993-01-13 | 13 | 6.555 | NOV 25 | 14 |  |  |  | 6.976 | NOV 25 | 14 | [6 empty] | 6.2028 | 1925-11-01 | 14 | 6.621 | NOV 25 | 14 |  |  |  | 6.2028 | 6.976
15 | 58.9 |  | 51.67 | 54.9214 | 45.38 | 55 | 55.03 | 55.16 | 51.08 |  |  | 300 | 3.404 | 1993-07-26 | 16 | 4.093 | JUL 26 | 17 |  |  |  | 4.657 | JUL 26 | 17 | [6 empty] | 4.2778 | 1926-07-01 | 17 | 4.929 | JUL 26 | 17 |  |  |  | 3.404 | 4.929
16 | 44.9 |  | 37.2 | 39.4869 | 32.7 | 40 | 39.61 | 39.73 | 36.25 |  |  | 310 | 2.848 | 1993-07-26 | 16 | 3.749 | JUN 30 | 17 |  |  |  | 4.164 | JUL 26 | 17 | [6 empty] | 3.5889 | 1926-07-01 | 17 | [6 empty] | 2.848 | 4.164
17 | 27.6 |  | 16.72 | 21.2906 | 17.7 | 21 | 21.42 | 21.6 | 15.95 |  |  | 320 | 5.701 | 1993-11-25 | 13 | 5.946 | NOV 25 | 14 |  |  |  | 6.553 | OCT 16 | 14 | [6 empty] | 6.1778 | Oct-17 | 14 | 6.141 | OCT 16 | 14 |  |  |  | 5.701 | 6.553
18 | 9 |  | 2.52 | 3.27 | 2.73 | 3 | 3.28 | 0 | 2.32 |  |  | 395 | 0 |  |  | 0.362 | JUL 26 | 18 | 0 |  |  | 0.394 | JUL 26 | 17 |  |  |  | 0.356 | JUL 26 | 18 | 0.3625 | 1926-07-01 | 18 | 0.345 | JUL 26 | 18 | 0.175 | 2006-07-27 | 17 | 0 | 0.394
19 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 400 | 0 |  |  | 0.581 | JUL 26 | 17 | 0.265 | JUL 27 | 17 | 0.666 | JUL 26 | 16 |  |  |  | 0.612 | JUL 26 | 17 | 0.61333 | 1926-07-01 | 17 | 0.572 | JUL 26 | 17 | 0.407 | 2006-07-27 | 16 | 0 | 0.666
20 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 410 | 0.035 | 1993-07-27 | 16 | 0.699 | JUL 26 | 17 | 0.413 | JUL 27 | 17 | 0.814 | JUL 26 | 15 |  |  |  | 0.724 | JUL 26 | -0.035 | 0.74306 | 1926-07-01 | 17 | 0.71 | JUL 26 | 17 | 0.559 | 2006-07-27 | 16 | 0.035 | 0.814
21 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 420 | 0.258 | 1993-07-27 | 15 | 0.923 | JUL 26 | 15 | 0.631 | JUL 27 | 15 | 1.047 | JUL 26 | 15 |  |  |  | 0.938 | JUL 26 | -0.258 | 0.93778 | 1926-07-01 | 16 | 0.921 | JUL 26 | 15 | 0.792 | 2006-07-27 | 15 | 0.258 | 1.047
22 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 430 | 1.493 | 1993-08-16 | 14 | 1.772 | AUG 26 | 14 | 1.427 | AUG 16 | 14 | 1.762 | JUL 26 | 15 |  |  |  | 1.575 | JUL 26 | -1.493 | 1.7983 | 1905-09-01 | 13 | 2.578 | SEP 05 | 12 | 2.113 | 2006-08-26 | 14 | 1.427 | 2.578
23 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 440 | 4.546 | 1993-10-17 | 13 | 4.424 | OCT 16 | 14 |  |  |  | 5.053 | OCT 16 | 14 | [6 empty] | 4.6861 | Oct-16 | 14 | 5.278 | OCT 17 | 14 |  |  |  | 4.424 | 5.278
24 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 800 | 0.585 | 1993-07-27 | 14 | 0.967 | AUG 16 | 14 | 0.743 | JUL 28 | 14 | 1.352 | JUL 27 | 14 |  |  |  | 1.028 | JUL 27 | -0.585 | 0.98278 | Aug-16 | 14 | 1.358 | SEP 05 | 12 | 1.267 | 2006-08-16 | 14 | 0.585 | 1.358
= | [11 empty] | 810 | 1.852 | 1993-09-02 | 14 | 2.357 | AUG 26 | 14 |  |  |  | 2.991 | SEP 02 | 14 | [6 empty] | 2.3436 | Sep-02 | 14 | 2.862 | SEP 02 | 14 |  |  |  | 1.852 | 2.991 | bar: kW to KW
HOURLY INCIDENT SOLAR RADIATION, CLEAR DAY, JULY 27
CASE 600
SOUTH SURFACE
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA
HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
= | bar: kW to KW
1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | FREE-FLOAT TEMPERATURE OUTPUT
2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | MAXIMUM ANNUAL HOURLY ZONE TEMPERATURE (C)
3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | CODENAME: |  | ESP |  |  | BLAST |  |  | DOE2 |  |  | SRES/SUN |  |  | SERIRES |  |  | S3PAS |  |  | TRNSYS |  |  | TASE |  |  | YOUR
4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | COUNTRY: |  | UK-DMU |  |  | USA/ITALY |  |  | USA |  |  | USA |  |  | UK-BRE |  |  | SPAIN |  |  | BEL/UK |  |  | FINLAND |  |  | DATA |  | SUMMARY
5 | 0.5 |  | 0 | 0.16667 | 0.14 | 0 | 0.17 | 0.2 | 0 |  |  | CASE# | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE |  | TMP (C) | DATE | HR | TMP (C) | DATE | HR | MIN | MAX
6 | 17.9 |  | 20.11 | 27.8275 | 29.94 | 28 | 27.01 | 25.7 | 21.25 |  |  | 600FF | 64.929 | 1993-10-17 | 15 | 65.11 | OCT 16 | 15 | 69.5 | OCT 17 | 15 | 68.6 | OCT 16 | 15 |  |  |  | 64.9 | OCT 16 | 16 | 65.25 | Oct-17 | 16 | 65.25 | OCT 15 | 16 | 73.4 | 2006-10-17 | 15 | 64.9 | 69.5
7 | 58.6 |  | 70.22 | 77.3025 | 89.2 | 80 | 63 | 62.1 | 73.53 |  |  | 900FF | 41.812 | 1993-10-17 | 15 | 43.44 | SEP 02 | 16 | 42.7 | SEP 02 | 15 | 44.8 | SEP 02 | 15 |  |  |  | 43 | SEP 02 | 15 | 42.46 | Oct-17 | 15 | 43.17 | SEP 15 | 15 | 45.5 | 2006-10-17 | 15 | 41.812 | 44.8
8 | 100.4 |  | 108.13 | 99.9892 | 112.85 | 104 | 71.22 | 107.47 | 110.86 |  |  | 650FF | 63.236 | 1993-10-17 | 15 | 63.45 | OCT 16 | 15 | 68.2 | OCT 17 | 15 | 67 | OCT 16 | 15 |  |  |  | 63.3 | OCT 16 | 16 | 63.74 | Oct-17 | 16 | 63.82 | OCT 16 | 16 | 71.7 | 2006-10-17 | 15 | 63.236 | 68.2
9 | 205.9 |  | 219.58 | 211.0064 | 164.86 | 217 | 187.72 | 232.33 | 212.63 |  |  | 950FF | 35.54 | 1993-09-02 | 16 | 36.23 | SEP 02 | 16 | 35.9 | SEP 02 | 16 | 38.5 | SEP 02 | 15 |  |  |  | 36.1 | SEP 02 | 16 | 35.67 | Sep-02 | 15 | 37.58 | SEP 15 | 16 | 37.1 | 2006-09-02 | 15 | 35.54 | 38.5
10 | 326 |  | 343.67 | 331.0058 | 291.84 | 336 | 314.17 | 349.16 | 334.38 |  |  | 960 | 48.943 | 1993-10-17 | 15 | 48.88 | OCT 06 | 15 | 49 | OCT 17 | 15 | 51 | OCT 17 | 15 |  |  |  | 50.2 | OCT 17 | 15 | 55.34 | Oct-17 | 15 | 48.92 | OCT 15 | 15 | 51.6 | 2006-10-17 | 15 | 48.88 | 55.34
11 | 415.1 |  | 435.54 | 418.1717 | 389.26 | 423 | 404.44 | 430.22 | 425.82 |  |  | MINIMUM ANNUAL HOURLY ZONE TEMPERATURE (C)
12 | 454.8 |  | 475.37 | 454.9942 | 437.2 | 459 | 443.61 | 459.85 | 465.2 |  |  | CODENAME: |  | ESP |  |  | BLAST |  |  | DOE2 |  |  | SRES/SUN |  |  | SERIRES |  |  | S3PAS |  |  | TRNSYS |  |  | TASE |  |  | YOUR
13 | 455.6 |  | 488.49 | 464.5689 | 455.75 | 469 | 452.5 | 462.28 | 478.4 |  |  | COUNTRY: |  | UK-DMU |  |  | USA/ITALY |  |  | USA |  |  | USA |  |  | UK-BRE |  |  | SPAIN |  |  | BEL/UK |  |  | FINLAND |  |  | DATA |  | SUMMARY
14 | 408.6 |  | 443.66 | 413.6364 | 413.67 | 418 | 400.56 | 404.57 | 433.75 |  |  | CASE# | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE | HR | TMP (C) | DATE |  | TMP (C) | DATE | HR | TMP (C) | DATE | HR | MIN | MAX
15 | 321.2 |  | 367.07 | 334.2839 | 341.53 | 340 | 316.94 | 319.26 | 357.6 |  |  | 600FF | -15.565 | 1993-01-04 | 7 | -17.05 | JAN 04 | 8 | -18.8 | JAN 04 | 8 | -18 | JAN 04 | 7 |  |  |  | -17.8 | JAN 04 | 8 | -17.81 | Jan-04 | 7 | -18.47 | JAN 08 | 9 | -17.7 | 2006-01-04 | 8 | -18.8 | -15.565
16 | 200.6 |  | 246.71 | 211.9439 | 223.71 | 218 | 188.89 | 193.61 | 238.77 |  |  | 900FF | -1.647 | 1993-01-04 | 8 | -3.15 | JAN 04 | 8 | -4.3 | JAN 04 | 8 | -4.5 | JAN 04 | 8 |  |  |  | -4 | JAN 04 | 8 | -6.38 | Jan-04 | 8 | -5.64 | JAN 08 | 9 | -2 | 2006-01-04 | 8 | -6.38 | -1.647
17 | 102.3 |  | 119.19 | 111.7408 | 105.72 | 115 | 86.03 | 132.3 | 121.87 |  |  | 650FF | -22.564 | 1993-01-04 | 6 | -22.96 | JAN 04 | 7 | -21.6 | JAN 04 | 2 | -23 | JAN 04 | 2 |  |  |  | -22.9 | JAN 04 | 2 | -22.83 | Jan-04 | 7 | -22.91 | JAN 02 | 23 | -21 | 2006-01-04 | 2 | -23 | -21.6
18 | 78.8 |  | 68.86 | 73.0792 | 68.47 | 74 | 69.78 | 76.6 | 71.71 |  |  | 950FF | -19.484 | 1993-01-04 | 6 | -20.04 | JAN 04 | 7 | -18.6 | JAN 04 | 7 | -19.7 | JAN 04 | 7 |  |  |  | -20.2 | JAN 04 | 7 | -19.34 | Jan-04 | 7 | -19.96 | JAN 07 | 22 | -17.8 | 2006-01-04 | 7 | -20.2 | -18.6
19 | 37.1 |  | 19.75 | 17.7025 | 14.35 | 18 | 17.61 | 18.05 | 20.51 |  |  | 960 | 2.729 | 1993-02-06 | 6 | 1.63 | FEB 06 | 7 | 3.9 | FEB 06 | 7 | 3.1 | FEB 06 | 7 |  |  |  | 1.4 | FEB 06 | 6 | -2.82 | Jan-04 | 8 | -0.39 | FEB 05 | 7 | 6 | 2006-02-06 | 7 | -2.82 | 3.9
20 | 1.1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | AVERAGE ANNUAL HOURLY ZONE TEMPERATURE (C)
21 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | CODENAME: |  | ESP |  |  | BLAST |  |  | DOE2 |  |  | SRES/SUN |  |  | SERIRES |  |  | S3PAS |  |  | TRNSYS |  |  | TASE |  |  | YOUR
22 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | COUNTRY: |  | UK-DMU |  |  | USA/ITALY |  |  | USA |  |  | USA |  |  | UK-BRE |  |  | SPAIN |  |  | BEL/UK |  |  | FINLAND |  |  | DATA |  | SUMMARY
23 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | CASE# | TMP (C) |  |  | TMP (C) |  |  | TMP (C) |  |  | TMP (C) |  |  | TMP (C) |  |  | TMP (C) |  |  | TMP (C) |  |  | TMP (C) |  |  | TMP (C) | DATE | HR | MIN | MAX
24 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 600FF | 25.126 |  |  | 25.43 |  |  | 24.6 |  |  | 25.48 |  |  | 25.93 |  |  | 25.2 |  |  | 24.49 |  |  | 24.22 |  |  | 26.993 |  |  | 24.22 | 25.93
= | [11 empty] | 900FF | 25.453 |  |  | 25.93 |  |  | 24.7 |  |  | 25.49 |  |  | 25.72 |  |  | 25.2 |  |  | 24.47 |  |  | 24.45 |  |  | 27.0563 |  |  | 24.45 | 25.93 | bar: kW to KW
[12 empty] | 650FF | 18.234 |  |  | 18.69 |  |  | 19.1 |  |  | 18.96 |  |  | 19.62 |  |  | 18.4 |  |  | 17.99 |  |  | 18.36 |  |  | 20.4281 |  |  | 17.99 | 19.62
[12 empty] | 950FF | 14.14 |  |  | 14.26 |  |  | 14.3 |  |  | 14.97 |  |  | 14.29 |  |  | 14 |  |  | 14.53 |  |  | 14.64 |  |  | 15.0742 |  |  | 14 | 14.97
[12 empty] | 960 | 27.49 |  |  | 27.72 |  |  | 28 |  |  | 28.69 |  |  | 28.54 |  |  | 28 |  |  | 28.96 |  |  | 26.43 |  |  | 30.0216 |  |  | 26.43 | 28.96
HOURLY INCIDENT SOLAR RADIATION, CLEAR DAY, JULY 27
CASE 600
WEST SURFACE
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA
HOUR | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2 | Wh/m2
= | bar: kW to KW
1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0.4 |  | 0 | 0.16667 | 0.14 | 0 | 0.17 | 0.2 | 0
6 | 17.9 |  | 19.96 | 27.8275 | 29.94 | 28 | 27.01 | 25.7 | 21.16
7 | 58.5 |  | 65.86 | 77.3025 | 89.2 | 80 | 63 | 62.1 | 69.31
8 | 91.8 |  | 97.11 | 99.9892 | 112.85 | 104 | 71.22 | 72 | 100.74
9 | 113.7 |  | 116.89 | 120.0506 | 121.41 | 125 | 85.58 | 92.6 | 119.05
10 | 131.2 |  | 128.97 | 134.9631 | 123.51 | 140 | 98.03 | 112.8 | 130.25
11 | 145.7 |  | 138.05 | 149.5847 | 125.06 | 154 | 109.14 | 136.75 | 139.62
12 | 153.8 |  | 141.34 | 153.1336 | 121.07 | 157 | 113.06 | 150.9 | 142.54
13 | 267.7 |  | 243.51 | 266.4489 | 117.94 | 270 | 235.17 | 382.5 | 244.31
14 | 464.8 |  | 462.83 | 461.2772 | 333.68 | 463 | 453.89 | 576.81 | 461.98
15 | 635.1 |  | 664.62 | 635.5103 | 525.35 | 635 | 652.5 | 744.52 | 662.1
16 | 738.3 |  | 786.35 | 719.3256 | 634.59 | 715 | 762.78 | 807.29 | 782.66
17 | 623.9 |  | 649.05 | 502.7889 | 478.44 | 497 | 568.33 | 541.68 | 651.77
18 | 296.9 |  | 243.11 | 141.2425 | 140.3 | 139 | 158 | 145.25 | 231.93
19 | 68.8 |  | 43.19 | 25.2472 | 21.96 | 24 | 26.6 | 24.9 | 38.33
20 | 1.6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
= | bar: kW to KW
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 600FF JAN 4
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA
HOUR | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C)
= | bar: kW to KW
1 | -8.88 | -12.0409 | -12.3 | -12.21 |  | -12.1 | -12.02 | -13.04 | -10.4
2 | -10.48 | -13.523 | -14.1 | -13.8 |  | -13.7 | -13.5 | -14.59 | -12.4
3 | -11.76 | -14.4018 | -15.4 | -14.9 |  | -14.7 | -14.7 | -15.65 | -13.8
4 | -12.75 | -15.2598 | -16.3 | -15.79 |  | -15.6 | -15.65 | -16.46 | -14.9
5 | -13.69 | -15.9988 | -17.1 | -16.55 |  | -16.4 | -16.47 | -17.16 | -15.8
6 | -14.49 | -16.3983 | -17.9 | -17.2 |  | -17 | -17.14 | -17.79 | -16.7
7 | -15.15 | -17.0108 | -18.5 | -17.74 |  | -17.6 | -17.7 | -18.32 | -17.4
8 | -15.63 | -17.0531 | -18.8 | -17.85 |  | -17.8 | -17.59 | -18.47 | -17.7
9 | -14.63 | -13.7364 | -14.7 | -14.88 |  | -14.6 | -13.46 | -15.47 | -13.3
10 | -10.03 | -7.9937 | -7.8 | -9.07 |  | -8.9 | -7.099 | -9.56 | -5.7
11 | -2.2 | 2.6043 | 3.2 | 1.01 |  | 1 | 3.657 | 0.49 | 6.1
12 | 8.84 | 12.2151 | 13.4 | 11.21 |  | 10.7 | 13.49 | 10.39 | 17.2
13 | 18.96 | 20.8602 | 22.3 | 20.03 |  | 19.2 | 21.77 | 18.75 | 26.8
14 | 27.19 | 27.532 | 29.5 | 27.27 |  | 26.1 | 28.26 | 25.48 | 34.6
15 | 33.22 | 31.3289 | 33.8 | 31.34 |  | 29.8 | 32.09 | 29.21 | 39.4
16 | 35.51 | 31.0594 | 33.5 | 31.47 |  | 29.7 | 32.16 | 28.97 | 39.4
17 | 31.46 | 24.2801 | 27 | 25.96 |  | 23.9 | 25.71 | 22.58 | 32.5
18 | 23.99 | 17.4634 | 19.7 | 18.96 |  | 17.6 | 18.84 | 15.59 | 24.8
19 | 18.08 | 12.0529 | 13.7 | 13.04 |  | 12.2 | 13.1 | 10.2 | 18.4
20 | 13.02 | 7.5727 | 8.7 | 8.31 |  | 7.8 | 8.408 | 6.02 | 13
21 | 8.87 | 3.5981 | 4.4 | 4.27 |  | 4 | 4.387 | 2.39 | 8.3
22 | 5.12 | 0.51861 | 1 | 0.99 |  | 0.9 | 0.9659 | -0.59 | 4.5
23 | 2.03 | -1.9381 | -1.9 | -1.66 |  | -1.7 | -1.781 | -3.04 | 1.2
24 | -1.03 | -4.0741 | -4.4 | -3.92 |  | -3.9 | -4.032 | -5.14 | -1.5
= | bar: kW to KW
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 900FF JAN 4
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA
HOUR | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C)
= | bar: kW to KW
1 | 1.61 | -0.17002 | -0.9 | -1.31 |  | -0.7 | -3.455 | -2.68 | 1.5
2 | 0.93 | -0.79333 | -1.6 | -1.97 |  | -1.4 | -3.986 | -3.33 | 0.8
3 | 0.49 | -1.0908 | -2 | -2.37 |  | -1.8 | -4.395 | -3.72 | 0.3
4 | 0.07 | -1.6745 | -2.5 | -2.81 |  | -2.3 | -4.8 | -4.1 | -0.1
5 | -0.41 | -2.0414 | -2.9 | -3.25 |  | -2.7 | -5.216 | -4.51 | -0.6
6 | -0.87 | -2.4328 | -3.4 | -3.68 |  | -3.2 | -5.604 | -4.93 | -1.1
7 | -1.27 | -2.9702 | -3.9 | -4.1 |  | -3.6 | -5.984 | -5.34 | -1.6
8 | -1.64 | -3.1541 | -4.3 | -4.4 |  | -4 | -6.078 | -5.64 | -2
9 | -1.54 | -2.3938 | -3.3 | -3.45 |  | -3.2 | -4.717 | -4.59 | -0.9
10 | -0.4 | -1.0924 | -1.6 | -1.6 |  | -1.7 | -2.977 | -2.64 | 0.9
11 | 1.59 | 1.5953 | 1.2 | 1.66 |  | 0.9 | 0.2494 | 0.75 | 3.9
12 | 4.4 | 3.6249 | 3.5 | 4.4 |  | 3.1 | 2.539 | 3.26 | 6.3
13 | 6.72 | 5.6203 | 5.5 | 6.56 |  | 5.1 | 4.382 | 4.99 | 8.5
14 | 8.66 | 7.3237 | 7.2 | 8.39 |  | 6.8 | 5.853 | 6.51 | 10.3
15 | 10.02 | 8.2691 | 8 | 9.04 |  | 7.6 | 6.614 | 7.11 | 11.2
16 | 10.4 | 8.1513 | 7.9 | 8.58 |  | 7.4 | 6.333 | 6.68 | 11
17 | 9.41 | 6.5309 | 6.2 | 6.44 |  | 5.8 | 4.204 | 4.24 | 9.2
18 | 7.66 | 5.2506 | 4.7 | 4.43 |  | 4.4 | 2.869 | 2.45 | 7.7
19 | 6.74 | 4.5191 | 3.8 | 3.37 |  | 3.6 | 2.107 | 1.71 | 6.8
20 | 6 | 3.8832 | 3.2 | 2.73 |  | 3 | 1.581 | 1.32 | 6.1
21 | 5.41 | 3.2206 | 2.7 | 2.11 |  | 2.4 | 1.047 | 0.82 | 5.5
22 | 4.74 | 2.8485 | 2.2 | 1.66 |  | 1.9 | 0.5504 | 0.42 | 5
23 | 4.2 | 2.4745 | 1.7 | 1.26 |  | 1.5 | 0.1517 | 0.05 | 4.5
24 | 3.66 | 1.8994 | 1.2 | 0.83 |  | 1 | -0.238 | -0.34 | 4
= | bar: kW to KW
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 650FF JULY 27
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA
HOUR | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C)
= | bar: kW to KW
1 | 22.58 | 22.223 | 21.8 | 22.37 |  | 22.4 | 22.69 | 22.26 | 22
2 | 21.15 | 21.1546 | 20.8 | 21.19 |  | 21.2 | 21.33 | 21.11 | 21
3 | 20.23 | 20.3068 | 19.9 | 20.33 |  | 20.4 | 20.41 | 20.28 | 20.1
4 | 19.45 | 19.5218 | 19.1 | 19.54 |  | 19.5 | 19.61 | 19.49 | 19.3
5 | 18.95 | 19.295 | 18.8 | 19.21 |  | 19.2 | 19.16 | 19.14 | 19
6 | 19.24 | 19.9144 | 19.5 | 19.86 |  | 19.9 | 19.6 | 19.81 | 19.7
7 | 21.16 | 22.5284 | 22.2 | 22.51 |  | 22.5 | 21.68 | 22.49 | 22.4
8 | 23.56 | 25.0275 | 24 | 24.89 |  | 24.7 | 23.47 | 24.81 | 24.8
9 | 25.67 | 28.3327 | 27.3 | 28.29 |  | 27.9 | 26.38 | 28.04 | 28.5
10 | 28.91 | 31.8311 | 31.5 | 32.42 |  | 31.7 | 30.35 | 32.11 | 32.8
11 | 32.8 | 35.825 | 36.2 | 37.12 |  | 36.2 | 34.82 | 36.54 | 37.6
12 | 37.49 | 40.1973 | 41.1 | 42.08 |  | 40.8 | 39.38 | 41.15 | 42.6
13 | 41.94 | 43.9026 | 45.4 | 46.46 |  | 45 | 43.48 | 45.03 | 46.8
14 | 45.43 | 46.3464 | 48.4 | 49.69 |  | 48.1 | 46.14 | 47.65 | 49.8
15 | 47.41 | 47.6362 | 50.1 | 51.3 |  | 49.6 | 47.4 | 49.04 | 51.6
16 | 47.84 | 47.6029 | 50.1 | 51.28 |  | 49.7 | 47.33 | 49.28 | 51.9
17 | 47.01 | 47.3406 | 49.1 | 50.46 |  | 49.1 | 46.71 | 48.73 | 51.1
18 | 45.53 | 45.3964 | 46.8 | 48.37 |  | 47.2 | 45.28 | 46.58 | 48.8
19 | 37.37 | 33.7034 | 34 | 35.39 |  | 35.1 | 33.1 | 34.91 | 34.7
20 | 31.57 | 30.8664 | 30.9 | 31.63 |  | 31.6 | 30.49 | 30.69 | 31.4
21 | 29.05 | 28.695 | 28.5 | 29.12 |  | 29.2 | 28.55 | 28.81 | 28.9
22 | 26.92 | 26.4968 | 26.3 | 26.83 |  | 26.9 | 26.66 | 26.66 | 26.6
23 | 25.52 | 25.6844 | 25.4 | 25.87 |  | 25.9 | 25.55 | 25.69 | 25.6
24 | 23.84 | 24.0543 | 23.7 | 24.19 |  | 24.2 | 24.26 | 24.1 | 23.9
= | bar: kW to KW
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 950FF JULY 27
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA
HOUR | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C) | TEMP (C)
= | bar: kW to KW
1 | 24.36 | 24.5601 | 24.2 | 24.52 |  | 24.6 | 25.28 | 24.53 | 24.6
2 | 23.46 | 23.8963 | 23.5 | 23.81 |  | 23.9 | 24.47 | 23.8 | 23.9
3 | 22.86 | 23.3126 | 22.9 | 23.22 |  | 23.3 | 23.87 | 23.23 | 23.3
4 | 22.27 | 22.6823 | 22.3 | 22.6 |  | 22.7 | 23.26 | 22.6 | 22.7
5 | 21.86 | 22.4527 | 22 | 22.32 |  | 22.4 | 22.87 | 22.27 | 22.4
6 | 22.01 | 22.8128 | 22.5 | 22.77 |  | 22.8 | 23.06 | 22.67 | 22.8
7 | 23.32 | 24.6678 | 24.3 | 24.73 |  | 24.6 | 24.38 | 24.55 | 24.6
8 | 25.62 | 27.3586 | 26.5 | 27.59 |  | 27.1 | 27.21 | 27.57 | 27.2
9 | 27.59 | 28.3229 | 27.5 | 29.09 |  | 28.2 | 27.98 | 29.42 | 28.3
10 | 28.82 | 29.2074 | 28.6 | 30.5 |  | 29.3 | 29.11 | 30.68 | 29.4
11 | 29.84 | 30.1901 | 29.8 | 31.98 |  | 30.5 | 30.31 | 31.91 | 30.7
12 | 30.98 | 31.3352 | 31.1 | 33.56 |  | 31.7 | 31.53 | 33.27 | 32
13 | 32.08 | 32.1879 | 32.2 | 34.79 |  | 32.8 | 32.55 | 34.27 | 33.1
14 | 32.85 | 32.845 | 33 | 35.65 |  | 33.6 | 33.15 | 34.9 | 33.9
15 | 33.33 | 33.1198 | 33.4 | 35.96 |  | 34 | 33.37 | 35.19 | 34.3
16 | 33.55 | 33.2478 | 33.5 | 35.82 |  | 34.1 | 33.38 | 35.28 | 34.5
17 | 33.44 | 33.3523 | 33.5 | 35.61 |  | 34.1 | 33.37 | 35.3 | 34.5
18 | 33.23 | 32.996 | 33.1 | 34.93 |  | 33.7 | 33.16 | 34.71 | 34
19 | 30.92 | 30.203 | 30 | 30.96 |  | 30.6 | 30.43 | 30.74 | 30.4
20 | 29.17 | 29.3534 | 29.1 | 29.79 |  | 29.6 | 29.61 | 29.38 | 29.5
21 | 28.31 | 28.5416 | 28.2 | 28.83 |  | 28.7 | 28.89 | 27.64 | 28.6
22 | 27.27 | 27.3759 | 27.1 | 27.59 |  | 27.5 | 27.93 | 27.46 | 27.5
23 | 26.62 | 27.174 | 26.8 | 27.28 |  | 27.3 | 27.42 | 27.1 | 27.2
24 | 25.54 | 25.9805 | 25.7 | 26.1 |  | 26.1 | 26.59 | 26.02 | 26
= | bar: kW to KW
HOURLY HEATING & COOLING LOAD DATA
CASE 600 JAN 4
[USE (-) FOR COOLING]
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA
HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | bar: kW to KW
1 | 3.25 | 3.8018 | 3.926 | 4.127 |  | 3.925 | 3.7667 | 4.225 | 3.645
2 | 3.409 | 3.9109 | 4.035 | 4.258 |  | 4.037 | 3.8667 | 4.354 | 3.75
3 | 3.392 | 3.8658 | 4.013 | 4.229 |  | 4.003 | 3.9028 | 4.321 | 3.74
4 | 3.381 | 3.9196 | 4.041 | 4.22 |  | 4.001 | 3.8944 | 4.308 | 3.765
5 | 3.417 | 3.9401 | 4.045 | 4.22 |  | 4.001 | 3.9167 | 4.303 | 3.767
6 | 3.432 | 3.9258 | 4.036 | 4.221 |  | 4.001 | 3.9306 | 4.307 | 3.758
7 | 3.421 | 3.937 | 4.045 | 4.222 |  | 4.001 | 3.9306 | 4.307 | 3.764
8 | 3.337 | 3.7023 | 3.857 | 4.09 |  | 3.898 | 3.7528 | 4.167 | 3.558
9 | 2.767 | 2.6752 | 2.559 | 2.902 |  | 2.706 | 2.4228 | 2.912 | 2.157
10 | 1.497 | 1.3833 | 0.843 | 1.275 |  | 1.151 | 0.79667 | 1.466 | 0.335
11 | 0.151 | 0 | 0 | 0 |  | 0 | -0.034833 | 0 | -0.194
12 | -0.771 | -1.2242 | -1.552 | -1.066 |  | -1.036 | -1.435 | -0.424 | -2.459
13 | -2.66 | -2.4871 | -2.854 | -2.586 |  | -2.498 | -2.7203 | -2.364 | -3.689
14 | -3.575 | -2.9579 | -3.398 | -3.225 |  | -3.085 | -3.1556 | -2.759 | -4.172
15 | -3.527 | -2.631 | -3.116 | -2.826 |  | -2.637 | -2.8444 | -2.431 | -3.874
16 | -2.435 | -1.3491 | -1.82 | -1.552 |  | -1.345 | -1.7158 | -1.14 | -2.522
17 | -0.356 | 0 | 0 | -0.001 |  | 0 | 0 | 0 | 0
18 | 0.243 | 0.95017 | 0.775 | 0.8 |  | 0.88 | 0.77306 | 1.292 | 0.203
19 | 1.53 | 2.3779 | 2.232 | 2.34 |  | 2.331 | 2.3014 | 2.445 | 1.823
20 | 2.321 | 2.8665 | 2.933 | 2.988 |  | 2.949 | 2.9667 | 2.941 | 2.603
21 | 2.641 | 3.2126 | 3.323 | 3.365 |  | 3.309 | 3.2778 | 3.405 | 3.029
22 | 2.899 | 3.2845 | 3.487 | 3.532 |  | 3.347 | 3.4611 | 3.594 | 3.214
23 | 3.017 | 3.3307 | 3.514 | 3.605 |  | 3.494 | 3.5 | 3.696 | 3.256
24 | 3.008 | 3.388 | 3.561 | 3.663 |  | 3.527 | 3.4722 | 3.769 | 3.304
= | bar: kW to KW
HOURLY HEATING & COOLING LOAD DATA
CASE 900 JAN 4
[USE (-) FOR COOLING]
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA
HOUR | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh
= | bar: kW to KW
1 | 2.441 | 3.1039 | 3.101 | 3.394 |  | 3.208 | 3.0806 | 3.4 | 2.774
2 | 2.606 | 3.1986 | 3.237 | 3.54 |  | 3.349 | 3.2028 | 3.547 | 2.912
3 | 2.623 | 3.2044 | 3.279 | 3.557 |  | 3.382 | 3.2778 | 3.573 | 2.968
4 | 2.667 | 3.3056 | 3.377 | 3.613 |  | 3.447 | 3.3306 | 3.629 | 3.064
5 | 2.744 | 3.3669 | 3.446 | 3.666 |  | 3.506 | 3.4167 | 3.687 | 3.132
6 | 2.8 | 3.3993 | 3.498 | 3.715 |  | 3.558 | 3.4694 | 3.747 | 3.187
7 | 2.834 | 3.4532 | 3.557 | 3.76 |  | 3.605 | 3.5167 | 3.797 | 3.248
8 | 2.837 | 3.376 | 3.516 | 3.749 |  | 3.608 | 3.4639 | 3.794 | 3.21
9 | 2.641 | 2.8981 | 2.974 | 3.17 |  | 3.08 | 2.8333 | 3.168 | 2.636
10 | 2.12 | 2.3463 | 2.202 | 2.32 |  | 2.348 | 2.0561 | 2.449 | 1.828
11 | 1.502 | 1.3981 | 1.034 | 0.949 |  | 1.117 | 0.79333 | 1.293 | 0.588
12 | 0.676 | 0.37698 | 0.232 | 0.101 |  | 0.3 | 0.037278 | 0.619 | 0
13 | 0.074 | 0 | 0 | 0 |  | 0 | 0 | 0.136 | 0
14 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
15 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
16 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0.088 | 0
17 | 0.027 | 0.12409 | 0 | 0.277 |  | 0.143 | 0.13494 | 1.198 | 0
18 | 0.413 | 0.76691 | 0.739 | 1.216 |  | 0.91 | 0.76444 | 1.602 | 0.036
19 | 0.804 | 1.3064 | 1.14 | 1.608 |  | 1.281 | 1.1986 | 1.805 | 0.52
20 | 1.068 | 1.613 | 1.429 | 1.816 |  | 1.543 | 1.4589 | 1.943 | 0.858
21 | 1.269 | 1.9255 | 1.7 | 2.038 |  | 1.81 | 1.7008 | 2.121 | 1.158
22 | 1.502 | 2.1361 | 1.894 | 2.174 |  | 1.995 | 1.9342 | 2.227 | 1.38
23 | 1.658 | 2.2208 | 2.028 | 2.293 |  | 2.154 | 2.0922 | 2.338 | 1.547
24 | 1.749 | 2.3111 | 2.193 | 2.423 |  | 2.311 | 2.2267 | 2.458 | 1.735
= | bar: kW to KW
FREE-FLOAT CASES
HOURLY ANNUAL ZONE TEMPERATURE BIN DATA
CASE 900FF
CODENAME: | ESP | BLAST | DOE2.1D | SRES/SUN | SERIRES | S3PAS | TRNSYS | TASE | YOUR
COUNTRY: | UK-DMU | USA/IT | USA | USA | UK-BRE | SPAIN | BEL/UK | FINLAND | DATA
TEMP (C) | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS | # HOURS
= | bar: kW to KW
-50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
-6 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 | 0
-5 | 0 | 0 | 1 | 2 | 0 | 0 | 3 | 4 | 0
-4 | 0 | 1 | 3 | 3 | 4 | 4 | 6 | 5 | 0
-3 | 0 | 3 | 7 | 5 | 2 | 3 | 6 | 7 | 0
-2 | 3 | 5 | 5 | 7 | 7 | 8 | 12 | 10 | 3
-1 | 3 | 6 | 10 | 7 | 5 | 5 | 13 | 18 | 7
0 | 8 | 10 | 18 | 19 | 18 | 18 | 12 | 20 | 6
1 | 6 | 17 | 17 | 19 | 10 | 20 | 12 | 12 | 8
2 | 18 | 14 | 18 | 13 | 20 | 14 | 20 | 16 | 15
3 | 18 | 19 | 19 | 15 | 15 | 19 | 18 | 25 | 16
4 | 17 | 14 | 20 | 23 | 20 | 21 | 20 | 24 | 19
5 | 18 | 25 | 30 | 28 | 24 | 27 | 26 | 27 | 17
6 | 22 | 19 | 25 | 29 | 27 | 30 | 34 | 35 | 19
7 | 31 | 33 | 37 | 28 | 28 | 33 | 29 | 45 | 29
8 | 30 | 34 | 51 | 46 | 33 | 46 | 44 | 59 | 26
9 | 42 | 42 | 59 | 62 | 57 | 61 | 55 | 73 | 29
10 | 51 | 54 | 84 | 69 | 53 | 71 | 57 | 118 | 50
11 | 67 | 72 | 107 | 111 | 89 | 116 | 95 | 134 | 57
12 | 90 | 115 | 139 | 137 | 112 | 127 | 127 | 138 | 75
13 | 115 | 137 | 153 | 141 | 142 | 157 | 143 | 173 | 95
14 | 156 | 159 | 158 | 154 | 151 | 160 | 162 | 183 | 120
15 | 172 | 165 | 206 | 188 | 178 | 207 | 183 | 234 | 140
16 | 215 | 198 | 239 | 232 | 195 | 224 | 234 | 274 | 154
17 | 244 | 245 | 274 | 253 | 248 | 255 | 273 | 298 | 188
18 | 293 | 277 | 350 | 301 | 266 | 315 | 296 | 342 | 226
19 | 338 | 317 | 322 | 336 | 332 | 347 | 356 | 352 | 252
20 | 387 | 365 | 375 | 342 | 344 | 352 | 346 | 331 | 324
21 | 398 | 358 | 392 | 362 | 361 | 366 | 388 | 334 | 336
22 | 385 | 372 | 364 | 329 | 376 | 349 | 380 | 343 | 335
23 | 396 | 341 | 370 | 348 | 366 | 357 | 366 | 349 | 375
24 | 380 | 368 | 381 | 352 | 341 | 341 | 401 | 338 | 414
25 | 417 | 357 | 432 | 361 | 397 | 392 | 404 | 404 | 362
26 | 455 | 389 | 431 | 373 | 426 | 399 | 436 | 393 | 402
27 | 459 | 420 | 415 | 415 | 418 | 403 | 465 | 396 | 400
28 | 445 | 463 | 452 | 390 | 446 | 440 | 412 | 411 | 430
29 | 459 | 419 | 410 | 405 | 432 | 396 | 408 | 391 | 441
30 | 415 | 396 | 404 | 418 | 422 | 395 | 398 | 362 | 427
31 | 406 | 393 | 342 | 401 | 389 | 360 | 335 | 342 | 448
32 | 369 | 348 | 349 | 341 | 334 | 337 | 348 | 322 | 404
33 | 339 | 315 | 309 | 330 | 338 | 306 | 310 | 291 | 370
34 | 277 | 321 | 242 | 285 | 311 | 306 | 297 | 266 | 342
35 | 230 | 303 | 197 | 246 | 262 | 256 | 202 | 210 | 318
36 | 191 | 254 | 185 | 213 | 203 | 217 | 197 | 169 | 275
37 | 164 | 195 | 136 | 156 | 189 | 166 | 161 | 151 | 189
38 | 108 | 175 | 92 | 146 | 137 | 138 | 97 | 132 | 189
39 | 71 | 99 | 74 | 112 | 103 | 97 | 86 | 85 | 154
40 | 37 | 66 | 35 | 90 | 71 | 57 | 48 | 59 | 109
41 | 15 | 32 | 16 | 58 | 35 | 31 | 22 | 32 | 80
42 | 0 | 25 | 5 | 36 | 18 | 10 | 11 | 20 | 47
43 | 0 | 5 | 0 | 18 | 5 | 1 | 2 | 1 | 23
44 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 13
45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2
46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
= | = | = | = | = | ======== | = | = | = | =
= | = | = | = | = | ======== | = | = | = | =
= | bar: kW to KW
= | bar: kW to KW