## Slide 1: Approval Request for EnergyGauge USA
June 11, 2015

## Slide 2: Overview
Presents key findings
  Methods handled by software
  Compliance results
Test report is in two volumes
  1st volume has overall descriptions and performance method results
  2nd volume has prescriptive method results
Other files required by the FBC Technical Assistance Manual were provided
  Input files
  Spreadsheet results

## Slide 3: Methods of Code Compliance
Cover sheet for request for approval by the Florida Building Commission as a Compliance Software tool
EnergyGauge USA
  Version Number: 4.0
This software calculate Residential Energy Efficiency Code Compliance:
   Prescriptive R-value Method
   Prescriptive Total UA Alternative Method
   Performance Method
  Prescriptive U-factor Alternative Method not part of EnergyGaugeUSA

## Slide 4: Performance Method Testing
The performance tests consist of:
  FL e-Ratio algorithms
  Two suites of building load tests, referred to as ASHRAE Standard 140 and Florida HERS BESTEST developed by the National Renewable Energy Laboratory
  A Standard Reference Design Auto-generation test suite developed by the State of Florida
  Three test suites developed by RESNET to test
    Heating, Ventilating and Air Conditioning (HVAC) equipment algorithms,
    Distribution System Efficiency (DSE) algorithms,
    Domestic Hot Water (DHW) algorithms.

## Slide 5: Performance Method Testing (cont’d)
Each of the performance Method Tests was passed.
Directions for anyone wanting to test the software for themselves are included in the report.
Submission includes a series of subdirectories, which include all of the specific information for the given series of verification tests, as follows:
  Input – contains the EnergyGauge input files for each test
  Output – contains PDF copies of the output files generated by EnergyGauge for each test
  Procedures – contains the written procedures for each test suite
  Results –completed spreadsheets provided by the Florida Building Commission for reporting results.

## Slide 6: ASHRAE 140 Test Heating
Annual Heating Loads: Colorado Springs, CO |  |  |  |  | 
 | Heating | range max | range min | Result | pass/fail
 | L100AC | 79.48 | 48.75 | 55.79 | pass
 | L110AC | 103.99 | 71.88 | 77.14 | pass
 | L120AC | 64.30 | 37.82 | 42.57 | pass
 | L130AC | 53.98 | 41.82 | 45.65 | pass
 | L140AC | 56.48 | 43.24 | 48.41 | pass
 | L150AC | 71.33 | 40.95 | 49.38 | pass
 | L155AC | 74.18 | 43.53 | 51.63 | pass
 | L160AC | 81.00 | 48.78 | 57.62 | pass
 | L170AC | 92.40 | 61.03 | 69.31 | pass
 | L200AC | 185.87 | 106.41 | 131.51 | pass
 | L202AC | 190.05 | 111.32 | 139.95 | pass
 | L302XC | 90.52 | 52.66 | 55.62 | pass
 | L304XC | 75.32 | 43.91 | 47.15 | pass
 | L322XC | 118.20 | 68.35 | 73.93 | pass
 | L324XC | 80.04 | 44.01 | 48.97 | pass
Chart: Annual Heating Loads: Colorado Springs, CO
| L100AC | L110AC | L120AC | L130AC | L140AC | L150AC | L155AC | L160AC
Min | 48.7472 | 71.8838 | 37.8248 | 41.822 | 43.243 | 40.9537 | 43.5293 | 48.7751
Max | 79.4781 | 103.9929 | 64.2979 | 53.979 | 56.481 | 71.3277 | 74.1847 | 80.9969
 | 64.1127 | 87.9383 | 51.0613 | 47.9005 | 49.862 | 56.1407 | 58.857 | 64.886
EnergyGauge USA v4.0 | 55.79 | 77.14 | 42.57 | 45.65 | 48.41 | 49.38 | 51.63 | 57.62

## Slide 7: ASHRAE 140 Test Cooling
Annual Cooling Loads: Las Vegas, NV |  |  |  |  | 
 | Cooling | range max | range min | Result | pass/fail
 | L100AL | 64.88 | 50.66 | 54.71 | pass
 | L110AL | 68.50 | 53.70 | 56.82 | pass
 | L120AL | 60.14 | 47.34 | 49.07 | pass
 | L130AL | 45.26 | 32.95 | 38.63 | pass
 | L140AL | 30.54 | 19.52 | 25.62 | pass
 | L150AL | 82.33 | 62.41 | 70.78 | pass
 | L155AL | 63.06 | 50.08 | 56.55 | pass
 | L160AL | 72.99 | 58.61 | 64.42 | pass
 | L170AL | 53.31 | 41.83 | 43.29 | pass
 | L200AL | 83.43 | 60.25 | 67.10 | pass
 | L202AL | 75.96 | 52.32 | 54.98 | pass

## Slide 8: Florida BESTEST Heating Results
Chart: Annual Heating Loads: Orlando, FL
| L100AO | L110AO | L120AO | L130AO | L140AO | L150AO | L155AO | L160AO
Min | 1.54 | 5.54 | -0.44 | -0.48 | -0.05 | 0.37 | 0.78 | 1.74
Max | 10.56 | 14.71 | 8.57 | 7.86 | 8.34 | 9.55 | 9.95 | 10.71
 | 6.05 | 10.125 | 4.065 | 3.69 | 4.145 | 4.96 | 5.365 | 6.225
EnergyGauge USA v.4.0 | 5.33 | 8.6 | 3.99 | 3.99 | 3.55 | 5.52 | 5.59 | 5.64

## Slide 9: Florida BESTEST Cooling Results
Chart: Annual Cooling Loads: Orlando, FL
| L100AO | L110AO | L120AO | L130AO | L140AO | L150AO
Min | 39.34 | 39.61 | 38.11 | 25.1 | 12.55 | 46.5362
Max | 55.152 | 55.6456 | 51.57 | 38.46 | 24.75 | 65.6172
 | 47.246 | 47.6278 | 44.84 | 31.78 | 18.65 | 56.0767
EnergyGauge USA v.4.0 | 46.42 | 46.69 | 42.79 | 32.42 | 19.87 | 56.66

## Slide 10: DHW Test
Chart: 
| MN,0.56,4 (delta) | MN,0.62,2 (delta) | FL,0.56,4 (delta) | FL,0.62,2 (delta) | % [(MN-FL)/(MN)]
Min | 0.26476 | -0.11809 | 0.19065 | -0.19453 | 0.28875
Max | 0.32172 | -0.068305 | 0.29084 | -0.077101 | 0.45064
 | 0.29324 | -0.093197 | 0.24074 | -0.13582 | 0.3697
EnergyGauge v.4.0 | 0.28922 | -0.098039 | 0.24194 | -0.1371 | 0.39216

## Slide 11: DSE Test

## Slide 12: E-Ratio Tests
Test result fields indicated by green |  |  |  | 
Test Case | eRatio | Baseline Home End Use Loads (REUL) |  | 
 |  | Winter | Summer | Hot Water
 |  | (MBtu) | (MBtu) | (MBtu)
L130AO-01 | 152.37 | 6.18 | 29.83 | 3.88
L130AO-02 | 142.14 | 6.18 | 29.83 | 3.88
L130AO-03 | 151.52 | 6.18 | 29.83 | 3.88
L130AO-04 | 118.53 | 6.18 | 29.83 | 3.88
L130AO-05 | 145.88 | 6.18 | 29.83 | 3.88
 | REUL Tests: | PASS | PASS | PASS
eRatio Tests
PASS
PASS
PASS
PASS
PASS

## Slide 13: FL Auto-Gen Tests
All 4 Standard Reference homes were generated accurately
All 4 tests generated e-ratios of 1.0 (PASS)

## Slide 14: HVAC Tests

## Slide 15: Prescriptive Compliance
Test House | R-Value Method | Notes | Total UA Alternative Method | Notes
Tampa01 | PASS |  | PASS | 
Tampa02 | PASS |  | PASS | 
Tampa03 | PASS |  | PASS | 
Miami-1 | PASS |  | PASS | 
Miami02 | PASS | Steel Frame Walls not allowed | PASS | 
Miami03 | PASS |  | PASS | 

## Slide 16: Conclusions
All requested tests have been completed and passed
Vendor has submitted documentation requested in Technical Assistance Manual
EnergyGauge USA 4.0 complies with the 5th Edition (2014) Florida Building Code Energy Conservation