Florida Supplement to the 2012 IBC

Chapters 1-35 (Excluding HVHZ and Florida Specific Chapter 4 Requirements)

PRE-GLITCH CORRECTION VERSION

Note 1:  Throughout the document, change International Building Code to Florida Building Code, Building; change the ICC Electrical Code to Chapter 27 of the Florida Building Code, Building; change the International Energy Conservation Code to the Florida Building Code, Energy Conservation; change the International Existing Building Code to Florida Building Code, Existing Building; change the International Fire code to Florida Fire Prevention Code; change International Fuel Gas Code to Florida Building Code, Fuel Gas; change the International Mechanical Code to Florida Building Code, Mechanical; change the International Plumbing Code to Florida Building Code, Plumbing; change the International Residential Code to Florida Building Code, Residential.

Chapter 1 – Scope and Administration

Section 101 – General

Change Section 101 to read as follows:

101.1 Title. These regulations shall be known as the Florida Building Code, hereinafter referred to as “this code.”

101.2 Scope. (No Change)

Exceptions:

1.  Detached one- and two-family dwellings and multiple single-family dwellings and multiple single-family dwellings (town houses) not more than three stories above grade plane in height with a separate means of egress and their accessory structures shall comply with the International Residential Code Florida Building Code, Residential.

2.  Existing buildings undergoing repair, alterations or additions and change of occupancy shall comply with Chapter 34 of this code.

101.2.1 Appendices. (No Change)

101.3 Intent. (No Change)

101.4 Referenced codes. The other codes listed in Sections 101.4.1 through 101.4.6 8 and referenced elsewhere in this code shall be considered part of the requirements of this code to the prescribed extent of each such reference.

101.4.1-101.4.3 (No Change)

101.4.4 Property maintenance. The provisions of the International Property Maintenance Code shall apply to existing structures and premises; equipment and facilities; light, ventilation, space heating, sanitation, life and fire safety hazards; responsibilities of owners, operators and occupants; and occupancy of existing premises and structures. Reserved.

101.4.5 Fire prevention. The provisions of the International Fire Code For provisions related to fire prevention, refer to the Florida Fire Prevention Code. The Florida Fire Prevention Code shall apply to matters affecting or relating to structures, processes and premises from the hazard of fire and explosion arising from the storage, handling or use of structures, materials or devices; from conditions hazardous to life, property or public welfare in the occupancy of structures or premises; and from the construction, extension, repair, alteration or removal of fire suppression, automatic sprinkler systems and alarm systems or fire hazards in the structure or on the premises from occupancy or operation.

101.4.6 (No Change)

101.4.7 Accessibility. For provisions related to accessibility, refer to the Florida Building Code, Accessibility.

101.4.8 Manufactured buildings. For additional administrative and special code requirements, see section 458, Florida Building Code, Building, and Rule 61-41 F.A.C.

(Mod CA4952 – R2 / AM)

Section 102 – Applicability

Add Section 102.1.1 to read as follows:

102.1.1  The Florida Building Code does not apply to, and no code enforcement action shall be brought with respect to, zoning requirements, land use requirements and owner specifications or programmatic requirements which do not pertain to and govern the design, construction, erection, alteration, modification, repair or demolition of public or private buildings, structures or facilities or to programmatic requirements that do not pertain to enforcement of the Florida Building Code.  Additionally, a local code enforcement agency may not administer or enforce the Florida Building Code, Building to prevent the siting of any publicly owned facility, including, but not limited to, correctional facilities, juvenile justice facilities, or state universities, community colleges, or public education facilities, as provided by law.

(Mod CA4986 / AS)

Section 102 – Applicability

Change Section 102 to read as follows:

102.2 Other Laws. Building. The provisions of this code shall not be deemed to nullify any provisions of local, state or federal law. The provisions of the Florida Building Code shall apply to the construction, erection, alteration, modification, repair, equipment, use and occupancy, location, maintenance, removal and demolition of every public and private building, structure or facility or floating residential structure, or any appurtenances connected or attached to such buildings, structures or facilities. Additions, alterations, repairs and changes of use or occupancy group in all buildings and structures shall comply with the provisions provided in Chapter 34 of this code. The following buildings, structures and facilities are exempt from the Florida Building Code as provided by law, and any further exemptions shall be as determined by the legislature and provided by law:

(a) Building and structures specifically regulated and preempted by the federal government.

(b) Railroads and ancillary facilities associated with the railroad.

(c)   Nonresidential farm buildings on farms.

(d) Temporary buildings or sheds used exclusively for construction purposes.

(e) Mobile or modular structures used as temporary offices, except that the provisions of Part II (Section 553.501-553.513, Florida Statutes) relating to accessibility by persons with disabilities shall apply to such mobile or modular structures.

(f)   Those structures or facilities of electric utilities, as defined in Section 366.02, Florida Statutes, which are directly involved in the generation, transmission, or distribution of electricity.

(g) Temporary sets, assemblies, or structures used in commercial motion picture or television production, or any sound-recording equipment used in such production, on or off the premises.

(h)  Chickees constructed by the Miccosukee Tribe of Indians of Florida or the Seminole Tribe of Florida. As used in this paragraph, the term “chickee” means an open-sided wooden hut that has a thatched roof of palm or palmetto or other traditional materials, and that does not incorporate any electrical, plumbing, or other nonwood features.

(i) Family mausoleums not exceeding 250 square feet in area which are prefabricated and assembled on site or preassembled and delivered on site and have walls, roofs, and a floor constructed of granite, marble, or reinforced concrete.

(j) Temporary housing provided by the Department of Corrections to any prisoner in the state correctional system.

(k) A building or structure having less than 1,000 square feet which is constructed and owned by a natural person for hunting and which is repaired or reconstructed to the same dimension and condition as existed on January 1, 2011, if the building or structure:

1. Is not rented or leased or used as a principal residence;

2. Is not located within the 100-year floodplain according to the Federal Emergency Management Agency’s current Flood Insurance Rate Map; and

3. Is not connected to an off-site electric power or water supply.

102.2.1 – 102.2.6. Add to read as follows:

102.2.1 In addition to the requirements of Section 553.79 and 553.80, Florida Statutes, facilities subject to the provisions of Chapter 395, Florida Statutes, and Part II of Chapter 400, Florida Statutes, shall have facility plans reviewed and construction surveyed by the state agency authorized to do so under the requirements of Chapter 395, Florida Statutes, and Part II of Chapter 400, Florida Statutes, and the certification requirements of the federal government.

102.2.2 Residential buildings or structures moved into or within a county or municipality shall not be required to be brought into compliance with the state minimum building code in force at the time the building or structure is moved, provided:

1.  The building or structure is structurally sound and in occupiable condition for its intended use;

2.  The occupancy use classification for the building or structure is not changed as a result of the move;

3.  The building is not substantially remodeled;

4.  Current fire code requirements for ingress and egress are met;

5.  Electrical, gas and plumbing systems meet the codes in force at the time of construction and are operational and safe for reconnection; and

6.  Foundation plans are sealed by a professional engineer or architect licensed to practice in this state, if required by the Florida Building Code, Building for all residential buildings or structures of the same occupancy class.

102.2.3 The building official shall apply the same standard to a moved residential building or structure as that applied to the remodeling of any comparable residential building or structure to determine whether the moved structure is substantially remodeled. The cost of the foundation on which the moved building or structure is placed shall not be included in the cost of remodeling for purposes of determining whether a moved building or structure has been substantially remodeled.

102.2.4 This section does not apply to the jurisdiction and authority of the Department of Agriculture and Consumer Services to inspect amusement rides or the Department of Financial Services to inspect state-owned buildings and boilers.

102.2.5 Each enforcement district shall be governed by a board, the composition of which shall be determined by the affected localities.

1. At its own option, each enforcement district or local enforcement agency may adopt rules granting to the owner of a single-family residence one or more exemptions from the Florida Building Code relating to:

a. Addition, alteration, or repairs performed by the property owner upon his or her own property, provided any addition or alteration shall not exceed 1,000 square feet or the square footage of the primary structure, whichever is less.

b. Addition, alteration, or repairs by a nonowner within a specific cost limitation set by rule, provided the total cost shall not exceed $5,000 within any 12-month period.

c. Building and inspection fees.

2. However, the exemptions under subparagraph 1 do not apply to single-family residences that are located in mapped flood hazard areas, as defined in the code, unless the enforcement district or local enforcement agency has determined that the work, which is otherwise exempt, does not constitute a substantial improvement, including the repair of substantial damage, of such single-family residences.

3. Each code exemption, as defined in sub-subparagraphs 1a, 1b, and 1c shall be certified to the local board 10 days prior to implementation and shall only be effective in the territorial jurisdiction of the enforcement district or local enforcement agency implementing it.

102.2.6 This section does not apply to swings and other playground equipment accessory to a one- or two-family dwelling.

Exception: Electrical service to such playground equipment shall be in accordance with Chapter 27 of this code.

(Mod CA4988 – R1 / AM)

Section 102 – Applicability

Change Section 102.5 to read as follows:

102.5 Partial invalidity. In the event that any part or provision of this code is held to be illegal or void, this shall not have the effect of making void or illegal any of the other parts or provisions. Reserved.

(Mod CA4992 – R1 / AM)

Section 102 – Applicability

Change Section 102.6 to read as follows:

102.6 Existing structures. The legal occupancy of any structure existing on the date of adoption of this code shall be permitted to continue without change, except as is specifically covered in this code, the International Property Maintenance Code or the International Fire Code, the Florida Fire Prevention Code, or as is deemed necessary by the building official for the general safety and welfare of the occupants and the public.

(Mod CA4994 – R1 / AM)

Section 102 – Applicability

Change Section 102.7 to read as follows:

102.7 Relocation of manufactured buildings.

(1)	Relocation of an existing manufactured building does not constitute an alteration.

(2) A relocated building shall comply with wind speed requirements of the new location, using the appropriate wind speed map.  If the existing building was manufactured in compliance with the Standard Building Code (prior to March 1, 2002), the wind speed map of the Standard Building Code shall be applicable. If the existing building was manufactured in compliance with the Florida Building Code (after March 1, 2002), the wind speed map of the Florida Building Code shall be applicable.

(3) A relocated building shall comply with the flood hazard area requirements of the new location, if applicable.

(Mod SP 5254 / AS)

Section 102 – Applicability

Add Section 102.8 to read as follows:

102.8  Existing mechanical equipment. An agency or local government may not require that existing mechanical equipment on the surface of a roof be installed in compliance with the requirements of the Florida Building Code until the equipment is required to be removed or replaced.

(Mod CA 4997 – R1 / AM)

Section 103 – Department of Building Safety

Change Section 103 to read as follows:

SECTION 103

DEPARTMENT OF BUILDING SAFETY

RESERVED

103.1 Creation of enforcement agency. 
The Department of Building Safety is hereby created and the official in charge thereof shall be known as the building official. 

103.2 Appointment. 
The building official shall be appointed by the chief appointing authority of the jurisdiction. 

103.3 Deputies. 
In accordance with the prescribed procedures of this jurisdiction and with the concurrence of the appointing authority, the building official shall have the authority to appoint a deputy building official, the related technical officers, inspectors, plan examiners and other employees. Such employees shall have powers as delegated by the building official. For the maintenance of existing properties, see the International Property Maintenance Code.

(Mod CA4991- R1 / AM)

Section 104 - Duties and Powers of Building Official

Change Section 103 to read as follows:

104.1 General. The building official is hereby authorized and directed to enforce the provisions of this code. The building official shall have the authority to render interpretations of this code and to adopt policies and procedures in order to clarify the application of its provisions. Such interpretations, policies and procedures shall be in compliance with the intent and purpose of this code. Such policies and procedures shall not have the effect of waiving requirements specifically provided for in this code.   Reserved.

104.2 Applications and permits. The building official shall receive applications, review construction documents and issue permits for the erection, and alteration, demolition and moving of buildings and structures, inspect the premises for which such permits have been issued and enforce compliance with the provisions of this code.  Reserved.

104.3 Notices and orders. The building official shall issue all necessary notices or orders to ensure compliance with this code. Reserved.

104.4 Inspections. The building official shall make all of the required inspections, or the building official shall have the authority to accept reports of inspection by approved agencies or individuals. Reports of such inspections shall be in writing and be certified by a responsible officer of such approved agency or by the responsible individual. The building official is authorized to engage such expert opinion as deemed necessary to report upon unusual technical issues that arise, subject to the approval of the appointing authority. Reserved.

104.5 Identification. The building official shall carry proper identification when inspecting structures or premises in the performance of duties under this code. Reserved.

104.6 Right of entry.  Where it is necessary to make an inspection to enforce the provisions of this code, or where the building official has reasonable cause to believe that there exists in a structure or upon a premises a condition which is contrary to or in violation of this code which makes the structure or premises unsafe, dangerous or hazardous, the building official is authorized to enter the structure or premises at reasonable times to inspect or to perform the duties imposed by this code, provided that if such structure or premises be occupied that credentials be presented to the occupant and entry requested. If such structure or premises is unoccupied, the building official shall first make a reasonable effort to locate the owner or other person having charge or control of the structure or premises and request entry. If entry is refused, the building official shall have recourse to the remedies provided by law to secure entry. Reserved.

104.7 Department records. The building official shall keep official records of applications received, permits and certificates issued, fees collected, reports of inspections, and notices and orders issued. Such records shall be retained in the official records for the period required for retention of public records. Reserved.

104.8 Liability.  The building official, member of the board of appeals or employee charged with the enforcement of this code, while acting for the jurisdiction in good faith and without malice in the discharge of the duties required by this code or other pertinent law or ordinance, shall not thereby be rendered liable personally and is hereby relieved from personal liability for any damage accruing to persons or property as a result of any act or by reason of an act or omission in the discharge of official duties. Any suit instituted against an officer or employee because of an act performed by that officer or employee in the lawful discharge of duties and under the provisions of this code shall be defended by legal representative of the jurisdiction until the final termination of the proceedings. The building official or any subordinate shall not be liable for cost in any action, suit or proceeding that is instituted in pursuance of the provisions of this code. Reserved.

104.9 Approved materials and equipment. (No change)

104.10 Modifications. Wherever there are practical difficulties involved in carrying out the provisions of this code, the building official shall have the authority to grant modifications for individual cases, upon application of the owner or owner’s representative, provided the building official shall first find that special individual reason makes the strict letter of this code impractical and the modification is in compliance with the intent and purpose of this code and that such modification does not lessen health, accessibility, life and fire safety, or structural requirements. The details of action granting modifications shall be recorded and entered in the files of the department of building safety. Reserved.

104.10.1 Flood hazard areas. The building official shall not grant modifications to any provision required in flood hazard areas as established by Section 1612.3 unless a determination has been made that:

1. A showing of good and sufficient cause that the unique characteristics of the size, configuration or topography of the site render the elevation standards of Section 1612 inappropriate.

2. A determination that failure to grant the variance would result in exceptional hardship by rendering the lot undevelopable.

3. A determination that the granting of a variance will not result in increased flood heights, additional threats to public safety, extraordinary public expense, cause fraud on or victimization of the public, or conflict with existing laws or ordinances.

4. A determination that the variance is the minimum necessary to afford relief, considering the flood hazard.

5. Submission to the applicant of written notice specifying the difference between the design flood elevation and the elevation to which the building is to be built, stating that the cost of flood insurance will be commensurate with the increased risk resulting from the reduced floor elevation, and stating that construction below the design flood elevation increases risks to life and property.  Reserved.

104.11 Alternative materials, design and methods of construction and equipment. (No change)

(Mod CA4998 – R1 / AM)

Section 105 – Permits

Change Section 105.1 to read as follows:

105.1 Required. Any owner or authorized agent who intends to construct, enlarge, alter, repair, move, demolish, or change the occupancy of a building or structure, or to erect, install, enlarge, alter, repair, remove, convert or replace any impact resistant coverings, electrical, gas, mechanical or plumbing system, the installation of which is regulated by this code, or to cause any such work to be done, shall first make application to the building official and obtain the required permit.

(Mod CA5634 / AS)

Section 105 – Permits

Change Section 105.1.1 to read as follows:

105.1.1 Annual facility permit. In lieu of an individual permit for each alteration to an already approved existing electrical, gas, mechanical, or plumbing or interior nonstructural office system(s) installation, the building official is authorized to issue an annual permit upon application therefor to any person, firm or corporation regularly employing one or more qualified tradepersons in the building, structure or on the premises owned or operated by the applicant for the permit. for any occupancy to facilitate routine or emergency service, repair, refurbishing, minor renovations of service systems or manufacturing equipment installations/relocations. The building official shall be notified of major changes and shall retain the right to make inspections at the facility site as deemed necessary. An annual facility permit shall be assessed with an annual fee and shall be valid for one year from date of issuance. A separate permit shall be obtained for each facility and for each construction trade, as applicable. The permit application shall contain a general description of the parameters of work intended to be performed during the year.

Add Section 105.1.3 to read as follows:

105.1.3 Food permit. As per Section 500.12, Florida Statutes, a food permit from the Department of Agriculture and Consumer Services is required of any person who operates a food establishment or retail store.

Change Section 105.2 to read as follows:

105.2 Work exempt from permit.  (No Change)

Building:

1. One-story detached accessory structures used as tool and storage sheds, playhouses and similar uses, provided the floor area is not greater than 120 square feet (11 m2).

2. Fences not over 7 feet (2134 mm) high.

3. Oil derricks.

4. Retaining walls that are not over 4 feet (1219 mm) in height measured from the bottom of the footing to the top of the wall, unless supporting a surcharge or impounding Class I, II or IIIA liquids.

5. Water tanks supported directly on grade if the capacity is not greater than 5,000 gallons (18 925 L) and the ratio of height to diameter or width is not greater than 2:1.

6. Sidewalks and driveways not more than 30 inches (762 mm) above adjacent grade, and not over any basement or story below and are not part of an accessible route.

7. Painting, papering, tiling, carpeting, cabinets, counter tops and similar finish work.

8. Temporary motion picture, television and theater stage sets and scenery.

9. Prefabricated swimming pools accessory to a Group R-3 occupancy that are less than 24 inches (610 mm) deep, are not greater than 5,000 gallons (18 925 L) and are installed entirely above ground.

10. Shade cloth structures constructed for nursery or agricultural purposes, not including service systems.

11. Swings and other playground equipment accessory to detached one- and two-family dwellings.

12. Window awnings in Group R-3 and U occupancies, supported by an exterior wall that do not project more than 54 inches (1372 mm) from the exterior wall and do not require additional support.

13. Nonfixed and movable fixtures, cases, racks, counters and partitions not over 5 feet 9 inches (1753 mm) in height.

Electrical:

Repairs and maintenance: Minor repair work, including the replacement of lamps or the connection of approved portable electrical equipment to approved permanently installed receptacles. 

Radio and television transmitting stations: The provisions of this code shall not apply to electrical equipment used for radio and television transmissions, but do apply to equipment and wiring for a power supply and the installations of towers and antennas. 

Temporary testing systems: A permit shall not be required for the installation of any temporary system required for the testing or servicing of electrical equipment or apparatus.

Gas: (No Change)

Mechanical:

1. – 7. (No Change)

8.  The installation, replacement, removal or metering of any load management control device.

Plumbing: (No Change)

Change Section 105.2.2 to read as follows:

105.2.2 Repairs. Minor repairs. Ordinary minor repairs may be made with the approval of the building official without a permit, provided the repairs do Application or notice to the building official is not required for ordinary repairs to structures, replacement of lamps or the connection of approved portable electrical equipment to approved permanently installed receptacles. Such repairs shall not include the cutting away of any wall, partition or portion thereof, the removal or cutting of any structural beam or load-bearing support, or the removal or change of any required means of egress, or rearrangement of parts of a structure affecting the egress requirements; additionally, ordinary minor repairs shall not include addition to, alteration of, replacement or relocation of any standpipe, water supply, sewer, drainage, drain leader, gas, soil, waste, vent or similar piping, electric wiring systems or mechanical equipment or other work affecting public health or general safety, and such repairs shall not violate any of the provisions of the technical codes.

Change Section 105.3 to read as follows:

105.3 Application for permit. To obtain a permit, the applicant shall first file an application therefor in writing on a form furnished by the department of building safety building department for that purpose. Such application shall:

1. Identify and describe the work to be covered by the permit for which application is made.

2. Describe the land on which the proposed work is to be done by legal description, street address or similar description that will readily identify and definitely locate the proposed building or work.

3. Indicate the use and occupancy for which the proposed work is intended.

4. Be accompanied by construction documents and other information as required in Section 107.

5. State the valuation of the proposed work.

6. Be signed by the applicant, or the applicant’s authorized agent.

7. Give such other data and information as required by the building official.

Permit application forms shall be in the format prescribed by a local administrative board, if applicable, and must comply with the requirements of Section 713.135(5) and (6), Florida Statutes.

Each application shall be inscribed with the date of application, and the code in effect as of that date. For a building permit for which an application is submitted prior to the effective date of the Florida Building Code, the state minimum building code in effect in the permitting jurisdiction on the date of the application governs the permitted work for the life of the permit and any extension granted to the permit.

105.3.1 Action on application. The building official shall examine or cause to be examined applications for permits and amendments thereto within a reasonable time after filing. If the application or the construction documents do not conform to the requirements of pertinent laws, the building official shall reject such application in writing, stating the reasons therefor. If the building official is satisfied that the proposed work conforms to the requirements of this code and laws and ordinances applicable thereto, the building official shall issue a permit therefor as soon as practicable. When authorized through contractual agreement with a school board, in acting on applications for permits, the building official shall give first priority to any applications for the construction of, or addition or renovation to, any school or educational facility.

105.3.1.1 If a state university, Florida college or public school district elects to use a local government’s code enforcement offices, fees charged by counties and municipalities for enforcement of the Florida Building Code on buildings, structures, and facilities of state universities, state colleges, and public school districts shall not be more than the actual labor and administrative costs incurred for plans review and inspections to ensure compliance with the code.

105.3.1.2 No permit may be issued for any building construction, erection, alteration, modification, repair, or addition unless the applicant for such permit provides to the enforcing agency which issues the permit any of the following documents which apply to the construction for which the permit is to be issued and which shall be prepared by or under the direction of an engineer registered under Chapter 471, Florida Statutes:

1.  Plumbing documents for any new building or addition which requires a plumbing system with more than 250 fixture units or which costs more than $125,000.

2.  Fire sprinkler documents for any new building or addition which includes a fire sprinkler system which contains 50 or more sprinkler heads. Personnel as authorized by chapter 633 Florida Statutes, may design a fire sprinkler system of 49 or fewer heads and may design the alteration of an existing fire sprinkler system if the alteration consists of the relocation, addition or deletion of not more than 49 heads, notwithstanding the size of the existing fire sprinkler system.

3. Heating, ventilation, and air-conditioning documents for any new building or addition which requires more than a 15-ton-per-system capacity which is designed to accommodate 100 or more persons or for which the system costs more than $125,000. This paragraph does not include any document for the replacement or repair of an existing system in which the work does not require altering a structural part of the building or for work on a residential one, two, three or four-family structure.

An air-conditioning system may be designed by an installing air-conditioning contractor certified under Chapter 489, Florida Statutes, to serve any building or addition which is designed to accommodate fewer than 100 persons and requires an air-conditioning system with a value of $125,000 or less; and when a 15-ton-per system or less is designed for a singular space of a building and each 15-ton system or less has an independent duct system. Systems not complying with the above require design documents that are to be sealed by a professional engineer.

Example 1: When a space has two 10-ton systems with each having an independent duct system, the contractor may design these two systems since each unit (system) is less than 15 tons.

Example 2: Consider a small single-story office building which consists of six individual offices where each office has a single three-ton package air conditioning heat pump. The six heat pumps are connected to a single water cooling tower. The cost of the entire heating, ventilation and air-conditioning work is $47,000 and the office building accommodates fewer than 100 persons. Because the six mechanical units are connected to a common water tower this is considered to be an 18-ton system.

NOTE: It was further clarified by the Commission that the limiting criteria of 100 persons and $125,000 apply to the building occupancy load and the cost for the total air-conditioning system of the building.

4.  Any specialized mechanical, electrical, or plumbing document for any new building or addition which includes a medical gas, oxygen, steam, vacuum, toxic air filtration, halon, or fire detection and alarm system which costs more than $5,000.

5. Electrical documents. See Florida Statutes 471.003(2)(h).

Documents requiring an engineer seal by this part shall not be valid unless a professional engineer who possesses a valid certificate of registration has signed, dated, and stamped such document as provided in Section 471.025, Florida Statutes.

6.  All public swimming pools and public bathing places defined by and regulated under Chapter 514, Florida Statutes

105.3.3 An enforcing authority may not issue a building permit for any building construction, erection, alteration, modification, repair or addition unless the permit either includes on its face or there is attached to the permit the following statement: “NOTICE: In addition to the requirements of this permit, there may be additional restrictions applicable to this property that may be found in the public records of this county, and there may be additional permits required from other governmental entities such as water management districts, state agencies, or federal agencies.”

105.3.4 A building permit for a single-family residential dwelling must be issued within 30 working days of application therefor unless unusual circumstances require a longer time for processing the application or unless the permit application fails to satisfy the Florida Building Code or the enforcing agency’s laws or ordinances.

105.3.5 Identification of minimum premium policy. Except as otherwise provided in Chapter 440, Florida Statutes, Workers’ Compensation, every employer shall, as a condition to receiving a building permit, show proof that it has secured compensation for its employees as provided in Section 440.10 and 440.38, Florida Statutes.

105.3.6 Asbestos removal. Moving, removal or disposal of asbestos-containing materials on a residential building where the owner occupies the building, the building is not for sale or lease, and the work is performed according to the owner-builder limitations provided in this paragraph. To qualify for exemption under this paragraph, an owner must personally appear and sign the building permit application. The permitting agency shall provide the person with a disclosure statement in substantially the following form:

Disclosure Statement: State law requires asbestos abatement to be done by licensed contractors. You have applied for a permit under an exemption to that law. The exemption allows you, as the owner of your property, to act as your own asbestos abatement contractor even though you do not have a license. You must supervise the construction yourself. You may move, remove or dispose of asbestos-containing materials on a residential building where you occupy the building and the building is not for sale or lease, or the building is a farm outbuilding on your property. If you sell or lease such building within 1 year after the asbestos abatement is complete, the law will presume that you intended to sell or lease the property at the time the work was done, which is a violation of this exemption. You may not hire an unlicensed person as your contractor. Your work must be done according to all local, state and federal laws and regulations which apply to asbestos abatement projects. It is your responsibility to make sure that people employed by you have licenses required by state law and by county or municipal licensing ordinances.

105.3.7 Applicable Code for Manufactured Buildings. Manufacturers should be permitted to complete all buildings designed and approved prior to the effective date of a new code edition, provided a clear signed contract is in place. The contract shall provide specific data mirroring that required by an application for permit, specifically, without limitation, date of execution, building owner or dealer, and anticipated date of completion. However, the construction activity must commence within 6 months of the contract's execution. The contract is subject to verification by the Department of Business and Professional Regulation.

(Mod CA4999  - R1/ AM)

(Mod CA5753 / AS)

(Mod CA5250 / AS)

Section 105 – Permits

Change Section 105.5 to read as follows:

105.5 Expiration. Every permit issued shall become invalid unless the work on the site authorized by such permit is commenced within 180 days after its issuance, or if the work authorized on the site by such permit is suspended or abandoned for a period of 180 days after the time the work is commenced. The building official is authorized to grant, in writing, one or more extensions of time, for periods not more than 180 days each. The extension shall be requested in writing and justifiable cause demonstrated. Reserved.

(Mod CA5002-R1 / AM)

Section 105 – Permits

Change Section 105.6 to read as follows:

105.6 Suspension or revocation.  Denial or revocation.  The building official is authorized to suspend or revoke a permit issued under the provisions of this code wherever the permit is issued in error or on the basis of incorrect, inaccurate or incomplete information, or in violation of any ordinance or regulation or any of the provisions of this code. Whenever a permit required under this section is denied or revoked because the plan, or the construction, erection, alteration, modification, repair, or demolition of a building, is found by the local enforcing agency to be not  in compliance with the Florida Building Code, the local enforcing agency shall identify the specific plan or project features that do not comply with the applicable codes, identify the specific code chapters and sections upon which the finding is based, and provide this information to the permit applicant. If the local building code administrator or inspector finds that the plans are not in compliance with the Florida Building Code, the local building code administrator or inspector shall identify the specific plan features that do not comply with the applicable codes, identify the specific code chapters and sections upon which the finding is based, and provide this information to the local enforcing agency. The local enforcing agency shall provide this information to the permit applicant.

(Mod CA5006 / AS)

Section 105 – Permits

Add Section 105.8 to read as follows:

105.8 Notice of commencement. As per Section 713.135, Florida Statutes, when any person applies for a building permit, the authority issuing such permit shall print on the face of each permit card in no less than 14-point, capitalized, boldfaced type: “WARNING TO OWNER: YOUR FAILURE TO RECORD A NOTICE OF COMMENCEMENT MAY RESULT IN YOUR PAYING TWICE FOR IMPROVEMENTS TO YOUR PROPERTY. A NOTICE OF COMMENCEMENT MUST BE RECORDED AND POSTED ON THE JOB SITE BEFORE THE FIRST INSPECTION. IF YOU INTEND TO OBTAIN FINANCING, CONSULT WITH YOUR LENDER OR AN ATTORNEY BEFORE RECORDING YOUR NOTICE OF COMMENCEMENT.”

(Mod CA5021-R1 / AM)

Section 105 – Permits

Add Section 105.9 to read as follows:

105.9 Asbestos. The enforcing agency shall require each building permit for the demolition or renovation of an existing structure to contain an asbestos notification statement which indicates the owner’s or operator’s responsibility to comply with the provisions of Section 469.003, Florida Statutes, and to notify the Department of Environmental Protection of his or her intentions to remove asbestos, when applicable, in accordance with state and federal law.

(Mod CA5022-R1 / AM)

Section 105 – Permits

Add Section 105.10 to read as follows:

105.10 Certificate of protective treatment for prevention of termites.   A weather-resistant job-site posting board shall be provided to receive duplicate treatment certificates as each required protective treatment is completed, providing a copy for the person the permit is issued to and another copy for the building permit files. The treatment certificate shall provide the product used, identity of the applicator, time and date of the treatment, site location, area treated, chemical used, percent concentration and number of gallons used, to establish a verifiable record of protective treatment. If the soil chemical barrier method for termite prevention is used, final exterior treatment shall be completed prior to final building approval.

(Mod CA5078-R1 / AM)

Section 105 – Permits

Add Section 105.11 to read as follows:

105.11 Notice of termite protection. A permanent sign which identifies the termite treatment provider and need for reinspection and treatment contract renewal shall be provided. The sign shall be posted near the water heater or electric panel.

(Mod CA5079-R1 / AM)

Section 105 – Permits

Add Section 105.12 to read as follows:

105.12 Work starting before permit issuance. Upon approval of the building official, the scope of work delineated in the building permit application and plan may be started prior to the final approval and issuance of the permit, provided any work completed is entirely at risk of the permit applicant and the work does not proceed past the first required inspection.

(Mod CA 5080 / AS)

Section 105 – Permits

Add Section 105.13 to read as follows:

105.13 Phased permit approval.  After submittal of the appropriate construction documents, the building official is authorized to issue a permit for the construction of foundations or any other part of a building or structure before the construction documents for the whole building or structure have been submitted. The holder of such permit for the foundation or other parts of a building or structure shall proceed at the holder’s own risk with the building operation and without assurance that a permit for the entire structure will be granted. Corrections may be required to meet the requirements of the technical codes.

(Mod CA5081 / AS)

Section 105 – Permits

Add Section 105.14 to read as follows:

105.14 Permit issued on basis of an affidavit.  Whenever a permit is issued in reliance upon an affidavit or whenever the work to be covered by a permit involves installation under conditions which, in the opinion of the building official, are hazardous or complex, the building official shall require that the architect or engineer who signed the affidavit or prepared the drawings or computations shall supervise such work. In addition, they shall be responsible for conformity to the permit, provide copies of inspection reports as inspections are performed, and upon completion make and file with the building official written affidavit that the work has been done in conformity to the reviewed plans and with the structural provisions of the technical codes. In the event such architect or engineer is not available, the owner shall employ in his stead a competent person or agency whose qualifications are reviewed by the building official. The building official shall ensure that any person conducting plans review is qualified as a plans examiner under Part XII of Chapter 468, Florida Statutes, and that any person conducting inspections is qualified as a building inspector under Part III of Chapter 468, Florida Statutes.

Exception: Permit issued on basis of an affidavit shall not extend to the flood load and flood resistance requirements of the Florida Building Code.

(Mod CA5082-R1 / AM)

Section 105 – Permits

Add Section 105.15 to read as follows:

105.15 Opening protection. When any activity requiring a building permit that is applied for on or after July 1, 2008, and for which the estimated cost is $50,000 or more for a site built single-family detached residential structure that is located in the wind borne debris region as defined in this Code and that has an insured value of $750,000 or more, or, if the site built single-family detached residential structure is uninsured or for which documentation of insured value is not presented, has a just valuation for the structure for purposes of ad valorem taxation of $750,000 or more; opening protections as required within this Code or Florida Building Code, Residential for new construction shall be provided.

Exception: Single family residential structures permitted subject to the Florida Building Code are not required to comply with this section.

(Mod CA5083 / AS)

Section 107 – Submittal Documents

Change Section 107.3 to read as follows:

107.3 Examination of documents. The building official shall examine or cause to be examined the accompanying submittal documents and shall ascertain by such examinations whether the construction indicated and described is in accordance with the requirements of this code and other pertinent laws or ordinances.

Exceptions:

1. Building plans approved pursuant to Section 553.77(5), Florida Statutes, and state-approved manufactured buildings are exempt from local codes enforcing agency plan reviews except for provisions of the code relating to erection, assembly or construction at the site. Erection, assembly and construction at the site are subject to local permitting and inspections. Photocopies of plans approved according to FAC 9B-1.009, F.A.C., shall be sufficient for local permit application documents of record for the modular building portion of the permitted project.

2. Industrial construction on sites where design, construction and fire safety are supervised by appropriate design and inspection professionals and which contain adequate in-house fire departments and rescue squads is exempt, subject to local government option, from review of plans and inspections, providing owners certify that applicable codes and standards have been met and supply appropriate approved drawings to local building and fire-safety inspectors.

(Mod CA 5085/ AS)

Section 107 – Submittal Documents

Add Section 107.3.4.3 to read as follows:

107.3.4.2 Certifications by contractors authorized under the provisions of Section 489.115(4)(b), Florida Statutes, shall be considered equivalent to sealed plans and specifications by a person licensed under Chapter 471, Florida Statutes, or Chapter 481 Florida Statutes, by local enforcement agencies for plans review for permitting purposes relating to compliance with the wind-resistance provisions of the code or alternate methodologies approved by the Florida Building Commission for one- and two-family dwellings. Local enforcement agencies may rely upon such certification by contractors that the plans and specifications submitted conform to the requirements of the code for wind resistance. Upon good cause shown, local government code enforcement agencies may accept or reject plans sealed by persons licensed under Chapters 471, 481 or 489, Florida Statutes.

(Mod CA 5086 / AS)

Section 107 – Submittal Documents

Add Section 107.3.5 to read as follows:

107.3.5 Minimum plan review criteria for buildings. The examination of the documents by the building official shall include the following minimum criteria and documents: a floor plan; site plan; foundation plan; floor/roof framing plan or truss layout; all fenestration penetrations; flashing; and rough opening dimensions; and all exterior elevations:

Commercial Buildings:

Building

1.   Site requirements:

Parking

Fire access

Vehicle loading

Driving/turning radius

Fire hydrant/water supply/post indicator valve (PIV)

Set back/separation (assumed property lines)

Location of specific tanks, water lines and sewer lines

Flood hazard areas, flood zones, and design flood elevations

2.   Occupancy group and special occupancy requirements shall be determined.

3.   Minimum type of construction shall be determined (see Table 503).

4.   Fire-resistant construction requirements shall include the following components:

Fire-resistant separations

Fire-resistant protection for type of construction

Protection of openings and penetrations of rated walls

Fire blocking and draftstopping and calculated fire resistance

5.   Fire suppression systems shall include:

Early warning smoke evacuation systems Schematic fire sprinklers

Standpipes

Preengineered systems

Riser diagram

Same as above.

6.   Life safety systems shall be determined and shall include the following requirements:

Occupant load and egress capacities

Early warning

Smoke control

Stair pressurization

Systems schematic

7.   Occupancy load/egress requirements shall include:

Occupancy load

Gross

Net

Means of egress

Exit access

Exit

Exit discharge

Stairs construction/geometry and protection

Doors

Emergency lighting and exit signs

Specific occupancy requirements

Construction requirements

Horizontal exits/exit passageways

8.   Structural requirements shall include:

Soil conditions/analysis

Termite protection

Design loads

Wind requirements

Building envelope

Impact resistant coverings or systems

Structural calculations (if required)

Foundation

Flood requirements in accordance with Section 1612, including lowest floor elevations, enclosures, flood damage-resistant materials

Wall systems

Floor systems

Roof systems

Threshold inspection plan

Stair systems

9.   Materials shall be reviewed and shall at a minimum include the following:

Wood

Steel

Aluminum

Concrete

Plastic

Glass

Masonry

Gypsum board and plaster

Insulating (mechanical)

Roofing

Insulation

10. Accessibility requirements shall include the following:

Site requirements

Accessible route

Vertical accessibility

Toilet and bathing facilities

Drinking fountains

Equipment

Special occupancy requirements

Fair housing requirements

11. Interior requirements shall include the following:

Interior finishes (flame spread/smoke development)

Light and ventilation

Sanitation

12. Special systems:

Elevators

Escalators

Lifts

13. Swimming pools:

Barrier requirements

Spas

Wading pools

Electrical

1.   Electrical:

Wiring

Services

Feeders and branch circuits

Overcurrent protection

Grounding

Wiring methods and materials

GFCIs

2.   Equipment

3.   Special occupancies

4.   Emergency systems

5.   Communication systems

6.   Low voltage

7.   Load calculations

8. Design flood elevation

Plumbing

1.   Minimum plumbing facilities

2.   Fixture requirements

3.   Water supply piping

4.   Sanitary drainage

5.   Water heaters

6.   Vents

7.   Roof drainage

8.   Back flow prevention

9.   Irrigation

10. Location of water supply line

11. Grease traps

12. Environmental requirements

13. Plumbing riser

14. Design flood elevation

Mechanical

1.   Energy calculations

2.   Exhaust systems:

Clothes dryer exhaust

Kitchen equipment exhaust

Specialty exhaust systems

3.   Equipment

4.   Equipment location

5.   Make-up air

6.   Roof-mounted equipment

7.   Duct systems

8.   Ventilation

9.   Combustion air

10. Chimneys, fireplaces and vents

11. Appliances

12. Boilers

13. Refrigeration

14. Bathroom ventilation

15. Laboratory

16. Design flood elevation

Gas

1.   Gas piping

2.   Venting

3.   Combustion air

4.   Chimneys and vents

5.   Appliances

6.   Type of gas

7.   Fireplaces

8.   LP tank location

9.   Riser diagram/shutoffs

10. Design flood elevation

Demolition

1.   Asbestos removal

Residential (one- and two-family)

1.   Site requirements

Set back/separation (assumed property lines)

Location of septic tanks

2.   Fire-resistant construction (if required)

3.   Fire

4.   Smoke detector locations

5.   Egress

Egress window size and location stairs construction requirements

6.   Structural requirements shall include:

Wall section from foundation through roof, including assembly and materials connector tables wind requirements structural calculations (if required)

Flood hazard areas, flood zones, design flood elevations, lowest floor elevations, enclosures, equipment, and flood damage-resistant materials

7.   Accessibility requirements: show/identify accessible bath

8. impact resistant coverings or systems

Exemptions.

Plans examination by the building official shall not be required for the following work:

1.   Replacing existing equipment such as mechanical units, water heaters, etc.

2.   Reroofs

3.   Minor electrical, plumbing and mechanical repairs

4.   Annual maintenance permits

5.   Prototype plans

Except for local site adaptions, siding, foundations and/or modifications.

Except for structures that require waiver.

6.    Manufactured buildings plan except for foundations and modifications of buildings on site.

(Mod SP 5254 / AS)

(Mod CA 5087 / AS)

(Mod CA 5766 / AS)

Section 107 – Submittal Documents

Add Section 107.6. to read as follows:

107.6 Affidavits. The building official may accept a sworn affidavit from a registered architect or engineer stating that the plans submitted conform to the technical codes. For buildings and structures, the affidavit shall state that the plans conform to the laws as to egress, type of construction and general arrangement and, if accompanied by drawings, show the structural design and that the plans and design conform to the requirements of the technical codes as to strength, stresses, strains, loads and stability. The building official may without any examination or inspection accept such affidavit, provided the architect or engineer who made such affidavit agrees to submit to the building official copies of inspection reports as inspections are performed and upon completion of the structure, electrical, gas, mechanical or plumbing systems a certification that the structure, electrical, gas, mechanical or plumbing system has been erected in accordance with the requirements of the technical codes. Where the building official relies upon such affidavit, the architect or engineer shall assume full responsibility for compliance with all provisions of the technical codes and other pertinent laws or ordinances. The building official shall ensure that any person conducting plans review is qualified as a plans examiner under Part XII of Chapter 468, Florida Statutes, and that any person conducting inspections is qualified as a building inspector under Part XII of Chapter 468, Florida Statutes.

(Mod CA 5088 / AS)

Section 107 – Submittal Documents

Add Section 107.6.1 to read as follows:

107.6.1 Building permits issued on the basis of an affidavit. Pursuant to the requirements of federal regulation for participation in the National Flood Insurance Program (44 C.F.R. Parts 59 and 60), the authority granted to the Building Official to issue permits, to rely on inspections, and to accept plans and construction documents on the basis of affidavits and plans submitted pursuant to 105.14 and Section 107.6, shall not extend to the flood load and flood resistance construction requirements of the Florida Building Code.

(Mod SP 5255 / AS)

Section 109 – Fees

Change Section 109.5 to read as follows:

109.5 Related fees. The payment of the fee for the construction, alteration, removal or demolition for work done in connection to or concurrently with the work authorized by a building permit shall not relieve the applicant or holder of the permit from the payment of other fees that are prescribed by law. Reserved.

(Mod CA5091-R1 / AM)

Section 109 – Fees

Change Section 109.6 to read as follows:

109.6 Refunds. The building official is authorized to establish a refund policy. Reserved.

(Mod CA5092-R1 / AM)

Section 110 – Inspections

Change Section 110.3.5 to read as follows:

110.3 Required inspections. The building official, upon notification, shall make the inspections set forth in Sections 110.3.1 through 110.3.10. The building official upon notification from the permit holder or his or her agent shall make the following inspections, and shall either release that portion of the construction or shall notify the permit holder or his or her agent of any violations which must be corrected in order to comply with the technical codes. The building official shall determine the timing and sequencing of when inspections occur and what elements are inspected at each inspection.

Building

1.   Foundation inspection. To be made after trenches are excavated and forms erected and shall at a minimum include the following building components:

·Stem-wall

·Monolithic slab-on-grade

·Piling/pile caps

·Footers/grade beams

1.1. In flood hazard areas, upon placement of the lowest floor, including basement, and prior to further vertical construction, the elevation certification shall be submitted to the authority having jurisdiction.

2.   Framing inspection. To be made after the roof, all framing, fireblocking and bracing is in place, all concealing wiring, all pipes, chimneys, ducts and vents are complete and shall at a minimum include the following building components:

·Window/door framing

·Vertical cells/columns

·Lintel/tie beams

·Framing/trusses/bracing/connectors

·Draft stopping/fire blocking

·Curtain wall framing

·Energy insulation

·Accessibility.

·Verify rough opening dimensions are within tolerances.

3.   Sheathing inspection. To be made either as part of a dry-in inspection or done separately at the request of the contractor after all roof and wall sheathing and fasteners are complete and shall at a minimum include the following building components:

·Roof sheathing

·Wall sheathing

·Sheathing fasteners

·Roof/wall dry-in.

4.   Roofing inspection. Shall at a minimum include the following building components:

·Dry-in

·Insulation

·Roof coverings

·Flashing

5.   Final inspection. To be made after the building is completed and ready for occupancy.

5.1. In flood hazard areas, as part of the final inspection, a final certification of the lowest floor elevation shall be submitted to the authority having jurisdiction.

6.   Swimming pool inspection. First inspection to be made after excavation and installation of reinforcing steel, bonding and main drain and prior to placing of concrete.

Final inspection to be made when the swimming pool is complete and all required enclosure requirements are in place.

In order to pass final inspection and receive a certificate of completion, a residential swimming pool must meet the requirements relating to pool safety features as described in Section 424.2.17.

7.   Demolition inspections. First inspection to be made after all utility connections have been disconnected and secured in such manner that no unsafe or unsanitary conditions shall exist during or after demolition operations.

Final inspection to be made after all demolition work is completed.

8.   Manufactured building inspections. The building department shall inspect construction of foundations; connecting buildings to foundations; installation of parts identified on plans as site installed items, joining the modules, including utility crossovers; utility connections from the building to utility lines on site; and any other work done on site which requires compliance with the Florida Building Code. Additional inspections may be required for public educational facilities (see Section 423.27.20).

9. Where impact resistant coverings or impact resistant systems are installed , the building official shall schedule adequate inspections of impact resistant coverings or impact resistant systems to determine the following:

The system indicated on the plans was installed.

The system is installed in accordance with the manufacturer’s installation instructions and the product approval.

Electrical

1.   Underground inspection. To be made after trenches or ditches are excavated, conduit or cable installed, and before any backfill is put in place.

2.   Rough-in inspection. To be made after the roof, framing, fireblocking and bracing is in place and prior to the installation of wall or ceiling membranes.

3.         Final inspection. To be made after the building is complete, all required electrical fixtures are in place and properly connected or protected, and the structure is ready for occupancy.

Plumbing

1.   Underground inspection. To be made after trenches or ditches are excavated, piping installed, and before any backfill is put in place.

2.   Rough-in inspection. To be made after the roof, framing, fireblocking and bracing is in place and all soil, waste and vent piping is complete, and prior to this installation of wall or ceiling membranes.

3.   Final inspection. To be made after the building is complete, all plumbing fixtures are in place and properly connected, and the structure is ready for occupancy.

Note: See Section P312 of the Florida Building Code, Plumbing for required tests.

Mechanical

1.   Underground inspection. To be made after trenches or ditches are excavated, underground duct and fuel piping installed, and before any backfill is put in place.

2.   Rough-in inspection. To be made after the roof, framing, fire blocking and bracing are in place and all ducting, and other concealed components are complete, and prior to the installation of wall or ceiling membranes.

3.         Final inspection. To be made after the building is complete, the mechanical system is in place and properly connected, and the structure is ready for occupancy.

Gas

1.   Rough piping inspection. To be made after all new piping authorized by the permit has been installed, and before any such piping has been covered or concealed or any fixtures or gas appliances have been connected.

2.   Final piping inspection. To be made after all piping authorized by the permit has been installed and after all portions which are to be concealed by plastering or otherwise have been so concealed, and before any fixtures or gas appliances have been connected. This inspection shall include a pressure test.

3.         Final inspection. To be made on all new gas work authorized by the permit and such portions of existing systems as may be affected by new work or any changes, to ensure compliance with all the requirements of this code and to assure that the installation and construction of the gas system is in accordance with reviewed plans.

(Mod CA 5252 / AS)

(Mod SP 5254/ AS)

Section 110 – Inspections

Add Section 110.3.11 to read as follows:

110.3.11 Termites. Building components and building surroundings required to be protected from termite damage in accordance with Section 1503.7, Section 2304.13 or Section 2304.11.6, specifically required to be inspected for termites in accordance with Section 2114, or required to have chemical soil treatment in accordance with Section 1816 shall not be covered or concealed until the release from the building official has been received. (Mod CA5093-R1 / AM)

Section 110 – Inspections

Add Section 110.3.12 to read as follows:

110.3.12 Impact resistant coverings or systems. Where impact resistant coverings or systems are installed to meet requirements of this code, the building official shall schedule adequate inspections of impact resistant coverings or systems to determine the following:

1. The system indicated on the plans was installed.

2. The system is installed in accordance with the manufacturer’s installation instructions and the product approval.

(Mod CA 5637 / AS)

Section 110 – Inspections

Change Section 110.4 to read as follows:

110.4 Inspection agencies. The building official is authorized to accept reports of approved inspection agencies, provided such agencies satisfy the requirements as to qualifications and reliability. Reserved.

(Mod CA5096-R1 / AM)

Section 110 – Inspections

Add Sections 110.7 – 110.8 to read as follows:

110.7 Shoring. For threshold buildings, shoring and associated formwork or falsework shall be designed and inspected by a Florida licensed professional engineer, employed by the permit holder or subcontractor, prior to any required mandatory inspections by the threshold building inspector.

110.8 Threshold building.

110.8.1 The enforcing agency shall require a special inspector to perform structural inspections on a threshold building pursuant to a structural inspection plan prepared by the engineer or architect of record. The structural inspection plan must be submitted to the enforcing agency prior to the issuance of a building permit for the construction of a threshold building. The purpose of the structural inspection plans is to provide specific inspection procedures and schedules so that the building can be adequately inspected for compliance with the permitted documents. The special inspector may not serve as a surrogate in carrying out the responsibilities of the building official, the architect, or the engineer of record. The contractor's contractual or statutory obligations are not relieved by any action of the special inspector.

110.8.2 The special inspector shall determine that a professional engineer who specializes in shoring design has inspected the shoring and reshoring for conformance with the shoring and reshoring plans submitted to the enforcing agency. A fee simple title owner of a building, which does not meet the minimum size, height, occupancy, occupancy classification, or number-of-stories criteria which would result in classification as a threshold building under s. 553.71(7), may designate such building as a threshold building, subject to more than the minimum number of inspections required by the Florida Building Code.

110.8.3 The fee owner of a threshold building shall select and pay all costs of employing a special inspector, but the special inspector shall be responsible to the enforcement agency. The inspector shall be a person certified, licensed or registered under Chapter 471, Florida Statutes, as an engineer or under Chapter 481, Florida Statutes, as an architect.

110.8.4 Each enforcement agency shall require that, on every threshold building:

110.8.4.1 The special inspector, upon completion of the building and prior to the issuance of a certificate of occupancy, file a signed and sealed statement with the enforcement agency in substantially the following form: “To the best of my knowledge and belief, the above described construction of all structural load-bearing components complies with the permitted documents, and the shoring and reshoring conforms to the shoring and reshoring plans submitted to the enforcement agency.”

110.8.4.2 Any proposal to install an alternate structural product or system to which building codes apply be submitted to the enforcement agency for review for compliance with the codes and made part of the enforcement agency’s recorded set of permit documents.

110.8.4.3 All shoring and reshoring procedures, plans and details be submitted to the enforcement agency for recordkeeping. Each shoring and reshoring installation shall be supervised, inspected and certified to be in compliance with the shoring documents by the contractor.

110.8.4.4 All plans for the building which are required to be signed and sealed by the architect or engineer of record contain a statement that, to the best of the architect’s or engineer’s knowledge, the plans and specifications comply with the applicable minimum building codes and the applicable fire-safety standards as determined by the local authority in accordance with this section and Chapter 633, Florida Statutes.

110.8.5 No enforcing agency may issue a building permit for construction of any threshold building except to a licensed general contractor, as defined in Section 489.105(3)(a), Florida Statutes, or to a licensed building contractor, as defined in Section 489.105(3)(b), Florida Statutes, within the scope of her or his license. The named contractor to whom the building permit is issued shall have the responsibility for supervision, direction, management and control of the construction activities on the project for which the building permit was issued.

110.8.6 The building department may allow a special inspector to conduct the minimum structural inspection of threshold buildings required by this code, Section 553.73, Florida Statutes, without duplicative inspection by the building department. The building official is responsible for ensuring that any person conducting inspections is qualified as a building inspector under Part XII of Chapter 468, Florida Statutes, or certified as a special inspector under Chapter 471 or 481, Florida Statutes. Inspections of threshold buildings required by Section 553.79(5), Florida Statutes, are in addition to the minimum inspections required by this code.

(Mod CA5093-R1 / AM)

Section 111 – Certificate of Occupancy

Change Section 111.2 to read as follows:

111.2 Certificate issued. After the building official inspects the building or structure and finds no violations of the provisions of this code or other laws that are enforced by the department of building safety, the building official shall issue a certificate of occupancy that contains the following:

1. The building permit number.

2. The address of the structure.

3. The name and address of the owner.

4. A description of that portion of the structure for which the certificate is issued.

5. A statement that the described portion of the structure has been inspected for compliance with the requirements of this code for the occupancy and division of occupancy and the use for which the proposed occupancy is classified.

6. For buildings and structures in flood hazard areas, a statement that documentation of the as-built lowest floor elevation has been provided and is retained in the records of the authority having jurisdiction department of building safety.

6. 7. The name of the building official.

7. 8. The edition of the code under which the permit was issued.

8. 9. The use and occupancy, in accordance with the provisions of Chapter 3.

9. 10. The type of construction as defined in Chapter 6.

10 11. The design occupant load.

11. 12. If an automatic sprinkler system is provided, whether the sprinkler system is required.

12. 13. Any special stipulations and conditions of the building permit.

(Mod SP5254 / AS)

Section 111 – Certificate of Occupancy

Add Section 111.5 to read as follows:

111.5 Certificate of Completion. A Certificate of Completion is proof that a structure or system is complete and for certain types of permits is released for use and may be connected to a utility system. This certificate does not grant authority to occupy a building, such as shell building, prior to the issuance of a Certificate of Occupancy.

(Mod CA5097-R1 / AM)

Section 113 – Board of Appeals

Change Section 113 to read as follows:

SECTION 113

BOARD OF APPEALS

RESERVED

113.1 General.  In order to hear and decide appeals of orders, decisions or determinations made by the building official relative to the application and interpretation of this code, there shall be and is hereby created a board of appeals. The board of appeals shall be appointed by the applicable governing authority and shall hold office at its pleasure. The board shall adopt rules of procedure for conducting its business. 

113.2 Limitations on authority. An application for appeal shall be based on a claim that the true intent of this code or the rules legally adopted thereunder have been incorrectly interpreted, the provisions of this code do not fully apply or an equally good or better form of construction is proposed. The board shall have no authority to waive requirements of this code. 

113.3 Qualifications. The board of appeals shall consist of members who are qualified by experience and training to pass on matters pertaining to building construction and are not employees of the jurisdiction.

(Mod CA5100-R1 / AM)

Section 114 – Violations

Change Section 114 to read as follows:

SECTION 114

VIOLATIONS

RESERVED

114.1 Unlawful acts. It shall be unlawful for any person, firm or corporation to erect, construct, alter, extend, repair, move, remove, demolish or occupy any building, structure or equipment regulated by this code, or cause same to be done, in conflict with or in violation of any of the provisions of this code. 

114.2 Notice of violation. The building official is authorized to serve a notice of violation or order on the person responsible for the erection, construction, alteration, extension, repair, moving, removal, demolition or occupancy of a building or structure in violation of the provisions of this code, or in violation of a permit or certificate issued under the provisions of this code. Such order shall direct the discontinuance of the illegal action or condition and the abatement of the violation.

114.3 Prosecution of violation. If the notice of violation is not complied with promptly, the building official is authorized to request the legal counsel of the jurisdiction to institute the appropriate proceeding at law or in equity to restrain, correct or abate such violation, or to require the removal or termination of the unlawful occupancy of the building or structure in violation of the provisions of this code or of the order or direction made pursuant thereto. 

114.4 Violation penalties. Any person who violates a provision of this code or fails to comply with any of the requirements thereof or who erects, constructs, alters or repairs a building or structure in violation of the approved construction documents or directive of the building official, or of a permit or certificate issued under the provisions of this code, shall be subject to penalties as prescribed by law.

(Mod CA5101-R1 / AM)

Section 116 – Unsafe Structures and Equipment

Change Section 116 to read as follows:

SECTION 116

UNSAFE STRUCTURES AND EQUIPMENT

RESERVED

116.1 Conditions. Structures or existing equipment that are or hereafter become unsafe, insanitary or deficient because of inadequate means of egress facilities, inadequate light and ventilation, or which constitute a fire hazard, or are otherwise dangerous to human life or the public welfare, or that involve illegal or improper occupancy or inadequate maintenance, shall be deemed an unsafe condition. Unsafe structures shall be taken down and removed or made safe, as the building official deems necessary and as provided for in this section. A vacant structure that is not secured against entry shall be deemed unsafe. 

116.2 Record. The building official shall cause a report to be filed on an unsafe condition. The report shall state the occupancy of the structure and the nature of the unsafe condition. 

116.3 Notice. If an unsafe condition is found, the building official shall serve on the owner, agent or person in control of the structure, a written notice that describes the condition deemed unsafe and specifies the required repairs or improvements to be made to abate the unsafe condition, or that requires the unsafe structure to be demolished within a stipulated time. Such notice shall require the person thus notified to declare immediately to the building official acceptance or rejection of the terms of the order. 

116.4 Method of service. Such notice shall be deemed properly served if a copy thereof is (a) delivered to the owner personally; (b) sent by certified or registered mail addressed to the owner at the last known address with the return receipt requested; or (c) delivered in any other manner as prescribed by local law. If the certified or registered letter is returned showing that the letter was not delivered, a copy thereof shall be posted in a conspicuous place in or about the structure affected by such notice. Service of such notice in the foregoing manner upon the owner’s agent or upon the person responsible for the structure shall constitute service of notice upon the owner.

116.5 Restoration. The structure or equipment determined to be unsafe by the building official is permitted to be restored to a safe condition. To the extent that repairs, alterations or additions are made or a change of occupancy occurs during the restoration of the structure, such repairs, alterations, additions or change of occupancy shall comply with the requirements of Section 105.2.2 and Chapter 34.

(Mod CA5103-R1 / AM)

Section 117 – Variances in Flood Hazard Areas

Add Section 117 to read as follows:

SECTION 117

VARIANCES IN FLOOD HAZARD AREAS

117.1 Flood hazard areas. Pursuant to section 553.73(5), F.S., the variance procedures adopted in the local floodplain management ordinance shall apply to requests submitted to the Building Official for variances to the provisions of Section 1612.4 of the Florida Building Code, Building or, as applicable, the provisions of R322 of the Florida Building Code, Residential. This section shall not apply to Section 3109 of the Florida Building Code, Building.

(Mod SP 5255 / AS)

Chapter 2 – Definitions

Section 202 – Definitions

Change Section 202 to read as follows:

ACCESSIBLE. A site, building, facility or portion thereof that complies with Chapter 11. See the Florida Building Code, Accessibility. (Mod A5104  / AM)

ACCESSIBLE ROUTE. A continuous, unobstructed path that complies with Chapter 11. See the Florida Building Code, Accessibility. (Mod A5104  / AM)

ACCESSIBLE UNIT. A dwelling unit or sleeping unit that complies with this code and the provisions for Accessible units in ICC A117.1. See the Florida Building Code, Accessibility. (Mod A5104  / AM)

ADDITION. An extension or increase in floor area, number of stories or height of a building or structure. (Mod F5191 / AS)

AGRICULTURAL, BUILDING. A structure designed and constructed to house farm implements, hay, grain, poultry, livestock or other horticultural products. This structure shall not be a place of human habitation or a place of employment where agricultural products are processed, treated or packaged, nor shall it be a place used by the public. Reserved (Mod CA5188 / AM)

APPLICABLE GOVERNING BODY. A city, county, state, state agency or other political government subdivision or entity authorized to administer and enforce the provisions of this code, as adopted or amended. Also applies to administrative authority. (Mod CA5188 / AM)

ARCHITECT. A Florida-registered architect. (Mod CA5188 / AM)

AWNING. An architectural projection that provides weather protection, identity or decoration and is partially or wholly supported by the building to which it is attached. An awning is comprised of a lightweight frame structure over which a covering is attached. An awning may be rigid fixed or moveable, cantilevered, or otherwise entirely supported from a building.

(Mod S5936 – R1 / AM)

BURIAL CHAMBER MAUSOLEUM. A family mausoleum consisting of 6 or fewer casket placement crypts plus a chamber to be used for loading of caskets from the interior of the mausoleum which is not below the level of the ground and which is substantially exposed above ground.  (Florida Specific Amendment)

CARBON DIOXIDE EXTINGUISHING SYSTEMS. A system supplying carbon dioxide (CO2) from a pressurized vessel through fixed pipes and nozzles. The system includes a manual- or automatic-actuating mechanism. See Section 902.1.  (Mod F5191 / AS)

CARBON MONOXIDE ALARM. A device for the purpose of detecting carbon monoxide, that produces a distinct audible alarm, and is listed or labeled with the appropriate standard, either ANSI/UL 2034 - 96, Standard for Single and Multiple Station CO Alarms, or UL 2075 - 04, Gas and Vapor Detector Sensor, in accordance with its application. (Mod F5191 / AS)

CHAPEL MAUSOLEUM. A mausoleum for the public that has heat or air conditioning, with or without a committal area or office. (Florida Specific Amendment)

CIRCULATION PATH. An exterior or interior way of passage from one place to another for pedestrians. See the Florida Building Code, Accessibility. (Mod A5104 / AM)

COASTAL HIGH HAZARD AREA FLOOD HAZARD AREA SUBJECT TO HIGH-VELOCITY WAVE ACTION. Area within the special flood hazard area extending from offshore to the inland limit of a primary frontal dune along an open coast and any other area that is subject to high-velocity wave action from storms or seismic sources, and shown on a Flood Insurance Rate Map (FIRM) or other flood hazard map as velocity zones Zone V, VO, VE or V1-30.  (Mod SP 5274 / AS)

COLUMBARIUM. A permanent structure consisting of niches. (Florida Specific Amendment)

COMMISSION. The Florida Building Commission. (Florida Specific Amendment)

COMPANION CRYPT. A permanent chamber in a mausoleum for the containment of human remains of more than one individual. (Florida Specific Amendment)

CRYPT. A permanent chamber in a mausoleum for the containment of human remains. (Florida Specific Amendment)

DETECTABLE WARNING.  See the Florida Building Code, Accessibility. (Mod A5104 / AM)

DRY FLOODPROOFING. A combination of design modifications that results in a building or structure, including the attendant utility utilities and equipment and sanitary facilities, being water tight with walls substantially impermeable to the passage of water and with structural components having the capacity to resist loads as identified in ASCE 7. (Mod SP5259 / AS)

DWELLING UNIT OR SLEEPING UNIT, TYPE A. Reserved. (Mod A5104 / AM)

DWELLING UNIT OR SLEEPING UNIT, TYPE B. Reserved.	(Mod A5104 / AM)

EMPLOYEE WORK AREA. All or any portion of a space used only by employees and only for work. Corridors, toilet rooms, kitchenettes and break rooms are not employee work areas. See the Florida Building Code, Accessibility. (Mod A5104 / AM)

ENFORCEMENT AGENCY.

Local enforcement agency. Means an agency of local government with authority to make inspections of buildings and to enforce the codes which establish standards for design, construction, erection, alteration, repair, modification or demolition of public or private buildings, structures or facilities.

State enforcement agency. Means the agency of state government with authority to make inspections of buildings and to enforce the codes, as required by this part, which establish standards for design, construction, erection, alteration, repair, modification or demolition of public or private buildings, structures or facilities. (Mod CA5188 / AM)

ENGINEER. A Florida-registered engineer. (Mod CA5188 / AM)

FAMILY MAUSOLEUM.  A mausoleum for the private use of a family or group of family members. (Florida Specific Amendment)

FLOATING RESIDENTIAL UNIT. Means a structure primarily designed or constructed as a living unit, built on a floating base, which is not designed primarily as a vessel, is not self-propelled although it may be towed about from place to place, and is primarily intended to be anchored or otherwise moored in a fixed location. (Mod CA5188 / AM)

GARAGE DOOR MANUFACTURER: The party responsible for the completed assembly of the garage door components.  (Mod S5324 / AS)

GARDEN MAUSOLEUM. A mausoleum for the public built without heat or air conditioning but may contain an open-air committal area. (Florida Specific Amendment)

HABITABLE SPACE. A space in a building  structure for living, sleeping, eating or cooking. Bathrooms, toilet rooms, closets, halls, screen enclosures, sunroom Categories I, II and III as defined in the AAMA/NPEA/NSA 2100, storage or utility spaces and similar areas are not considered habitable spaces. (Mod CA5725 / AM) (Mod CA5188 / AM)

HEIGHT, THRESHOLD BUILDING. The height of the building is at the mean distance between the eaves and the ridge of the roofing structure. If the distance from grade to the line which is the mean distance between the eaves and the ridge of the roofing structure is more than 50 feet, the building is to be considered a "threshold building" within the contemplation of the Threshold Building Act. (Mod CA 5188 / AM)

HIGH VELOCITY HURRICANE ZONE. This zone consists of Broward and Dade counties. (Florida Specific Amendment)

HISTORIC BUILDINGS. Buildings that are listed in or eligible for listing in the National Register of Historic Places, or designated as historic under an appropriate state or local law (see Chapter 12 of the Florida Existing Building Code). (Mod CA 5188 / AM)

LANDSCAPE ARCHITECT. A Florida-registered landscape architect. (Mod CA 5188 / AM)

LOCAL FLOODPLAIN MANAGEMENT ORDINANCE. An ordinance or regulation adopted pursuant to the requirements in Title 44 Code of Federal Regulations, Parts 59 and 60 for participation in the National Flood Insurance Program. (Mod SP5259 / AS)

LOWEST FLOOR. The lowest floor of the lowest enclosed area, including basement, but excluding any unfinished or flood-resistant enclosure, usable solely for vehicle parking, building access or limited storage provided that such enclosure is not built so as to render the structure in violation of this section. 1612. (Mod SP5259 / AS)

MATERIAL CODE VIOLATION. A material code violation is a violation that exists within a completed building, structure or facility which may reasonably result, or has resulted, in physical harm to a person or significant damage to the performance of a building or its systems. (Mod CA5188 / AM)

MATERIAL VIOLATION. As defined in Florida Statutes. (Mod CA5188 / AM)

MAUSOLEUM. A permanent structure or building which is substantially exposed above the ground and is intended for the interment, entombment, or inurnment of human remains. (Florida Specific Amendment)

MEANS OF ESCAPE. As used in Section 1008.1.4.5, a way out of a building or structure that does not conform to the strict definition of means of egress but does provide an alternate way out. A means of escape consists of a door, stairway, passage or hall providing a way of unobstructed travel to the outside at street or ground level. It may also consist of a passage through an adjacent non-lockable space, independent of and remotely located from the means of egress, to any approved exit. (Mod F5716-R1 / AM)

NICHE.  A permanent chamber in a columbarium or mausoleum to hold the cremated remains of one or more individuals.

NON-VISITATION CRYPT MAUSOLEUM. A mausoleum for the public where the crypts are not accessible to the public. (Florida Specific Amendment)

PLANS. All construction drawings and specifications for any structure necessary for the building official to review in order to determine whether a proposed structure, addition or renovation will meet the requirements of this code and other applicable codes. (Mod CA5188 / AM)

REGISTERED TERMITICIDE.  Product listed as registered for use as a preventative treatment for termites for new construction by the Florida Department of Agriculture and Consumer Services under authority of Chapter 487, Florida Statutes. (Florida Specific Amendment)

SCREEN ENCLOSURE. A building or part thereof, in whole or in part self-supporting, and having walls of insect screening with or without removable vinyl or acrylic wind break panels and a roof of insect screening, plastic, aluminum or similar lightweight material, or other materials and assemblies such as a patio or deck roof of a structure. (Mod S5726 / AS)

SEPARATE ATMOSPHERE. The atmosphere that exists between rooms, spaces, or areas that are separated by an approved smoke barrier. (Mod F5191 / AS)

SKYLIGHTS AND SLOPED GLAZING. Glass or other transparent or translucent glazing material installed at a slope of 15 degrees (0.26 rad) or more from vertical. Glazing material in skylights, including unit skylights, tubular daylighting devices, solariums, sunrooms, roofs and sloped walls, are included in this definition.   (S5633 AS). (S5635 AS) (S5636-R1 / AM)

SPECIAL INSPECTION. Reserved. Inspection of construction requiring the expertise of an approved special inspector in order to ensure compliance with this code and the approved construction documents.

Continuous Special Inspection. Special inspection by the special inspector who is present when and where the work to be inspected is being performed.

Periodic Special Inspection. Special inspection by the special inspector who is intermittently present where the work to be inspected has been or is being performed. (Mod CA5188 / AM) (Mod S5149 / AM)

SPECIAL INSPECTOR. Reserved. A qualified person employed or retained by an approved agency and approved by the building official as having the competence necessary to inspect a particular type of construction requiring special inspection. (Mod S5149 / AM)

STATE ENFORCEMENT AGENCY. Means the agency of state government with authority to make inspections of buildings and to enforce the codes, as required by this part, which establish standards for design, construction, erection, alteration, repair, modification or demolition of public or private buildings, structures or facilities. (Florida Specific Amendment)

STRUCTURAL DETERMINATION. For purposes of this code, "structural“ shall mean any part, material or assembly of a building or structure which affects the safety of such building or structure and/or which supports any dead or designed live load and the removal of which part, material or assembly could cause, or be expected to cause, all or any portion to collapse or fail. (Mod CA5188 / AM)

STRUCTURAL OBSERVATION. Reserved. The visual observation of the structural system by a registered design professional for general conformance to the approved construction documents. Structural observation does not include or waive the responsibility for the inspection required by Section 110, 1705 or other sections of this code. (Mod CA5188 / AM) (Mod S5149 / AM)

SUBSTANTIAL IMPROVEMENT. Any repair, reconstruction, rehabilitation, alteration, addition or other improvement of a building or structure, the cost of which equals or exceeds 50 percent of the market value of the structure before the improvement or repair is started. If the structure has sustained substantial damage, any repairs are considered substantial improvement regardless of the actual repair work performed. The term does not, however, include either:

1. Any project for improvement of a building required to correct existing health, sanitary or safety code violations identified by the building official and that are is the minimum necessary to assure safe living conditions.

2. Any alteration of a historic structure provided that the alteration will not preclude the structure’s continued designation as a historic structure.  (Mod SP5259 / AS)

SUNROOM.

1. A one-story structure attached to a building with a glazing area in excess of 40 percent 	of the gross area of the structure’s exterior walls and roof.

2. A one-story structure added to a dwelling with solid roof panels without sloped 	glazing. The sunroom walls may have any configuration, provided the open areas with 	operable or fixed glass or windows or side hinged or sliding glass doors of the longer 	wall and one additional wall is equal to at least 65 percent of the area below 6 foot 8 	inches (2032 mm) of each wall, measured from the floor. For the purposes of this code 	the term sunroom as used herein shall include conservatories, sunspaces, solariums, and 	porch or patio covers or enclosures. (Mod S5727 / AS)

TECHNICALLY INFEASIBLE. An alteration of a building or a facility that has little likelihood of being accomplished because the existing structural conditions require the removal or alteration of a load-bearing member that is an essential part of the structural frame, or because other existing physical or site constraints prohibit modification or addition of elements, spaces or features which are in full and strict compliance with the minimum requirements for new construction and which are necessary to provide accessibility. See the Florida Building Code, Accessibility. (Mod A5104 / AM)

THRESHOLD BUILDING. In accordance with Florida Statute, any building which is greater than 3 stories or 50 feet in height, or which has an assembly occupancy classification that exceeds 5,000 square feet in area and an occupant content of greater than 500 persons. (Mod CA5188 / AM)

TOWNHOUSE. A single-family dwelling unit constructed in a group of three or more attached units with property lines separating each unit in which each unit extends from foundation to roof and with open space on at least two sides. (Mod F5191 / AS)

VALUE. The estimated current replacement cost of the building in kind. (Mod CA5188 / AM)

WHEELCHAIR SPACE. A space for a single wheelchair and its occupant. See the Florida Building Code, Accessibility. (Mod A5104-R1 / AM)

Chapter 3 – Use and Occupancy Classification

Florida Specific Amendment

Section 304 – Business Group B

Add Section 304 to read as shown:

304.3 Public and private colleges and universities shall comply with Section 468.

304.4 Florida colleges shall comply with Section 453.

Florida Specific Amendment

Section 305 – Educational Group E

Add Section 305 to read as shown:

305.3 Public and private educational occupancies shall comply with Section 443.

305.4 Public education occupancies shall comply with Section 453.

Section 307 – High-hazard Group H

Change Section 307.1 to read as shown:

307.1 High-hazard Group H. High-hazard Group H occupancy includes, among others, the use of a building or structure, or a portion thereof, that involves the manufacturing, processing, generation or storage of materials that constitute a physical or health hazard in quantities in excess of those allowed in control areas complying with Section 414, based on the maximum allowable quantity limits for control areas set forth in Tables 307.1(1) and 307.1(2). Hazardous occupancies are classified in Groups H-1, H-2, H-3, H-4 and H-5 and shall be in accordance with this section, the requirements of Section 415 and the International Fire Code Florida Fire Prevention Code. Hazardous materials stored, or used on top of roofs or canopies shall be classified as outdoor storage or use and shall comply with the International Fire Code Florida Fire Prevention Code.

Exceptions: The following shall not be classified in Group H, but shall be classified in the occupancy that they most nearly resemble:

1. – 13. (No Change)

14.    Mercantile occupancies offering for retail sale sparklers, novelties and trick noisemakers as defined at Section 791.01, Florida Statutes, and that are not defined as fireworks by Chapter 791, Florida Statutes. Storage of sparklers and other novelties or trick noisemakers as defined in Chapter 791, Florida Statutes, within mercantile occupancies shall be in accordance with Section 791.055, Florida Statutes.

(Mod F5105 / AS)

Chapter 4 – Special Detailed Requirements Based on Use and Occupancy

(See Attached Chapter 4 changes)

Chapter 5 – General Building Heights and Areas

Section 505 – Mezzanines and Equipment Platforms

Change Section 505.2.1 to read as follows:

505.2.1 Area limitation. (No Change)

Exceptions:

1. – 2.  (No Change)

3.    In sprinklered Group S2 occupancies of Type III construction, the enclosed and unenclosed areas under mezzanines shall be allowed to be included when calculating the permissible size of mezzanines.

(Mod F5106 / AS)

Florida Specific Amendment

Section 507 – Group E Buildings

Change Section 507.10 to read as shown:

507. 10 Group E buildings.  The area of a Group E building no more than one story above grade plane, of Type II, IIIA or IV construction, shall not be limited provided all of the following criteria are met:

1.	Each classroom shall have not less than two means of egress, with one of the means of egress being a direct exit to the outside of the building complying with Section 1020 or the building is provided with smoke barriers having a minimum 1-hour fire-resistance rating dividing the building into areas not to exceed 30,000 square feet (2,787 m2) in floor area.

2. – 3. (No change)

Section 510 – Special Provisions

Change Section 510.4 to read as follows:

510.4 Parking beneath Group R.  Where a maximum one-story above grade plane Group S-2 parking garage, enclosed or open, or combination thereof, of Type I construction or open of Type IV construction, with grade entrance, is provided under a building of Group R, the number of stories to be used in determining the minimum type of construction shall be measured from the floor above such a parking area. The number of stories to be used in determining the height in stories in accordance with Section 903.2.11.3 903.6 shall include the parking garage as a story. The floor assembly between the parking garage and the Group R above shall comply with the type of construction required for the parking garage and shall also provide a fire-resistance rating not less than the mixed occupancy separation required in Section 508.4.

(Mod F5107 / AS)

Chapter 6 – Types of Construction

(No Change)

Chapter 7 – Fire and Smoke Protection Features

Section 706 – Fire Walls

Add Section 706.4.1 to read as follows:

706.4.1 Townhouse fire separation.

706.4.1.1   Each townhouse shall be considered a separate building and shall be separated from adjoining townhouses by a party wall complying with Section 706.1.1 or by the use of separate exterior walls meeting the requirements of Tables 601 and 602 for zero clearance from property lines as required for the type of construction. Separate exterior walls shall include one of the following:

1. A parapet not less than 18 inches (457 mm) above the roof line.

2. Roof sheathing of noncombustible material or fire retardant treated wood, for not less than a 4 foot (1219 mm) width on each side of the exterior dividing wall.

3. One layer of 5/8 inch (15.9 mm) Type X gypsum board attached to the underside of roof decking, for not less than a 4 foot (1219 mm) width on each side of the exterior dividing wall.

706.4.1.2   When not more than three stories in height, townhouses may be separated by a single wall meeting the following requirements:

1. Such wall shall provide not less than a 2-hour fire-resistance rating. Plumbing, piping, ducts, electrical or other building services shall not be installed within or through the 2-hour wall, unless such materials and methods of penetration have been tested in accordance with Section 703.

2. Such wall shall be continuous from the foundation to the underside of  no less than a 4-foot (1219 mm) width on each side of the wall shall be of noncombustible material, or fire-retardant-treated wood, or one layer of 5/8-inch (15.9 mm) Type X gypsum wallboard attached to the underside of the roof decking.

3. Each dwelling unit sharing such wall shall be designed and constructed to maintain its structural integrity independent of the unit on the opposite side of the wall.

Exception: Said wall may be penetrated by roof and floor structural members provided that the fire-resistance rating and the structural integrity of the wall is maintained.

(Mod F5108 / AS)

Section 708 – Fire Partitions

Change Section 708.3 to read as follows:

708.3 Fire resistance rating. Fire partitions shall have a fire-resistance rating of not less than 1 hour.

Exceptions:

1. – 2. (No Change)

3. In mini-warehouses/self-storage buildings, walls used to separate tenants shall not be required to have fire-resistance rating, provided a sprinkler system meeting the requirements of Ordinary Hazard Group II as defined by NFPA 13, is installed employing quick response heads.

(Mod F5109 / AS)

Chapter 8 – Interior Finishes

(No Change)

Chapter 9 – Fire Protection Systems

Section 901 - General

Change Section 901.1 to read as follows:

901.1 Scope. The provisions of this chapter shall specify where fire protection systems are required and shall apply to the design, installation and operation of fire protection systems and carbon monoxide detection alarms.

(Mod F5110 / AS)

Florida Specific Amendment

Section 903 – Automatic Sprinkler Systems

Change Section 903.2.3 to read as shown:

903.2.3 Group E.  An automatic sprinkler system shall be provided for Group E occupancies as follows:

1.– 2. (No change)

Exception: An automatic fire sprinkler system is not required in any area below the lowest level of exit discharge serving that area where every classroom throughout the building has at least one exterior exit door at ground level. existing educational buildings unless 50 percent of the aggregate area of the building is being remodeled.

Section 903 – Automatic Sprinkler Systems

Change Section 903.2.11.3 to read as follows:

903.2.11.3 Buildings over 55 feet in height. Buildings three stories or more in height. An automatic sprinkler system shall be installed throughout buildings with a floor level having an occupant load of 30 or more that is located 55 feet (16 764 mm) or more above the lowest level of fire department vehicle access. Any building which is of three stories or more in height shall be equipped with an approved automatic sprinkler system installed in accordance with Section 903.1.

Exceptions:

1. Airport control towers. Single- and two-family dwellings.

2. Open parking structures. A stand-alone parking garage constructed with noncombustible materials, the design of which is such that all levels of the garage are uniformly open to the atmosphere on all sides with the percentages of openings equal to or greater than those specified in Section 406.3. Such garages shall be separated from any other structure by not less than 20 feet (6096 mm). A stand-alone parking garage is one that is solely for the parking of vehicles and does not have any other occupancy group in the building.

3. Occupancies in Group F-2. Telecommunication spaces located within telecommunication buildings, if the spaces are equipped to meet an equivalent fire prevention standard approved by both the Florida Building Commission and the State Fire Marshal.

4. Telecommunications spaces within telecommunication buildings, if the telecommunications space is equipped with:

4.1. Air sampling smoke detection.

4.2. Remote, proprietary or central station fire alarm monitoring.

4.3. Automatic smoke exhaust system.

4.4. One-hour fire-resistance wall separating the telecommunications space from the adjacent areas on the same floor.

4.5. Two-hour floor/ceiling assembly separating the telecommunications space from adjacent floors.

4.6. All other portions ancillary to the telecommunications equipment area shall be provided with fire sprinkler protection.

5. Sprinkler systems installed solely as a requirement of Section 903.62.11.3 may be a NFPA 13R or NFPA 13D system in accordance with their scopes.

903.2.11.3.1 NFPA 101 as adopted by Florida Fire Prevention Code, as regarding the requirements for fire protection sprinklers, is applicable to all multiple-family residential buildings, whether designated as townhouses, condominiums, apartment houses, tenements, garden apartments or by any other name. The attorney general has determined that for the purpose of the fire protection sprinkler requirements in Section 553.895(2), Florida Statutes, townhouses that are three or more stories tall and consist of three or more units together are multiple-family dwellings. Therefore, these types of townhouses are not exempt from being considered for the requirements to provide fire protection sprinklers (even if there are any other definitions that define a townhouse as a single-family residence). When determining whether townhouses require fire protection sprinkler systems, the building official must consider in parallel: (a) the attorney general’s opinion defining the statutory language for townhouses; (b) the building code requirements, including all life-safety chapters, that provide additional determining criteria, such as construction types, fire-resistance, fire protection systems and egress; and (c) the NFPA 101 as adopted by Florida Fire Prevention Code, egress and protection determining criteria. The more restrictive criteria are then applied.

(Mod F5111 / AS)

Section 907 – Fire Alarm and Detection Systems

Add Sections 907.1.4 and 907.9 to read as follows:

907.1.4 Accessibility. Every required fire alarm system shall include a visible alarm indicating appliances in public and common areas. For more specific accessibility requirements related to alarm indicating appliances, refer to Section 11-4.28. applicable sections of the Florida Building Code, Accessibility

Add Section 907.9 to read as follows:

907.9 Accessibility. Alarm systems required to be accessible shall comply with the applicable sections of the Florida Building Code, Accessibility

(Mod A5112 / AS)

Section 908 – Carbon Monoxide Protection

Add Section 908.7 to read as follows:

908.7 Carbon monoxide alarms. Group I or R occupancies located in a building containing a fuel-burning appliance or in a building which has an attached garage shall be equipped with single-station carbon monoxide alarms. The carbon monoxide alarms shall be listed as complying with UL 2034 and be installed and maintained in accordance with NFPA 720 and the manufacturer’s instructions. An open parking garage, as defined in Chapter 2, or an enclosed parking garage ventilated in accordance with Section 404 of the International Mechanical Code shall not be considered an attached garage.  Carbon monoxide protection. Every separate building or an addition to an existing building for which a permit for new construction is issued and having a fossil-fuel-burning heater or appliance, a fireplace, an attached garage, or other feature, fixture, or element that emits carbon monoxide as a byproduct of combustion shall have an operational carbon monoxide alarm installed within 10 feet of each room used for sleeping purposes in the new building or addition, or at such other locations as required by this Code.

Exception: Sleeping units or dwelling units which do not themselves contain a fuel-burning appliance or have an attached garage, but which are located in a building with a fuel-burning appliance or an attached garage, need not be equipped with single-station carbon monoxide alarms provided that:

1. The sleeping unit or dwelling unit is located more than one story above or below any story which contains a fuel-burning appliance or an attached garage;

2. The sleeping unit or dwelling unit is not connected by duct work or ventilation shafts to any room containing a fuel-burning appliance or to an attached garage; and

3. The building is equipped with a common area carbon monoxide alarm system.

908.7.1 Carbon monoxide detection systems. Carbon monoxide detection systems, which include carbon monoxide detectors and audible notification appliances, installed and maintained in accordance with this section for carbon monoxide alarms and NFPA 720 shall be permitted. The carbon monoxide detectors shall be listed as complying with UL 2075. 916.1.1  Carbon monoxide alarm. The requirements of Section 908.7 shall be satisfied by providing for one of the following alarm installations:

1. A hard-wired carbon monoxide alarm.

2. A battery-powered carbon monoxide alarm.

3. A hard-wired combination carbon monoxide and smoke alarm.

4. A battery-powered combination carbon monoxide and smoke alarm.

908.7.2  Combination alarms. Combination smoke/carbon monoxide alarms shall be listed and labeled by a Nationally Recognized Testing Laboratory.

Exceptions:

1. An approved operational carbon monoxide detector shall be installed inside or directly outside of each room or area within a hospital, inpatient hospice facility or nursing home facility licensed by the Agency for Health Care Administration, or a new state correctional institution where a fossil-fuel burning heater, engine, or appliance is located. The carbon monoxide detector shall be connected to the fire-alarm system of the hospital, inpatient hospice facility, or nursing home facility as a supervisory signal.

2. This section shall not apply to existing buildings that are undergoing alterations or repair unless the alteration is an addition as defined in Section 908.7.3 916.1.3.

908.7.3  Addition shall mean an extension or increase in floor area, number of stories or height of a building or structure.

(Mod F5113-R1 / AM)

Chapter 10 – Means of Egress

Section 1002 - Definitions

Change Section 1002.1 to add definition as follows:

1002.1 Definitions. The following terms are defined in Chapter 2:

Means of Escape

(Mod F5638 / AS)

Section 1003 – General Means of Egress

Add Section 1003.5.1 to read as follows:

1003.5.1 Accessibility. For accessibility provisions related to changes in levels, see the Florida Building Code, Accessibility.

(Mod A5114 / AS)

Section 1007 – Accessible Means of Egress

Change Section 1007.1 to read as shown:

1007.1 Accessible means of egress required. Accessible means of egress shall be provided in accordance with the applicable sections of the Florida Building Code, Accessibility. comply with this section. Accessible spaces shall be provided with not less than one accessible means of egress. Where more than one means of egress are required by Section 1015.1 or 1021.1 from any accessible space, each accessible portion of the space shall be served by not less than two accessible means of egress. 

Exceptions:

1. Accessible means of egress are not required in alterations to existing buildings.

2. One accessible means of egress is required from an accessible mezzanine level in accordance with Section 1007.3, 1007.4 or 1007.5.

3. In assembly areas with sloped or stepped aisles, one accessible means of egress is permitted where the common path of travel is accessible and meets the requirements in Section 1028.8.

Change Section 1007.2 to read as shown:

1007.2 Continuity and components.  Reserved.

Change Section 1007.3 to read as shown:

1007.3 Stairways. Reserved.

Change Section 1007.4 to read as shown:

1007.4 Elevators.  Reserved.

Change Section 1007.5 to read as shown:

1007.5 Platform lifts. Reserved.

Change Section 1007.6 to read as shown:

1007.6 Areas of refuge.  Reserved.

Change Section 1007.7 to read as shown:

1007.7 Exterior area for assisted rescue.  Reserved.

Change Section 1007.8 to read as shown:

1007.8 Two-way communication. Reserved.

Change Section 1007.9 to read as shown:

1007.9 Signage. Reserved.

Change Section 1007.10 to read as shown:

1007.10 Directional signage. Reserved.

Change Section 1007.11 to read as shown:

1007.11 Instructions. Reserved.

(Mod A5115 / AS)

Section 1008 – Doors, Gates and Turnstiles

Change Section 1008.1 to read as shown:

1008.1 Doors. Means of egress doors shall meet the requirements of this section. Doors serving a means of egress system shall meet the requirements of this section and Section 1020.2. Doors provided for egress purposes in numbers greater than required by this code shall meet the requirements of this section. For accessibility provisions related to doors, refer to the Florida Building Code, Accessibility.

Means of egress doors shall be readily distinguishable from the adjacent construction and finishes such that the doors are easily recognizable as doors. Mirrors or similar reflecting materials shall not be used on means of egress doors. Means of egress doors shall not be concealed by curtains, drapes, decorations or similar materials.

(Mod A5117 / AS)

Section 1008 – Doors, Gates and Turnstiles

Change Section 1008.1.1 to read as shown:

1008.1.1 Size of doors. (No change to main body of text)

Exceptions:

1. – 6. (No change)

7.  In other than Group R-1 occupancies, the minimum widths shall not apply to interior egress doors within a dwelling unit or sleeping unit that is not required to be an Accessible unit, Type A unit or Type B unit.

8. Door openings required to be accessible within Type B units shall have a minimum clear width of 31.75 inches (806 mm).Buildings that are 400 square feet or less and that are intended for use in conjunction with one- and two-family residences are not subject to the door height and width requirements of this code.

(Mod SP5120 / AS)

Section 1008 – Doors, Gates and Turnstiles

Add Section 1008.1.4.5 to read as shown:

1008.1.4.5 Protection devices for emergency escape and rescue openings. The temporary installation or closure of storm shutters, panels and other approved hurricane protection devices shall be permitted on emergency escape and rescue openings in Group R occupancies during the threat of a storm. Such devices shall not be required to comply with the operational constraints of Section 1029.4. While such protection is provided, at least one means of escape from the dwelling or dwelling unit shall be provided. The means of escape shall be within the first floor of the dwelling or dwelling unit and shall not be located within a garage without a side hinged door leading directly to the exterior. Occupants in any part of the dwelling or dwelling unit shall be able to access the means of escape without passing through a lockable door not under their control.

(Mod F5640 / AS)

Section 1008 – Doors, Gates and Turnstiles

Change Section 1008.1.7 to read as shown:

1008.1.7 Thresholds. Thresholds at doorways shall not exceed 3/4 inch (19.1 mm) in height above the finished floor or landing for sliding doors serving dwelling units or 1/2 inch (12.7 mm) above the finished floor or landing for other doors. Raised thresholds and floor level changes greater than 1/4 inch (6.4 mm) at doorways shall be beveled with a slope not greater than one unit vertical in two units horizontal (50-percent slope). 

	Exceptions: In occupancy Group R-2 or R-3, threshold heights for sliding and side-	hinged exterior doors shall be permitted to be up to 73/4 inches (197 mm) in height if all 	of the following apply:

1. The door is not part of the required means of egress. The threshold height shall be 	limited to 73/4 inches (197 mm) where the occupancy is Group R-2; the door is an 	exterior door that is not a component of the required means of egress and the doorway is 	not on an accessible route. In one- and two-family dwellings where the door discharges to 	the outside or to an exterior balcony or exterior exit access, the floor level outside the 	door shall be permitted to be one step lower than the inside, but not more than 8 inches 	(203 mm) lower.

2. The door is not part of an accessible route as required by Chapter 11. For exterior 	doors serving dwelling units, thresholds at doorways shall not exceed the height required 	to pass the water resistance test of ANSI/AAMA/WDMA 101/I.S.2, or TAS 202 for high-	velocity hurricane zones, or the maximum allowable height difference between interior 	floor levels. Exterior floor level shall comply with the following:

| LEVEL DIFFERENCE (inches) | AT PRIMARY DOOR |
| --- | --- |
| 0 | Pervious construction (e.g., wood decking with spaces) |
| 1/2 | Impervious construction (e.g., concrete, brick or flag stone) |
| LEVEL DIFFERENCE (inches) | AT SECONDARY DOOR |
| 1/2 | Pervious construction |
| 4 | Impervious construction |

3. The door is not part of an Accessible unit, Type A unit or Type B unit.

(Mod F5719 – R1 / AM)

Section 1009 – Stairways

Change Section 1009.1 to read as follows:

1009.9.1 Stairway walking surface. The walking surface of treads and landings of a stairway shall not be sloped steeper than one unit vertical in 48 units horizontal (2-percent slope) in any direction. Stairway treads and landings shall have a solid surface. Finish floor surfaces shall be securely attached.

Exceptions:

(1-2 No change)

3. See also the Florida Building Code, Accessibility.

(Mod A5126 / AS)

Section 1009 – Stairways

Add Section 1009.18 to read as shown:

1009.18 Accessible stairs. Stairs required to be accessible shall comply with the Florida Building Code, Accessibility.

(Mod A5127 / AS)

Section 1010 – Ramps

Change Section 1010.1 to read as shown:

1010.1 Scope. The provisions of this section shall apply to ramps used as a component of a means of egress.

1010.1 Exceptions:

1. Other than ramps that are parts of accessible routes providing access in accordance with Sections 1108.2 through 1108.2.4 and 1108.2.6 the provisions of the Florida Building Code, Accessibility, ramped aisles within assembly rooms or spaces shall conform to the provisions in 1028.11

2. Curb ramps not subject to Florida Building Code, Accessibility, shall comply with ICC ANSI A117.1.

3. Vehicle ramps in parking garages for pedestrian exit access shall not be required to comply with Sections 1010.4 through 1010.10 the provisions of the Florida Building Code, Accessibility when they are not an accessible route serving accessible parking spaces, other required accessible elements, or part of an accessible means of egress.

(Mod A5128-R1 / AM)

Section 1010 – Ramps

Change Section 1010.4 to read as shown:

1010.3 4 Cross slope. The slope measured perpendicular to the direction of travel of a ramp shall not be steeper than one unit vertical in 48 units horizontal (2-percent slope).

Exception: See also the Florida Building Code, Accessibility.

(Mod A5129 / AS)

Section 1010 – Ramps

Change Section 1010.7 to read as shown:

1010.7 Landings. Ramps shall have landings at the bottom and top of each ramp, points of turning, entrance, exits, and at doors and in accordance with the Florida Building Code, Accessibility. Landings shall comply with Sections 1010.67.1 through 1010.7.5.

Change Section 1010.7.1 to read as shown:

1010.7.1 Slope. Landings shall have a slope not steeper than one unit vertical in 48 units horizontal (2-percent slope) in any direction. Changes in level are not permitted.

Exception: see also the Florida Building Code, Accessibility.

Change Section 1010.7.3 to read as shown:

1010.7.3 Length. The landing length shall be 60 inches (1525 mm) minimum.

Exceptions:

1. In Group R-2 and R-3 individual dwelling and sleeping units that are not required to be Accessible units, Type A units or Type B units in accordance with Section 1107 landings are permitted to be 36 inches (914 mm) minimum.

2.  (No change)

3. Accessible landings shall comply with the Florida Building Code, Accessibility.

(Mod A5130 / AS)

Section 1010 – Ramps

Change Section 1010.10 to read as shown:

1010.10 Edge protection. Edge protection complying with Sections 1010.10.1 or 1010.109.2 shall be provided on each side of ramp runs and at each side of ramp landings.

Exceptions:

1.      Edge protection is not required on ramps not required to have handrails, provided they have flared sides that comply with the ICC A117.1 curb ramp provisions of the Florida Building Code, Accessibility.

2 – 4 No change.

(Mod A5132 / AS)

Section 1012 – Handrails

Change Section 1012.3 to read as shown:

1012.3 Handrail graspability. All required handrails shall comply with Section 1012.3.1 or shall provide equivalent graspability.

Exceptions:

1. In Group R-3 occupancies; within dwelling units in Group R-2 occupancies; and in Group U occupancies that are accessory to a Group R-3 occupancy or accessory to individual dwelling units in Group R-2 occupancies; handrails shall be Type I in accordance with Section 1012.3.1, Type II in accordance with Section 1012.3.2 or shall provide equivalent graspability.

2. Accessible handrails shall meet the requirements of the Florida Building Code, Accessibility.

(Mod A5133 / AS)

Section 1012 – Handrails

Change Section 1012.6 to read as shown:

1012.6 Handrail extensions. Handrails shall return to a wall, guard or the walking surface or shall be continuous to the handrail of an adjacent stair flight or ramp run. Where handrails are not continuous between flights, the handrails shall extend horizontally at least 12 inches (305 mm) beyond the top riser and continue to slope for the depth of one tread beyond the bottom riser. At ramps where handrails are not continuous between runs, the handrails shall extend horizontally above the landing 12 inches (305 mm) minimum beyond the top and bottom of ramp runs. The extensions of handrails shall be in the same direction of the stair flights at stairways and the ramp runs at ramps.

Exceptions:

1. – 3. (No change)

4. Accessible handrail extensions shall be as per the Florida Building Code, Accessibility.

(Mod A5134 / AS)

Section 1015 - Exit and Exit Access Doorways

Change Section 1015.1 to read as shown:

1015.1 Exits or exit access doorways from spaces. Two exits or exit access doorways from any space shall be provided where one of the following conditions exists:

1. The occupant load of the space exceeds one of the values in Table 1015.1.

Exceptions:

1. In Group R-2 and R-3 occupancies, one means of egress is permitted within and from individual dwelling units with a maximum occupant load of 20 where the dwelling unit is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2.  Reserved

2. Care suites in Group I-2 occupancies complying with Section 407.4.3.

2. The common path of egress travel exceeds one of the limitations of Section 1014.3.

3. Where required by Section 1015.3, 1015.4, 1015.5, or 1015.6. 

Where a building contains mixed occupancies, each individual occupancy shall comply with the applicable requirements for that occupancy. Where applicable, cumulative occupant loads from adjacent occupancies shall be considered in accordance with the provisions of Section 1004.1.

TABLE 1015.1

SPACES WITH ONE EXIT OR EXIT ACCESS DOORWAY

| OCCUPANCY | MAXIMUM OCCUPANT LOAD |
| --- | --- |
| A,B, E,F,M,U, R2, R3 | 49 |
| H-1,H-2,H-3 | 3 |
| H-4, H-5, I-1, I-3, I-4, R R-1, R-4 | 10 |
| S | 29 |

Change Section 1015.2.1 to read as shown:

1015.2.1 Two exits or exit access doorways.  (No Change)

.Exceptions:

1. – 2. ( No change.)

3.  In Group R1 and R2 occupancies, the distance between exits is not applicable to common nonlooped exit access corridors in a building that has corridor doors from the guestroom or guest suite or dwelling unit, which are arranged so that the exits are located in opposite directions from such doors.

(Mod A5985-R1  / AM)

Section 1029 – Emergency Escape and Rescue

Change Section 1029.1 to read as shown:

1029.1 General. In addition to the means of egress required by this chapter, provisions shall be made for emergency escape and rescue openings in Group R-2 occupancies in accordance with Tables 1021.2(1) and 1021.2(2) and Group R-3 occupancies. Basements and sleeping rooms below the fourth story above grade plane shall have at least one exterior emergency escape and rescue opening in accordance with this section. Where basements contain one or more sleeping rooms, emergency escape and rescue openings shall be required in each sleeping room, but shall not be required in adjoining areas of the basement. Such openings shall open directly into a public way or to a yard or court that opens to a public way.

Exceptions:

- Basements with a ceiling height of less than 80 inches (2032 mm) shall not be required to have emergency escape and rescue openings.

- Emergency escape and rescue openings are not required from basements or sleeping rooms that have an exit door or exit access door that opens directly into a public way or to a yard, court or exterior exit balcony that opens to a public way.

- Basements without habitable spaces and having no more than 200 square feet (18.6 m2) in floor area shall not be required to have emergency escape and rescue openings.

4. Security and hurricane devices installed in accordance with Section 1008.1.4.5.

(Mod A5796 / AS)

Chapter 11 – Accessibility

Florida Specific Amendment

Section 1101 – General

Change Section 1101.1 to read as shown:

1101.1 Scope. The provisions of this chapter shall control the design and construction of facilities for accessibility to physically disabled persons. This chapter governs the design and construction of buildings for accessibility.

1101.1.1 Criteria. Buildings shall be designed and constructed in accordance with the Florida Building Code, Accessibility.

Chapter 12 – Interior Environment

(No change)

Chapter 13 – Energy Efficiency

Florida Specific Amendment

Section 1301 – Energy Efficiency

Change Section 1301.1 to read as shown:

1301.1.1 Criteria. Buildings shall be designed and constructed in accordance with the International Energy Conservation Code. Florida Building Code, Energy Conservation.

Chapter 14 – Exterior Walls

Section 1401 – General

Change Section 1401.1 to read as shown:

1401.1 Scope. The provisions of this chapter shall establish the minimum requirements for exterior walls, exterior wall coverings, exterior wall openings, exterior windows and doors, architectural trim, balconies and similar projections; and bay and oriel windows.

Exception: Buildings and structures located within the high-velocity hurricane zone shall comply with the provisions of Sections 1403.8 and 1410.

(Mod S4926 / AS)

Section 1403 – Performance Requirements

Change Section 1403.7 to read as shown:

1403.7 Flood resistance for velocity wave action areas  coastal high hazard areas. For buildings in flood hazard areas subject to high-velocity wave action coastal high hazard areas as established in Section 1612.3, electrical, mechanical and plumbing system components shall not be mounted on or penetrate through exterior walls that are designed to break away under flood loads.

(Mod SP5274 / AS)

Florida Specific Amendment

Section 1403 – Performance Requirements

Add Section 1403.8 to read as shown:

- 1403.8  In order to provide for inspection for termite infestation, clearance between exterior wall coverings and final earth grade on the exterior of a building shall not be less than 6 inches (152 mm).

- Exceptions:

- 1.	Paint or decorative cementitious finish less than 5/8 inch (17.1 mm) thick adhered directly to the masonry foundation sidewall.

- 2.	Access or vehicle ramps which rise to the interior finish floor elevation for the width of such ramps only.

- 3.	A 4-inch (102 mm) inspection space above patio and garage slabs and entry areas.

- 4.	If the patio has been soil treated for termites, the finish elevation may match the building interior finish floor elevations on masonry construction only.

5.	Masonry veneers constructed in accordance with Section 2114.2.

Section 1404 – Materials

Change Section 1404.5 to read as shown:

1404.5 Metal. Exterior walls of formed steel construction, structural steel or lightweight metal alloys shall be designed in accordance with Chapters 22 and 20, respectively.

1404.5.1 Aluminum siding. Aluminum siding shall conform to the requirements of AAMA 1402 and TAS 202 and 203 in the HVHZ. (Mod S4801 / AS)

AAMA 1402, shall be modified to read as follows:

Section 1 Standard Specifications for Aluminum Siding, Soffit, and Fascia, 2.0 Siding Specifications, 2.2 Performance Criteria, 2.2.1 Windload Resistance

2.2.1.1 Static Pressure Test

2.2.1.1.1All siding products shall be capable of resisting the design pressures specified for walls for components and cladding loads in accordance with Section 1609.1.1. To verify that the siding will perform under these conditions, it shall be tested in accordance with Test Method #1, “Standard for Testing of Aluminum Siding/Fastener for Windload Resistance” or in an approved manner. The static test pressure shall be as required to demonstrate compliance with the provisions of Section 1609.1.

2.2.1.1.2 For applications where the effective design pressure as specified in Section 1609.1.1 is greater than 1040 Pa(21.7 psf) [e.g. wind zone areas greater than 36 m/s (80 mph) or elevations above 33 feet (10 m)] the product shall b tested in accordance with Test Method #1 under a static test pressure determined by the formula:

PT = 1.5 × DP

Where:
PT = Static Test Pressure [Pa (psf)] 
DP = Design Pressure [Pa (psf)] 
1.5 = Safety Factor

* Delete Section 2.2.1.2 and corresponding table.

Strike Table:

See uploaded support file for table.

3.0
Soffit and Fascia Specifications, 3.2 Performance Criteria, 3.2.1 Windload Resistance

3.2.1.1 Static Pressure Test

3.2.1.1.1 All soffit products shall be capable of resisting the design pressures specified for walls for components and cladding loads in accordance with Section 1609.1.1. To verify that the soffit will perform under these conditions, it shall be tested in the maximum unsupported length for which the manufacturer seeks conformance when tested in accordance with Test Method #4, “Standard for Testing of Soffits and Windload Resistance.”

The static test pressure shall be as required to demonstrate compliance with the provisions of Section 1609.1.

3.2.1.1.2 For applications where the effective design pressure as specified in Section 1609.1.1 is greater than 1040 Pa (21.7 psf) [e.g. wind zone areas greater than (80 mph) 36 m/s or elevations above (33 ft.) 10 m] the product shall be tested in accordance with Test Method #4 under a static test pressure determined by the formula:

PT = × 1.5 × DPp

Where:

PT = Static Test Pressure [Pa (psf)] 
DPp = Design Pressure [Pa (psf)] 
1.5 = Safety Factor

Section 3, Appendix, Windload Criteria is deleted in its entirety.

(Mod S5728 / AS)

(Mod S4801 / AS)

Section 1404 – Materials

Add Section 1404.13 to read as shown:

1404.13 Manufactured soffit materials and systems shall be labeled in accordance with the provisions of Section 1710.9 of this code.

(Mod S5733 / AS)

Section 1405 – Installation of Wall Coverings

Change Section 1405.1 to read as shown:

1405.1 General. Exterior wall coverings shall be designed and constructed in accordance with the applicable provisions of this section and TAS 202 and 203 in the HVHZ.

(Mod S4931 / AS)

Section 1405 – Installation of Wall Coverings

Change Table 1405.2 to read as shown:

TABLE 1405.2

MINIMUM THICKNESS OF WEATHER COVERINGS

| COVERING TYPE | MINIMUM THICKNESS (inches) |
| --- | --- |
| Adhered masonry veneer | 0.25 |
| Aluminum siding | 0.019 |
| Anchored masonry veneer | 2.625 |
| Asbestos-cement boards | 0.125 |
| Asbestos shingles | 0.156 |
| Cold-rolled copperd | 0.0216 nominal |
| Copper shinglesd | 0.0162 nominal |
| Exterior plywood (with sheathing) | 0.313 |
| Exterior plywood (without sheathing) | See Section 2304.6 (HVHZ see Section 2315.2) |
| Fiber-cement lap siding | 0.25c |
| Fiber-cement panel siding | 0.25c |
| Fiberboard siding | 0.5 |
| Glass-fiber reinforced concrete panels | 0.375 |
| Hardboard sidingc | 0.25 |
| High-yield copperd | 0.0162 nominal |
| Lead-coated high-yield copper | 0.0162 nominal |
| Marble slabs | 1 |
| Particleboard (with sheathing) | See Section 2304.6 (HVHZ see Section 2315.1.11) |
| Particleboard (without sheathing) | See Section 2304.6 (HVHZ see Section 2315.1.11) |
| Precast stone facing | 0.625 |
| Steel (approved corrosion resistant) | 0.0149 |
| Stone (cast artificial) | 1.5 |
| Stone (natural) | 2 |
| Structural glass | 0.344 |
| Stucco or exterior cement plaster |  |
| Three-coat work over: |  |
| Metal plaster base | 0.875b |
| Unit masonry | 0.625b |
| Cast-in-place or precast concrete | 0.625b |
| Two-coat work over: |  |
| Unit masonry | 0.5b |
| Cast-in-place or precast concrete | 0.375b |
| Terra cotta (anchored) | 1 |
| Terra cotta (adhered) | 0.25 |
| Vinyl siding | 0.035 |
| Wood shingles | 0.375 |
| Wood siding (without sheathing)a | 0.5 |
| Lead-coated copperd | 0.0216 nominal |

For SI: 1 inch = 25.4 mm, 1 ounce per square foot = 0.305 kg/m2.

a. Wood siding of thicknesses less than 0.5 inch shall be placed over sheathing that conforms to Section 2304.6. (HVHZ see Section 2315.2)

b. Exclusive of texture.

c. As measured at the bottom of decorative grooves.

d. 16 ounces per square foot for cold-rolled copper and lead-coated copper, 12 ounces per square foot for copper shingles, high-yield copper and lead-coated high-yield copper.

e. Includes scratch coat, setting bed, and precast stone.

(Mod S4933 / AS)

Section 1405 – Installation of Wall Coverings

Change Section 1405.17 to read as shown:

1405.17 Fastening.  Weather boarding and wall coverings shall be securely fastened with aluminum, copper, zinc, zinc-coated or other approved corrosion-resistant fasteners in accordance with the nailing schedule in Table 2304.9.1, the HVHZ shall comply with Table 2323.1 or the approved manufacturer's installation instructions. Shingles and other weather coverings shall be attached with appropriate standard-shingle nails to furring strips securely nailed to studs, or with approved mechanically bonding nails, except where sheathing is of wood not less than 1-inch (25 mm) nominal thickness or of wood structural panels as specified in Table 2308.9.3(3) (the HVHZ shall comply with Section 2322).

(Mod S4932 / AS)

Chapter 15 - Roof Assemblies and Rooftop Structures

Florida Specific Amendment

Section 1501 – General

change Section 1501.1 to read as shown:

1501.1 Scope.  The provisions of this chapter shall govern the design, materials, construction and quality of roof assemblies, and rooftop structures.

Exception: Buildings and structures located within the high-velocity hurricane zone shall comply with the provisions of Section 1503.6 and Sections 1512 through 1525.

Section 1502 – Definitions

Change Section 1502.1 to read as shown:

1502.1 Definitions General. The following words and terms shall, for the purposes of this chapter and as used elsewhere in this code, have the meanings shown herein. The following terms are defined in Chapter 2:

AGGREGATE. In roofing, crushed stone, crushed slag or water-worn gravel used for surfacing for roof coverings. 

BALLAST. In roofing, ballast comes in the form of large stones or paver systems or light-weight interlocking paver systems and is used to provide uplift resistance for roofing systems that are not adhered or mechanically attached to the roof deck. 

BUILDING INTEGRATED PHOTOVOLTAIC ROOFING. A roofing product consisting of electricity generating photovoltaic component integrated into a roof covering. 

BUILT-UP ROOF COVERING. Two or more layers of felt cemented together and surfaced with a cap sheet, mineral aggregate, smooth coating or similar surfacing material. 

INTERLAYMENT. A layer of felt or nonbituminous saturated felt not less than 18 inches (457 mm) wide, shingled between each course of a wood-shake roof covering. 

MECHANICAL EQUIPMENT SCREEN. A partially enclosed rooftop structure used to aesthetically conceal heating, ventilating and air conditioning (HVAC) electrical or mechanical equipment from view. 

METAL ROOF PANEL. An interlocking metal sheet having a minimum installed weather exposure of 3 square feet (0.279 m2) per sheet. 

METAL ROOF SHINGLE. An interlocking metal sheet having an installed weather exposure less than 3 square feet (0.279 m2) per sheet. 

MODIFIED BITUMEN ROOF COVERING. One or more layers of polymer-modified asphalt sheets. The sheet materials shall be fully adhered or mechanically attached to the substrate or held in place with an approved ballast layer. 

PENTHOUSE. An enclosed, unoccupied structure above the roof of a building, other than a tank, tower, spire, dome cupola or bulkhead. 

POSITIVE ROOF DRAINAGE. The drainage condition in which consideration has been made for all loading deflections of the roof deck, and additional slope has been provided to ensure drainage of the roof within 48 hours of precipitation. 

REROOFING. The process of recovering or replacing an existing roof covering. See "Roof recover" and "Roof replacement." 

ROOF ASSEMBLY. A system designed to provide weather protection and resistance to design loads. The system consists of a roof covering and roof deck or a single component serving as both the roof covering and the roof deck. A roof assembly includes the roof deck, vapor retarder, substrate or thermal barrier, insulation, vapor retarder and roof covering. 

The definition of "Roof assembly" is limited in application to the provisions of Chapter 15. 

ROOF COVERING. The covering applied to the roof deck for weather resistance, fire classification or appearance. 

ROOF COVERING SYSTEM. See "Roof assembly." 

ROOF DECK. The flat or sloped surface not including its supporting members or vertical supports. 

ROOF RECOVER. The process of installing an additional roof covering over a prepared existing roof covering without removing the existing roof covering. 

ROOF REPAIR. Reconstruction or renewal of any part of an existing roof for the purposes of its maintenance. 

ROOF REPLACEMENT. The process of removing the existing roof covering, repairing any damaged substrate and installing a new roof covering. 

ROOF SECTION. A separation or division of a roof area by existing joints, parapet walls, flashing (excluding valleys), difference of elevation (excluding hips and ridges), roof type or legal description; not including the roof area required for a proper tie-off with an existing system. 

ROOF VENTILATION. The natural or mechanical process of supplying conditioned or unconditioned air to, or removing such air from, attics, cathedral ceilings or other enclosed spaces over which a roof assembly is installed. 

ROOFTOP STRUCTURE. An enclosed structure on or above the roof of any part of a building. 

SCUPPER. An opening in a wall or parapet that allows water to drain from a roof. 

SINGLE-PLY MEMBRANE. A roofing membrane that is field applied using one layer of membrane material (either homogeneous or composite) rather than multiple layers. 

UNDERLAYMENT. One or more layers of felt, sheathing paper, nonbituminous saturated felt or other approved material over which a steep-slope roof covering is applied.

(Mod R5258 / AS)

Section 1503 – Weather Protection

Change Section 1503.2 to read as shown:

1503.2 Flashing. Flashing shall be installed in such a manner so as to prevent moisture entering the wall and roof through joints in copings, through moisture-permeable materials and at intersections with parapet walls and other penetrations through the roof plane.

1503.2.1 Locations. Flashing shall be installed at wall and roof intersections, at gutters, wherever there is a change in roof slope or direction and around roof openings. Where flashing is of metal, the metal shall be corrosion resistant with a thickness not less than 0.019 inch (0.483 mm) (No. 26 galvanized sheet) provided in Table 1503.2.

Exception: This requirement does not apply to hip and ridge junctions.

TABLE 1503.2
METAL FLASHING MATERIAL

| MATERIAL | MINIMUM THICKNESS (INCHES) | GAGE | WEIGHT (LBS PER SQ FT) |
| --- | --- | --- | --- |
| Copper |  |  | 1 (16 oz) |
| Aluminum | 0.024 |  |  |
| Stainless Steel |  | 28 |  |
| Galvanized Steel | 0.0179 | 26 (zinc coated G90) |  |
| Aluminum Zinc Coated Steel | 0.0179 | 26 (AZ50 Alum Zinc) |  |
| Zinc Alloy | 0.027 |  |  |
| Lead |  |  | 2.5 (40 oz) |
| Painted Terne |  |  | 1.25 (20 oz) |

(Mod R5340 / AS) (Mod R5341 / AS)

Section 1503 – Weather Protection

Change Section 1503.4 to read as shown:

1503.4 Roof drainage. Unless roofs are sloped to drain over roof edges, D design and installation of roof drainage systems shall comply with Section 1503 of this code and Sections 1106 and 1108, as applicable, of and the Florida Building Code, Plumbing, Chapter 11 International Plumbing Code.

(Mod R5345 / AS)

Section 1503 – Weather Protection

Change Section 1503.4.1 to read as shown:

1503.4.1 Secondary (emergency overflow) drains or scuppers. Where roof drains are required, secondary (emergency overflow) roof drains or scuppers shall be provided where the roof perimeter construction extends above the roof in such a manner that water will be entrapped if the primary drains allow buildup for any reason. The installation and sizing of secondary emergency overflow drains, leaders and conductors shall comply with Sections 1106 and 1108 1107, as applicable, of the International Plumbing Code Florida Building Code, Plumbing, Chapter 11 .

(Mod R5342 / AS)

Section 1503 – Weather Protection

Change Section 1503.4.2 to read as shown:

1503.4.2 Scuppers. Where required for roof drainage, a scupper shall be placed level with the roof surface in a wall or parapet. The scupper shall be located as determined by the slope and the contributing area of the roof. The exterior facing or lining of a scupper, if metal, shall be the same as flashing material required by Sections 1503 through 1510 for the particular type of covering specified for the building. For other type materials, follow manufacturer's specifications. When scuppers are used for secondary (emergency overflow) roof drainage, the quantity, size, location and inlet elevation of the scuppers shall be sized to prevent the depth of ponding water from exceeding that for which the roof was designed as determined by Section 1611.1. Scuppers shall not have an opening dimension of less than 4 inches (102 mm). The flow through the primary system shall not be considered when locating and sizing scuppers.

(Mod R5344 / AS)

Section 1503 – Weather Protection

Add Section 1503.4.2.1 to read as shown:

1503.4.2.1 Overflow scuppers. When other means of drainage of overflow water is not provided, overflow scuppers shall be placed in walls or parapets not less than 2 inches (51 mm) nor more than 4 inches (102 mm) above the finished roof covering and shall be located as close as practical to required vertical leaders or downspouts or wall and parapet scuppers. An overflow scupper shall be sized in accordance with the Florida Building Code, Plumbing.

(Mod R5343 / AS)

Section 1503 – Weather Protection

Change Section 1503.5 to read as shown:

1503.5 Roof ventilation. Attic ventilation Intake and exhaust vents shall be provided in accordance with Section 1203.2 and the manufacturer's installation instructions.

(Mod R5346 / AS)

Section 1503 – Weather Protection

Change Section 1503.7 to read as shown:

1503.7 Protection against decay and termites.  Condensate lines and roof downspouts shall discharge at least 1 foot (305 mm) away from the structure sidewall, whether by underground piping, tail extensions, or splash blocks. Gutters with downspouts are required on all buildings with eaves of less than 6 inches (152 mm) horizontal projection except for gable end rakes or on a roof above another roof.

Section 1504 – Performance Requirements

Change Section 1504.1.1 to read as shown:

1504.1.1 Wind resistance of asphalt shingles. Asphalt shingles shall comply be designed for wind speeds in accordance with Section 1507.2.7.

(Mod R5348 / AS)

Section 1504 – Performance Requirements

Change Section 1504.3.2 to read as shown:

Section 1504.3.2 Metal panel roof systems. Change to read as shown:

1504.3.2 Metal panel roof systems. Metal panel roof systems through fastened or standing seam shall be tested in accordance with UL 580 or ASTM E 1592 or TAS 125.

(No change to remainder of text).

(Mod R5349 / AS)

Section 1504 – Performance Requirements

Change Section 1504.5 to read as shown:

1504.5 Edge securement for low-slope roofs. Low-slope built-up, modified bitumen and single-ply roof system metal edge securement, except gutters, shall be designed and installed for wind loads in accordance with Chapter 16 and tested for resistance in accordance with Test Methods RE-1, RE-2 and RE-3 of ANSI/SPRI ES-1, or RAS 111 except Vult wind speed shall be determined from Figure 1609A, 1609B, or 1609C as applicable.

(Mod R5350 / AS)

Section 1504 – Performance Requirements

Change Section 1504.6 to read as shown:

1504.6 Physical properties. Roof coverings installed on low-slope roofs (roof slope < 2:12) in accordance with Section 1507 shall demonstrate physical integrity over the working life of the roof based upon 2,000 hours of exposure to accelerated weathering tests conducted in accordance with ASTM G 152, ASTM G 153, ASTM G 155 or ASTM G 154. Those roof coverings that are subject to cyclical flexural response due to wind loads shall not demonstrate any significant loss of tensile strength for unreinforced membranes or breaking strength for reinforced membranes when tested as herein required.

(Mod R5351 / AS)

Section 1504 – Performance Requirements

Change Section 1504.7 to read as shown:

1504.7 Impact resistance. Roof coverings installed on low-slope roofs (roof slope < 2:12) in accordance with Section 1507 shall resist impact damage based on the results of tests conducted in accordance with ASTM D 3746, ASTM D 4272, CGSB 37-GP-52M or the "Resistance to Foot Traffic Test" in Section 5.5 of FM 4470. All structural metal roofing systems having a thickness equal to or greater than 22 gage and all non-structural metal roof systems having a thickness equal to or greater than 26 gage shall be exempt from the tests listed above.

(Mod R5352 / AS)

Section 1504 – Performance Requirements

Change Section 1504.8 to read as shown:

1504.8 Aggregate.  Aggregate used as surfacing for roof coverings and aggregate, gravel or stone used as ballast shall not be used on the roof of a building located in a hurricane-prone region as defined in Section 202, or on any other building with a mean roof height exceeding that permitted by Table 1504.8 based on the exposure category and basic wind speed at the site  shall be permitted as roof surfacing when installed on slopes of 3:12 or less, not less than 400 pound (182 kg) of roofing gravel or 300 pounds (145 kg) of slag per square shall be applied. A minimum of 50 percent of the total aggregate shall be embedded in the flood coat of bitumen or installed in accordance with its product approval. Aggregate shall be dry and free from dirt and shall be in compliance with the sizing requirements set forth in ASTM D 1863. A building official may request a test to confirm compliance with these requirements.

TABLE 1504.8

MAXIMUM ALLOWABLE MEAN ROOF HEIGHT PERMITTED FOR BUILDINGS WITH AGGREGATE ON THE ROOF IN AREAS OUTSIDE A HURRICANE-PRONE REGION

Reserved.

| NOMINAL DESIGN WIND SPEED, Vasd (mph)b, d | MAXIMUM MEAN ROOF HEIGHT (ft)a, c |  |  |
| --- | --- | --- | --- |
|  | Exposure category |  |  |
|  | B | C | D |
| 85 | 170 | 60 | 30 |
| 90 | 110 | 35 | 15 |
| 95 | 75 | 20 | NP |
| 100 | 55 | 15 | NP |
| 105 | 40 | NP | NP |
| 110 | 30 | NP | NP |
| 115 | 20 | NP | NP |
| 120 | 15 | NP | NP |
| Greater than 120 | NP | NP | NP |
| For SI: 1 foot = 304.8 mm; 1 mile per hour = 0.447 m/s. |  |  |  |
| a. Mean roof height as defined in ASCE 7. |  |  |  |
| b. For intermediate values of Vasd, the height associated with the next higher value of Vasd shall be used, or direct interpolation is permitted. |  |  |  |
| c. NP = gravel and stone not permitted for any roof height. |  |  |  |

d. Vasd shall be determined in accordance with Section 1609.3.1.

(Mod R5353 / AS)

Section 1504 – Performance Requirements

Add Section 1504.9 to read as shown:

1504.9 Margin of Safety.  A margin of safety of 2:1 shall be applied to all wind uplift resistance test results except when a margin of safety is specified in the test standard.

Exception:  Asphalt shingles testing resulting in a miles per hour rating as required in section 1507.2.7.

(Mod R5686 / AS)

Section 1505 – Fire Classification

Change Section 1505.7 to read as shown:

Section 1505.7 Special purpose roofs. Change to read as shown:

1505.7 Special purpose roofs.  Reserved.  Special purpose wood shingle or wood shake roofing shall conform with the grading and application requirements of Section 1507.8 or 1507.9. In addition, an underlayment of 5/8-inch (15.9 mm) Type X water-resistant gypsum backing board or gypsum sheathing shall be placed under minimum nominal 1/2-inch-thick (12.7 mm) wood structural panel solid sheathing or 1-inch (25 mm) nominal spaced sheathing.

(Mod R5356 / AS)

Section 1506 – Materials

Add Section 1506.5 to read as shown:

1506.5 Nails. Nails shall be corrosion resistant nails conforming to ASTM F 1667. The corrosion resistance shall meet ASTM A 641, Class 1 or an equal corrosion resistance by coating, electro galvanization, mechanical galvanization, hot dipped galvanization, stainless steel, nonferrous metal and alloys or other suitable corrosion resistant material.

(Mod R5357 / AS)

Section 1506 – Materials

Add Section 1506.6 to read as shown:

1506.6 Screws. Wood screws conform to ANSI/ASME B 18.6.1. Screws shall be corrosion resistant by coating, galvanization, stainless steel, nonferrous metal or other suitable corrosion resistant material. The corrosion resistance shall be demonstrated through one of the following methods:

1. Corrosion resistance equivalent to ASTM A 641, Class 1;

2. Corrosion resistance in accordance with TAS114, Appendix E; or

3. Corrosion resistant coating exhibiting not more than 5 percent red rust after 1000 hours exposure in accordance with ASTM B 117.

(Mod R5358 / AS)

Section 1506 – Materials

Add Section 1506.7 to read as shown:

1506.7 Clips. Clips shall be corrosion resistant clips. The corrosion resistance shall meet 0.90 ounce per square foot (0.458 kg/m2) measured according to ASTM A 90/A 90M, TAS 114 Appendix E or an equal corrosion resistance coating, electro galvanization, mechanical galvanization, hot dipped galvanization, stainless steel, nonferrous metals and alloys or other suitable corrosion resistant material. Stainless steel clips shall conform to ASTM A167, Type 304.

(Mod R5359 / AS)

Section 1507 – Requirements for Roof Coverings

Change Section 1507.2.3 to read as shown:

Section 1507.2.3 Underlayment. Change section to read as shown:

1507.2.3 Underlayment.  Unless otherwise noted, required underlayment shall conform to ASTM D 226, Type I or Type II, or ASTM D 4869 Type I  II or Type IV or ASTM D 6757.

(Mod R5360 / AS)

Section 1507 – Requirements for Roof Coverings

Change Section 1507.2.5 to read as shown:

1507.2.5 Asphalt shingles. Asphalt shingles shall have self-seal strips or be interlocking and comply with ASTM D 225 or ASTM D 3462. Shingles shall also comply with Table 1507.2.7.1. Asphalt shingle packaging shall bear labeling indicating compliance with one of the required classifications as shown in Table 1507.2.7.1.

(Mod R5361 / AS)

Section 1507 – Requirements for Roof Coverings

Add Section 1507.2.6.1 to read as shown:

1507.2.6.1 The nail component of plastic cap nails shall meet the corrosion resistance requirements of Section 1506.5.

(Mod R5362 / AS)

Section 1507 – Requirements for Roof Coverings

Change Section 1507.2.7 to read as shown:

1507.2.7 Attachment. Asphalt shingles shall have the minimum number of fasteners required by the manufacturer, but  and Section 1504.1. Asphalt shingles shall be secured to the roof with not less than four fasteners per strip shingle or two fasteners per individual strip shingle or two fasteners per individual shingle. Where the roof slope exceeds 21 units vertical in 12 units horizontal (21:12), asphalt shingles shall be installed as required by in accordance with the manufacturer's printed installation instructions for steep-slope roof applications.

(Mod R5364 / AS)

Section 1507 – Requirements for Roof Coverings

Change Section 1507.2.7.1 to read as shown:

1507.2.7.1 Wind Resistance of Asphalt Shingles. Asphalt shingles shall be tested classified in accordance with ASTM D 3161, TAS 107 or ASTM D 7158.  Asphalt shingles shall meet the classification requirements of Table 1507.2.7.1(1) for the appropriate maximum basic wind speed. Shingles classified as ASTM D 3161 Class D or ASTM D 7158 Class G are acceptable for use in the 100-mph wind zone. Shingles classified as ASTM D 3161 Class F, TAS107 or ASTM D 7158 Class H are acceptable for use in all wind zones. Asphalt shingle packaging wrappers shall bear a label to indicate compliance with ASTM D 7158 and the one of the required classifications as shown in Table 1507.2.7.1(1).

Exception: Asphalt shingles not included in the scope of ASTM D 7158 shall be tested and labeled to indicate compliance with ASTM D 3161 and the required classification in Table 1507.2.7.1(2).

TABLE 1507.2.7.1(1)

CLASSIFICATION OF ASPHALT ROOF SHINGLES PER ASTM D 7158a

| NOMINAL DESIGN WIND SPEED, Vasdb (mph) | CLASSIFICATION REQUIREMENT |
| --- | --- |
| 85 | D, G or H |
| 90 | D, G or H |
| 100 | G or H |
| 110 | G or H |
| 120 | G or H |
| 130 | H |
| 140 | H |
| 150 | H |
| For SI: 1 foot = 304.8 mm; 1 mph = 0.447 m/s. |  |
| a. The standard calculations contained in ASTM D 7158 assume exposure category B or C and building height of 60 feet or less. Additional calculations are required for conditions outside of these assumptions. |  |
| b. Vasd shall be determined in accordance with Section 1609.3.1. |  |

| MAXIMUM BASIC WIND SPEED FROM FIGURE 1609A, B, C or ASCE-7 | Vasd | ASTM D 7158 | ASTM D 3161 |
| --- | --- | --- | --- |
| 110 | 85 | D, G or H | A, D or F |
| 116 | 90 | D, G or H | A, D or F |
| 129 | 100 | G or H | A, D or F |
| 142 | 110 | G or H | F |
| 155 | 120 | G or H | F |
| 168 | 130 | H | F |
| 181 | 140 | H | F |
| 194 | 150 | H | F |

TABLE 1507.2.7.1(2)

CLASSIFICATION OF ASPHALT SHINGLES PER ASTM D 3161

Reserved.

|  | NOMINAL DESIGN WIND SPEED, Vasda (mph) | CLASSIFICATION REQUIREMENT |  |
| --- | --- | --- | --- |
|  | 85 | A, D or F |  |
|  | 90 | A, D or F |  |
|  | 100 | A, D or F |  |
|  | 110 | F |  |
|  | 120 | F |  |
|  | 130 | F |  |
|  | 140 | F |  |
|  | 150 | F |  |
| For SI: 1 mph = 0.447 m/s. |  |  |  |
| a. Vasd shall be determined in accordance with Section 1609.3.1. |  |  |  |

(Mod R5363- R2 / AM)

Section 1507 – Requirements for Roof Coverings

Change Section 1507.2.8 to read as shown:

1507.2.8 Underlayment application. Underlayment shall be installed using one of the following methods:    For roof slopes from two units vertical in 12 units horizontal (17-percent slope) and up to four units vertical in 12 units horizontal (33-percent slope), underlayment shall be two layers applied in the following manner. Apply a minimum 19-inch-wide (483 mm) strip of underlayment felt parallel with and starting at the eaves, fastened sufficiently to hold in place. Starting at the eave, apply 36-inch-wide (914 mm) sheets of underlayment overlapping successive sheets 19 inches (483 mm), by fastened sufficiently to hold in place. Distortions in the underlayment shall not interfere with the ability of the shingles to seal. For roof slopes of four units vertical in 12 units horizontal (33-percent slope) or greater, underlayment shall be one layer applied in the following manner. Underlayment shall be applied shingle fashion, parallel to and starting from the eave and lapped 2 inches (51 mm), fastened sufficiently to hold in place. Distortions in the underlayment shall not interfere with the ability of the shingles to seal.

1.      For roof slopes from two units vertical in 12 units horizontal (17-percent slope), and less than four units vertical in 12 units horizontal (33-percent slope). Underlayment shall comply with ASTM D 226, Type I or Type II or ASTM D 4869, Type II or Type IV or ASTM D 6757 and shall be two layers applied in the following manner. Apply a 19-inch (483 mm) strip of underlayment felt parallel to and starting at the eaves, fastened sufficiently to hold in place. Starting at the eave, apply 36-inch-wide (914 mm) sheets of underlayment, overlapping successive sheets 19 inches (483 mm), and fastened with 1 inch (25 mm) round plastic cap, metal cap nails or nails and tin-tabs attached to a nailable deck with one row in the field of the sheet with a maximum fastener spacing of 12 in. o.c. (305 mm), and one row at the overlaps fastened 6 in. o.c. (152 mm). Synthetic underlayment shall be fastened in accordance with this section and the manufacturer’s recommendations.

2.      For roof slopes of four units vertical in 12 units horizontal (33-percent slope) or greater. Underlayment shall comply with ASTM D 226, Type II or ASTM D 4869, Type IV or ASTM D 6757 and shall be one layer applied in the following manner. Underlayment shall be applied shingle fashion, parallel to and starting from the eave and lapped 2 inches (51 mm), fastened with 1 inch (25 mm) round plastic cap, metal cap nails or nails and tin-tabs attached to a nailable deck with two staggered rows in the field of the sheet with a maximum fastener spacing of 12 in. o.c. (305 mm), and one row at the overlaps fastened 6 in. o.c. (152 mm). Synthetic underlayment shall be fastened in accordance with this section and the manufacturer’s recommendations End laps shall be offset by 6 feet (1829 mm).

3.      As an alternative, the entire roof deck shall be covered with an approved self-adhering polymer modified bitumen sheet meeting ASTM D 1970 or an approved self-adhering synthetic underlayment installed in accordance with the manufacturer’s installation instructions.

(Mod R5562 / AS)

Section 1507 – Requirements for Roof Coverings

Change Section 1507.2.8.1 to read as shown:

1507.2.8.1 High wind attachment. Reserved
Underlayment applied in areas subject to high winds [Vasd greater than 110 mph (49 m/s) as determined in accordance with Section 1609.3.1] shall be applied with corrosion-resistant fasteners in accordance with the manufacturer's instructions. Fasteners are to be applied along the overlap at a maximum spacing of 36 inches (914 mm) on center. 
Underlayment installed where Vasd, in accordance with Section 1609.3.1, equals or exceeds 120 mph (54 m/s) shall comply with ASTM D 226 Type II, ASTM D 4869 Type IV, or ASTM D 6757. The underlayment shall be attached in a grid pattern of 12 inches (305 mm) between side laps with a 6-inch (152 mm) spacing at the side laps. Underlayment shall be applied in accordance with Section 1507.2.8 except all laps shall be a minimum of 4 inches (102 mm). Underlayment shall be attached using metal or plastic cap nails with a head diameter of not less than 1 inch (25 mm) with a thickness of at least 32-gauge [0.0134 inch (0.34 mm)] sheet metal. The cap nail shank shall be a minimum of 12 gauge [0.105 inch (2.67 mm)] with a length to penetrate through the roof sheathing or a minimum of 3/4 inch (19.1 mm) into the roof sheathing. 
Exception: As an alternative, adhered underlayment complying with ASTM D 1970 shall be permitted.

(Mod R5365 / AS)

Section 1507 – Requirements for Roof Coverings

Change Section 1507.2.8.2 to read as shown:

1507.2.8.2 Ice barrier. Reserved. 
In areas where there has been a history of ice forming along the eaves causing a backup of water, an ice barrier that consists of at least two layers of underlayment cemented together or of a self-adhering polymer modified bitumen sheet shall be used in lieu of normal underlayment and extend from the lowest edges of all roof surfaces to a point at least 24 inches (610 mm) inside the exterior wall line of the building. 
Exception: Detached accessory structures that contain no conditioned floor area.

(Mod R5367 / AS)

Section 1507 – Requirements for Roof Coverings

Change Section 1507.2.9.1 to read as shown:

1507.2.9.1 Base and cap counter flashing. Base and cap counter flashing shall be installed in accordance with the manufacturer's instructions. Base flashing shall be of either corrosion-resistant metal of minimum nominal 0.019-inch (0.483 mm) thickness or mineral-surfaced roll roofing weighing a minimum of 77 pounds per 100 square feet (3.76 kg/m2). Cap flashing shall be corrosion-resistant metal of minimum nominal 0.019-inch (0.483 mm) thickness. as follows:

1.      In accordance with manufacturer's installation instructions, or

2.       A continuous metal minimum 4? × 4? "L" flashing shall be set in approved flashing cement and set flush to base of wall and over the underlayment. Both horizontal and vertical metal flanges shall be fastened 6 inches (152 mm) on center with approved fasteners. All laps shall be a minimum of 4 inches (102 mm) fully sealed in approved flashing cement. Flashing shall start at the lower portion of roof to insure water-shedding capabilities of all metal laps. The entire edge of the horizontal flange shall be sealed covering all nail penetrations with approved flashing cement and membrane. Shingles will overlap the horizontal flange and shall be set in approved flashing cement. 

Base flashing shall be of either corrosion resistant metal with a minimum thickness provided in Table 1503.2 or mineral surface roll roofing weighing a minimum of 77 pounds per 100 square feet (3.76 kg/m2). Counter flashing shall be corrosion resistant metal with a minimum thickness provided in Table 1503.2.

(Mod R5370 / AS)

Section 1507 – Requirements for Roof Coverings

Change Section 1507.2.9.2 to read as shown:

1507.2.9.2 Valleys. Valley linings shall be installed in accordance with the manufacturer's instructions before applying shingles. Valley linings of the following types shall be permitted:

1. For open valleys (valley lining exposed) lined with metal, the valley lining shall be at least 24 16 inches (610 406 mm) wide and of any of the corrosion-resistant metals in Table 15073.2.9. 2.

2. For open valleys, valley lining of two plies of mineral-surfaced roll roofing complying with ASTM D 3909 or ASTM D 6380 Class M shall be permitted. The bottom layer shall be 18 inches (457 mm) and the top layer a minimum of 36 inches (914 mm) wide.

3. For closed valleys (valleys covered with shingles), valley lining of one ply of smooth roll roofing complying with ASTM D 6380 Class S , and at least 36 inches (914 mm) wide or types as described in Item 1 or 2 above shall be permitted. Self-adhering polymer modified bitumen underlayment complying with ASTM D 1970 shall be permitted in lieu of the lining material.

TABLE 1507.2.9.2

VALLEY LINING MATERIAL

Reserved.

| MATERIAL | MINIMUM THICKNESS | GAGE | WEIGHT |  |
| --- | --- | --- | --- | --- |
| Aluminum | 0.024 in. | — | — |  |
| Cold-rolled copper | 0.0216 in. | — | ASTM B 370, 16 oz. per square ft. |  |
| Copper | — | — | 16 oz |  |
| Galvanized steel | 0.0179 in. | 26 (zinc-coated G90) | — |  |
| High-yield copper | 0.0162 in. | — | ASTM B 370, 12 oz. per square ft. |  |
| Lead | — | — | 2.5 pounds |  |
| Lead-coated copper | 0.0216 in. | — | ASTM B 101, 16 oz. per square ft. |  |
| Lead-coated high-yield copper | 0.0162 in. | — | ASTM B 101, 12 oz. per square ft. |  |
| Painted terne | — | — | 20 pounds |  |
| Stainless steel | — | 28 | — |  |
| Zinc alloy | 0.027 in. | — | — |  |
| For SI: 1 inch = 25.4 mm, 1 pound = 0.454 kg, 1 ounce = 28.35 g, 1 square foot = 0.093 m2. |  |  |  |  |

(Mod R5371 / AS)

Section 1507 – Requirements for Roof Coverings

Change Section 1507.2.9.3 to read as shown:

1507.2.9.3 Drip edge. Provide drip edge at eaves and gables of shingle roofs. Overlap to be a minimum of 2 3 inches (51 76 mm). Eave drip edges shall extend ¼ 1/2 inch (6.4 13 mm) below sheathing and extend back on the roof a minimum of 2 inches (51 mm). Drip edge at eaves shall be permitted to be installed either over or under the underlayment. If installed over the underlayment, there shall be a minimum 4 inches (51 mm) width of roof cement installed over the drip edge flange. Drip edge shall be mechanically fastened a maximum of 12 inches (305 mm) on center. Where the Vasd as determined in accordance with Section 1609.3.1 is 110 mph (177 km/h) or greater or the mean roof height exceeds 33 feet (10 058 mm), drip edges shall be mechanically fastened a maximum of 4 inches (102 mm) on center.

(Mod R5372 / AS)

Section 1507 – Requirements for Roof Coverings Change Section 1507.3 to read as shown: Section 1507.3 Clay and concrete tile. Change to read as shown: 1507.3 Clay and concrete tile. The installation of clay and concrete tile shall comply with the provisions of this section. 1507.3.1 Deck requirements. Concrete and clay tile shall be installed only over solid sheathing or except where the roof covering is specifically designed and tested in accordance with Section 1609.5.2 to be applied over spaced structural spaced sheathing boards. (Mod R5373 / AS) 1507.3.2 Deck slope. Clay and concrete roof tile shall be installed on roof slopes of 21/2 units vertical in 12 units horizontal (21-percent slope) or greater. For roof slopes from 21/2 units vertical in 12 units horizontal (21-percent slope) to four units vertical in 12 units horizontal (33-percent slope), double underlayment application is required in accordance with Section 1507.3.3. in accordance with the recommendations of FRSA/TRI Florida High Wind Concrete and Clay Roof Tile Installation Manual, Fifth Edition where the Vasd as determined in accordance with Section 1609.3.1 or the recommendations of RAS 118, 119 or 120. 1507.3.3 Underlayment. Unless otherwise noted, required underlayment shall conform to: ASTM D 226, Type II; ASTM D 2626, ASTM D 1970 or ASTM D 6380, Class M mineral-surfaced roll roofing. Underlayment shall be applied according to the tile manufacturer's installation instructions or the recommendations of the FRSA/TRI Florida High Wind Concrete and Clay Roof Tile Installation Manual, Fifth Edition where the basic wind speed, Vasd, is determined in accordance with Section 1609.3.1 or the recommendations of RAS 118, 119 or 120. 1507.3.3.1 Low-slope roofs Slope and underlayment requirements. Refer to FRSA/TRI Florida High Wind Concrete and Clay Roof Tile Installation Manual, Fifth Edition where the basic wind speed, Vasd, is determined in accordance with Section 1609.3.1 for underlayment and slope requirements for specific roof tile systems or the recommendations of RAS 118, 119 or 120. For roof slopes from 21/2 units vertical in 12 units horizontal (21-percent slope), up to four units vertical in 12 units horizontal (33-percent slope), underlayment shall be a minimum of two layers applied as follows: 1. Starting at the eave, a 19-inch (483 mm) strip of underlayment shall be applied parallel with the eave and fastened sufficiently in place. 2. Starting at the eave, 36-inch-wide (914 mm) strips of underlayment felt shall be applied overlapping successive sheets 19 inches (483 mm) and fastened sufficiently in place. 1507.3.3.2 High-slope roofs. Reserved. For roof slopes of four units vertical in 12 units horizontal (33-percent slope) or greater, underlayment shall be a minimum of one layer of underlayment felt applied shingle fashion, parallel to, and starting from the eaves and lapped 2 inches (51 mm), fastened only as necessary to hold in place. 1507.3.3.3 High wind attachment. Reserved. Underlayment applied in areas subject to high wind [Vasd greater than 110 mph (49 m/s) as determined in accordance with Section 1609.3.1] shall be applied with corrosion-resistant fasteners in accordance with the manufacturer's installation instructions. Fasteners are to be applied along the overlap not farther apart than 36 inches (914 mm) on center. Underlayment installed where Vasd, in accordance with Section 1609.3.1, equals or exceeds 120 mph (54 m/s) shall be attached in a grid pattern of 12 inches (305 mm) between side laps with a 6-inch (152 mm) spacing at the side laps. Underlayment shall be applied in accordance with Sections 1507.3.3.1 and 1507.3.3.2 except all laps shall be a minimum of 4 inches (102 mm). Underlayment shall be attached using metal or plastic cap nails with a head diameter of not less than 1 inch (25 mm) with a thickness of at least 32-gauge [0.0134 inch (0.34 mm)] sheet metal. The cap nail shank shall be a minimum of 12 gauge [0.105 inch (2.67 mm)] with a length to penetrate through the roof sheathing or a minimum of 3/4 inch (19.1 mm) into the roof sheathing. Exception: As an alternative, adhered underlayment complying with ASTM D 1970 shall be permitted. 1507.3.4 Clay tile. Clay roof tile shall comply with ASTM C 1167. 1507.3.5 Concrete tile. Concrete roof tile shall comply with ASTM C 1492. 1507.3.6 Fasteners. Tile fasteners shall be corrosion resistant and not less than 11 gage, 5/16-inch (8.0 mm) head, and of sufficient length to penetrate the deck a minimum of ¾ 0.75 inch (19.1 mm) or through the thickness of the deck, whichever is less or in accordance with the FRSA/TRI Florida High Wind Concrete and Clay Roof Tile Installation Manual, Fifth Edition where the basic wind speed, Vasd, is determined in accordance with Section 1609.3.1 or in accordance with RAS 118, 119 or 120. Attaching wire for clay or concrete tile shall not be smaller than 0.083 inch (2.1 mm). Perimeter fastening areas include three tile courses but not less than 36 inches (914 mm) from either side of hips or ridges and edges of eaves and gable rakes. 1507.3.7 Attachment. Clay and concrete roof tiles shall be fastened in accordance with Table 1507.3.7Section 1609 or in accordance with FRSA/TRI Florida High Wind Concrete and Clay Roof Tile Installation Manual, Fifth Edition where the basic wind speed, Vasd, is determined in accordance with Section 1609.3.1. . TABLE 1507.3.7 CLAY AND CONCRETE TILE ATTACHMENTa, b, c Reserved. GENERAL - CLAY OR CONCRETE ROOF TILE. Maximum Nominal Design Wind Speed, Vasdf (mph); Mean roof height (feet); Roof slope < 3:12; Roof slope 3:12 and over. 85; 0-60; One fastener per tile. Flat tile without vertical laps, two fasteners per tile.; Two fasteners per tile. Only one fastener on slopes of 7:12 and less for tiles with installed weight exceeding 7.5 lbs./sq. ft. having a width no greater than 16 inches.. 100; 0-40. 100; >40-60; The head of all tiles shall be nailed. The nose of all eave tiles shall be fastened with approved clips. All rake tiles shall be nailed with two nails. The nose of all ridge, hip and rake tiles shall be set in a bead of roofer's mastic.. 110; 0-60; The fastening system shall resist the wind forces in Section 1609.5.3.. 120; 0-60; The fastening system shall resist the wind forces in Section 1609.5.3.. 130; 0-60; The fastening system shall resist the wind forces in Section 1609.5.3.. All; >60; The fastening system shall resist the wind forces in Section 1609.5.3.. INTERLOCKING CLAY OR CONCRETE ROOF TILE WITH PROJECTING ANCHOR LUGSd, e (Installations on spaced/solid sheathing with battens or spaced sheathing). Maximum Nominal Design Wind Speed, Vasdf (mph); Mean roof height (feet); Roof slope < 5:12; Roof slope 5:12 < 12:12; Roof slope 12:12 and over. 85; 0-60; Fasteners are not required. Tiles with installed weight less than 9 lbs./sq. ft. require a minimum of one fastener per tile.; One fastener per tile every other row. All perimeter tiles require one fastener. Tiles with installed weight less than 9 lbs./sq. ft. require a minimum of one fastener per tile.; One fastener required for every tile. Tiles with installed weight less than 9 lbs./sq. ft. require a minimum of one fastener per tile.. 100; 0-40. 100; >40-60; The head of all tiles shall be nailed. The nose of all eave tiles shall be fastened with approved clips. All rake tiles shall be nailed with two nails The nose of all ridge, hip and rake tiles shall be set in a bead of roofer's mastic.. 110; 0-60; The fastening system shall resist the wind forces in Section 1609.5.3.. 120; 0-60; The fastening system shall resist the wind forces in Section 1609.5.3.. 130; 0-60; The fastening system shall resist the wind forces in Section 1609.5.3.. All; >60; The fastening system shall resist the wind forces in Section 1609.5.3.. INTERLOCKING CLAY OR CONCRETE ROOF TILE WITH PROJECTING ANCHOR LUGS (Installations on solid sheathing without battens). Maximum Nominal Design Wind Speed, Vasdf (mph); Mean roof height (feet); All roof slopes. 85; 0-60; One fastener per tile.. 100; 0-40; One fastener per tile.. 100; > 40-60; The head of all tiles shall be nailed. The nose of all eave tiles shall be fastened with approved clips. All rake tiles shall be nailed with two nails The nose of all ridge, hip and rake tiles shall be set in a bead of roofer's mastic.. 110; 0-60; The fastening system shall resist the wind forces in Section 1609.5.3.. 120; 0-60; The fastening system shall resist the wind forces in Section 1609.5.3.. 130; 0-60; The fastening system shall resist the wind forces in Section 1609.5.3.. All; > 60; The fastening system shall resist the wind forces in Section 1609.5.3.. For SI: 1 inch =25.4 mm, 1 foot = 304.8 mm, 1 mile per hour = 0.447 m/s, 1 pound per square foot = 4.882 kg/m2.. a. Minimum fastener size. Corrosion-resistant nails not less than No. 11 gage with 5/16-inch head. Fasteners shall be long enough to penetrate into the sheathing 3/4 inch or through the thickness of the sheathing, whichever is less. Attaching wire for clay and concrete tile shall not be smaller than 0.083 inch.. b. Snow areas. A minimum of two fasteners per tile are required or battens and one fastener.. c. Roof slopes greater than 24:12. The nose of all tiles shall be securely fastened.. d. Horizontal battens. Battens shall be not less than 1 inch by 2 inch nominal. Provisions shall be made for drainage by a minimum of 1/8-inch riser at each nail or by 4-foot-long battens with at least a 1/2-inch separation between battens. Horizontal battens are required for slopes over 7:12.. e. Perimeter fastening areas include three tile courses but not less than 36 inches from either side of hips or ridges and edges of eaves and gable rakes.. f. Vasd shall be determined in accordance with Section 1609.3.1.. 1507.3.8 Application. Tile shall be applied according to the manufacturer's installation instructions or recommendations of the FRSA/TRI Florida High Wind Concrete and Clay Roof Tile Installation Manual, Fifth Edition where the basic wind speed, Vasd, is determined in accordance with Section 1609.3.1 or the recommendation of RAS 118, 119 or 120., based on the following: 1. Climatic conditions. 2. Roof slope. 3. Underlayment system. 4. Type of tile being installed. 1507.3.9 Flashing. At the juncture of the roof vertical surfaces, flashing and counterflashing shall be provided in accordance with the manufacturer's installation instructions , and where of metal, shall not be less than 0.019-inch (0.48 mm) (No. 26 galvanized sheet gage) corrosion-resistant metal. The valley flashing shall extend at least 11 inches (279 mm) from the centerline each way and have a splash diverter rib not less than 1 inch (25 mm) high at the flow line formed as part of the flashing. Sections of flashing shall have an end lap of not less than 4 inches (102 mm). For roof slopes of three units vertical in 12 units horizontal (25-percent slope) and over, the valley flashing shall have a 36-inch-wide (914 mm) underlayment of either one layer of Type I underlayment running the full length of the valley, or a self-adhering polymer-modified bitumen sheet complying with ASTM D 1970, in addition to other required underlayment. In areas where the average daily temperature in January is 25°F (-4°C) or less or where there is a possibility of ice forming along the eaves causing a backup of water, the metal valley flashing underlayment shall be solid cemented to the roofing underlayment for slopes under seven units vertical in 12 units horizontal (58-percent slope) or self-adhering polymer-modified bitumen sheet shall be installed or the recommendations of the FRSA/TRI Florida High Wind Concrete and Clay Roof Tile Installation Manual, Fifth Edition where the basic wind speed, Vasd, is determined in accordance with Section 1609.3.1 or the recommendation of RAS 118, 119 or 120.

(Mod R5587-A1 / AM)

Section 1507 – Requirements for Roof Coverings

Change Section 1507.4 to read as shown:

1507.4 Metal roof panels. The installation of metal roof panels shall comply with the provisions of this section. 1507.4.1 Deck requirements. Metal roof panel roof coverings shall be applied to a solid or closely fitted deck, except where the roof covering is specifically designed to be applied to spaced supports. 1507.4.2 Deck slope. Minimum slopes for metal roof panels shall comply with the following: 1. The minimum slope for lapped, nonsoldered seam metal roofs without applied lap sealant shall be three units vertical in 12 units horizontal (25-percent slope). 2. The minimum slope for lapped, nonsoldered seam metal roofs with applied lap sealant shall be one-half unit vertical in 12 units horizontal (4-percent slope). Lap sealants shall be applied in accordance with the approved manufacturer's installation instructions. 3. The minimum slope for standing seam of roof systems shall be one-quarter unit vertical in 12 units horizontal (2-percent slope). 1507.4.3 Material standards. Metal-sheet roof covering systems that incorporate supporting structural members shall be designed in accordance with Chapter 22. Metal-sheet roof coverings installed over structural decking shall comply with Table 1507.4.3(1). The materials used for metal-sheet roof coverings shall be naturally corrosion resistant or provided with corrosion resistance in accordance with the standards and minimum thicknesses shown in Table 1507.4.3(2). TABLE 1507.4.3(1) METAL ROOF COVERINGS ROOF COVERING TYPE; STANDARD APPLICATION RATE/THICKNESS. Aluminum; ASTM B 209, 0.024 inch minimum thickness for roll-formed panels and 0.019 inch minimum thickness for press-formed shingles.. Aluminum-zinc alloy coated steel; ASTM A 792 AZ 50. Cold-rolled copper; ASTM B 370 minimum 16 oz./sq. ft. and 12 oz./sq. ft. high yield copper for metal-sheet roof covering systems: 12 oz./sq. ft. for preformed metal shingle systems.. Copper; 16 oz./sq. ft. for metal-sheet roof-covering systems; 12 oz./sq. ft. for preformed metal shingle systems.. Galvanized steel; ASTM A 653 G-90 zinc-coateda.. Hard lead; 2 lbs./sq. ft.. Lead-coated copper; ASTM B 101. Prepainted steel; ASTM A 755. Soft lead; 3 lbs./sq. ft.. Stainless steel; ASTM A 240, 300 Series Alloys. Steel; ASTM A 924. Terne and terne-coated stainless; Terne coating of 40 lbs. per double base box, field painted where applicable in accordance with manufacturer's installation instructions.. Zinc; 0.027 inch minimum thickness; 99.995% electrolytic high grade zinc with alloy additives of copper (0.08% - 0.20%), titanium (0.07% - 0.12%) and aluminum (0.015%).. ROOF COVERING TYPE; STANDARD; STANDARD APPLICATION RATE/THICKNESS. Aluminum; ASTM B 209; 0.024 inch minimum thickness for roll-formed panels and 0.019 inch minimum thickness for press-formed shingles.. Aluminum-zinc coated steel; ASTM A 792; 0.013 inch minimum thickness, AZ 50 (coated minimum application rate). Cold-rolled copper; ASTM B 370; Minimum 16 oz/sq. ft. and 12 oz./sq. ft. high yield copper for metal-sheet roof covering systems: 12 oz/sq. ft. for preformed metal shingle systems.. Copper; ASTM B 370; 16 oz./sq. ft. for metal-sheet roof-covering systems; 12 oz./sq. ft. for preformed metal shingle systems.. Galvanized steel; ASTM A 653; 0.013 inch minimum thickness, G-90 zinc-coateda.. Hard lead; -; 2 lbs./sq. ft.. Lead-coated copper; ASTM B 101; -. Prepainted steel; ASTM A 755; -. Soft lead; 3 lbs./sq. ft.. Stainless steel; ASTM A 240; 300 Series Alloys. Steel; ASTM A 924/ ASTM A 924M; -. Terne and terne-coated stainless; -; Terne coating of 40 lbs. per double base box, field painted where applicable in accordance with manufacturer's installation instructions.. Zinc; -; 0.027 inch minimum thickness; 99.995% electrolytic high grade zinc with alloy additives of copper (0.08% - 0.20%), titanium (0.07% - 0.12%) and aluminum (0.015%).. For SI: 1 ounce per square foot = 0.0026 kg/m2,. 1 pound per square foot = 4.882 kg/m2,. 1 inch = 25.4 mm, 1 pound = 0.454 kg.. a. For Group U buildings, the minimum coating thickness for ASTM A 653 galvanized steel roofing shall be G-60.. TABLE 1507.4.3(2) MINIMUM CORROSION RESISTANCE 55% Aluminum-zinc alloy coated steel; ASTM A 792 AZ 50. 5% Aluminum alloy-coated steel; ASTM A 875 GF60. Aluminum-coated steel; ASTM A 463 T2 65. Galvanized steel; ASTM A 653 G-90. Prepainted steel; ASTM A 755a. a. Paint systems in accordance with ASTM A 755 shall be applied over steel products with corrosion-resistant coatings complying with ASTM A 792, ASTM A 875, ASTM A 463 or ASTM A 653.. 1507.4.4 Attachment. Metal roof panels shall be secured to the supports in accordance with the approved manufacturer's fasteners. In the absence of manufacturer recommendations, the following fasteners shall be used: 1. Galvanized fasteners shall be used for steel roofs. 2. Copper, brass, bronze, copper alloy or 300 series stainless-steel fasteners shall be used for copper roofs. 3. Aluminum-zinc coated fasteners are acceptable for aluminum-zinc coated roofs. 4. Stainless-steel fasteners are acceptable for all types of metal roofs. 1507.4.5 Underlayment and high wind. Reserved. Underlayment applied in areas subject to high winds [Vasd greater than 110 mph (49 m/s) as determined in accordance with Section 1609.3.1] shall be applied with corrosion-resistant fasteners in accordance with the manufacturer's installation instructions. Fasteners are to be applied along the overlap not farther apart than 36 inches (914 mm) on center. Underlayment installed where Vasd, in accordance with Section 1609.3.1, equals or exceeds 120 mph (54 m/s) shall comply with ASTM D 226 Type II, ASTM D 4869 Type IV, or ASTM D 1970. The underlayment shall be attached in a grid pattern of 12 inches (305 mm) between side laps with a 6-inch (152 mm) spacing at the side laps. Underlayment shall be applied in accordance with the manufacturer's installation instructions except all laps shall be a minimum of 4 inches (102 mm). Underlayment shall be attached using metal or plastic cap nails with a head diameter of not less than 1 inch (25 mm) with a thickness of at least 32-gauge [0.0134 inch (0.34 mm)] sheet metal. The cap nail shank shall be a minimum of 12 gauge [0.105 inch (2.67 mm)] with a length to penetrate through the roof sheathing or a minimum of 3/4 inch (19.1 mm) into the roof sheathing. Exception: As an alternative, adhered underlayment complying with ASTM D 1970 shall be permitted. 1507.4.5.1 Underlayment. Underlayment shall comply with ASTM D 226, Type I or Type II or ASTM D 4869, Type II or Type IV or ASTM D 1970 or ASTM D 6757. 1507.4.5.2 Underlayment Application. Underlayment shall be installed using one of the following methods: - Two layer underlayment shall comply with ASTM D 226, Type I or Type II or ASTM D 4869, Type II or Type IV or ASTM D 6757: Apply a 19-inch (483 mm) strip of underlayment felt parallel to and starting at the eaves, fastened sufficiently to hold in place. Starting at the eave, apply 36-inch-wide (914 mm) sheets of underlayment, overlapping successive sheets 19 inches (483 mm), and fastened with 1 inch (25 mm) round plastic cap, metal cap nails or nails and tin-tabs attached to a nailable deck with one row in the field of the sheet with a maximum fastener spacing of 12 in. o.c. (305 mm), and one row at the overlaps fastened 6 in. o.c. (152 mm). Synthetic underlayment shall be fastened in accordance with this section and the manufacturer’s recommendations. - One layer underlayment shall comply with ASTM D 226, Type II or ASTM D 4869, Type IV or ASTM D 6757: Underlayment shall be applied shingle fashion, parallel to and starting from the eave and lapped 2 inches (51 mm), fastened with 1 inch (25 mm) round plastic cap, metal cap nails or nails and tin-tabs attached to a nailable deck with two staggered rows in the field of the sheet with a maximum fastener spacing of 12 in. o.c. (305 mm), and one row at the overlaps fastened 6 in. o.c. (152 mm). Synthetic underlayment shall be fastened in accordance with this section and the manufacturer’s recommendations End laps shall be offset by 6 feet (1829 mm). - As an alternative, the entire roof deck shall be covered with an approved self-adhering polymer modified bitumen sheet meeting ASTM D 1970 or an approved self-adhering synthetic underlayment installed in accordance with the manufacturer’s installation instructions.

(Mod R5275-A1 / AM)

Section 1507 – Requirements for Roof Coverings

Change Section 1507.5.2 to read as shown:

Section 1507.5.2. Add a section to read as shown:

1507.5.2.1 Underlayment shall be installed as per manufacturer's installation guidelines.

(Mod R5387 / AS)

Section 1507 – Requirements for Roof Coverings

Change Section 1507.5.3 to read as shown:

Section 1507.5.3 Underlayment. Change to read as shown:

1507.5.3 Underlayment. Underlayment shall comply with ASTM D 226, Type I or Type II or ASTM D 4869, Type II or Type IV or ASTM D 1970 or ASTM D 6757.

1507.5.3.1 Underlayment and high wind. Reserved. 
Underlayment applied in areas subject to high winds [Vasd greater than 110 mph (49 m/s) as determined in accordance with Section 1609.3.1] shall be applied with corrosion-resistant fasteners in accordance with the manufacturer's installation instructions. Fasteners are to be applied along the overlap not farther apart than 36 inches (914 mm) on center. 
Underlayment installed where Vasd, in accordance with Section 1609.3.1, equals or exceeds 120 mph (54 m/s) shall comply with ASTM D 226 Type II or ASTM D 4869 Type IV. The underlayment shall be attached in a grid pattern of 12 inches (305 mm) between side laps with a 6-inch spacing (152 mm) at the side laps. Underlayment shall be applied in accordance with the manufacturer's installation instructions except all laps shall be a minimum of 4 inches (102 mm). Underlayment shall be attached using metal or plastic cap nails with a head diameter of not less than 1 inch (25 mm) with a thickness of at least 32-gauge [0.0134 inch (0.34 mm)] sheet metal. The cap nail shank shall be a minimum of 12 gauge [0.105 inch (2.67 mm)] with a length to penetrate through the roof sheathing or a minimum of 3/4 inch (19.1 mm) into the roof sheathing. 
Exception: As an alternative, adhered underlayment complying with ASTM D 1970 shall be permitted.

1507.5.3.2 Underlayment Application. Underlayment shall be installed using one of the following methods:

- Two layer underlayment shall comply with ASTM D 226, Type I or Type II or ASTM D 4869, Type II or Type IV or ASTM D 6757: Apply a 19-inch (483 mm) strip of underlayment felt parallel to and starting at the eaves, fastened sufficiently to hold in place. Starting at the eave, apply 36-inch-wide (914 mm) sheets of underlayment, overlapping successive sheets 19 inches (483 mm), and fastened with 1 inch (25 mm) round plastic cap, metal cap nails or nails and tin-tabs attached to a nailable deck with one row in the field of the sheet with a maximum fastener spacing of 12 in. o.c. (305 mm), and one row at the overlaps fastened 6 in. o.c. (152 mm). Synthetic underlayment shall be fastened in accordance with this section and the manufacturer’s recommendations.

- One layer underlayment shall comply with ASTM D 226, Type II or ASTM D 4869, Type IV or ASTM D 6757: Underlayment shall be applied shingle fashion, parallel to and starting from the eave and lapped 2 inches (51 mm), fastened with 1 inch (25 mm) round plastic cap, metal cap nails or nails and tin-tabs attached to a nailable deck with two staggered rows in the field of the sheet with a maximum fastener spacing of 12 in. o.c. (305 mm), and one row at the overlaps fastened 6 in. o.c. (152 mm). Synthetic underlayment shall be fastened in accordance with this section and the manufacturer’s recommendations End laps shall be offset by 6 feet (1829 mm).

- As an alternative, the entire roof deck shall be covered with an approved self-adhering polymer modified bitumen sheet meeting ASTM D 1970 or an approved self-adhering synthetic underlayment installed in accordance with the manufacturer’s installation instructions.

(Mod R5564 / AS)

Section 1507 – Requirements for Roof Coverings Change Section 1507.5.4 to read as shown: Section 1507.5.4 Ice barrier. Change to read as shown: 1507.5.4 Ice barrier. Reserved. In areas where there has been a history of ice forming along the eaves causing a backup of water, an ice barrier that consists of at least two layers of underlayment cemented together or of a self-adhering polymer-modified bitumen sheet shall be used in lieu of normal underlayment and extend from the lowest edges of all roof surfaces to a point at least 24 inches (610 mm) inside the exterior wall line of the building. Exception: Detached accessory structures that contain no conditioned floor area. (Mod R5389 / AS) Section 1507 – Requirements for Roof Coverings Change Section 1507.5.7 to read as shown: 1507.5.7 Flashing. Roof valley flashing shall be of corrosion-resistant metal of the same material as the roof covering or shall comply with the standards in Table 1507.4.3(1). The valley flashing shall extend at least 8 inches (203 mm) from the centerline each way and shall have a splash diverter rib not less than 3/4 0.75 inch (19.1 mm) high at the flow line formed as part of the flashing. Sections of flashing shall have an end lap of not less than 4 inches (102 mm). In areas where the average daily temperature in January is 25°F (-4°C) or less or where there is a possibility of ice forming along the eaves causing a backup of water, the metal valley flashing shall have a 36-inch-wide (914 mm) underlayment directly under it consisting of either one layer of underlayment running the full length of the valley or a self-adhering polymer-modified bitumen sheet complying with ASTM D 1970, in addition to underlayment required for metal roof shingles. The metal valley flashing underlayment shall be solidly cemented to the roofing underlayment for roof slopes under seven units vertical in 12 units horizontal (58-percent slope) or self-adhering polymer-modified bitumen sheet shall be installed. (Mod R5390 / AS)

Section 1507 – Requirements for Roof Coverings

Change Section 1507.6 to read as shown:

1507.6 Mineral-surfaced roll roofing. The installation of mineral-surfaced roll roofing shall comply with this section.

1507.6.1 Deck requirements. Mineral-surfaced roll roofing shall be fastened to solidly sheathed roofs.

1507.6.2 Deck slope. Mineral-surfaced roll roofing shall not be applied on roof slopes below one unit vertical in 12 units horizontal (8-percent slope).

1507.6.3 Underlayment. Underlayment shall comply with ASTM D 226, Type I or Type II, ASTM D 4869, Type II or Type IV or ASTM D 1970 or ASTM D 6757.

1507.6.3.1 Underlayment and high wind. Underlayment applied in areas subject to high winds [Vasd greater than 110 mph (49 m/s) as determined in accordance with Section 1609.3.1] shall be applied with corrosion-resistant fasteners in accordance with the manufacturer's installation instructions. Fasteners are to be applied along the overlap not farther apart than 36 inches (914 mm) on center. 

Underlayment installed where Vasd, in accordance with Section 1609.3.1, equals or exceeds 120 mph (54 m/s) shall comply with ASTM D 226 Type II or ASTM D 4869 Type IV. The underlayment shall be attached in a grid pattern of 12 inches (305 mm) between side laps with a 6-inch spacing (152 mm) at the side laps. Underlayment shall be applied in accordance with the manufacturer's installation instructions except all laps shall be a minimum of 4 inches (102 mm). Underlayment shall be attached using metal or plastic cap nails with a head diameter of not less than 1 inch (25 mm) with a thickness of at least 32-gauge [0.0134 inch (0.34 mm)] sheet metal. The cap nail shank shall be a minimum of 12 gauge [0.105 inch (2.67 mm)] with a length to penetrate through the roof sheathing or a minimum of 3/4 inch (19.1 mm) into the roof sheathing. 

Exception: As an alternative, adhered underlayment complying with ASTM D 1970 shall be permitted. Reserved.

1507.6.3.2 Underlayment Application. Underlayment shall be installed using one of the following methods:

1.      Two layer underlayment shall comply with ASTM D 226, Type I or Type II or ASTM D 4869, Type II or Type IV or ASTM D 6757: Apply a 19-inch (483 mm) strip of underlayment felt parallel to and starting at the eaves, fastened sufficiently to hold in place. Starting at the eave, apply 36-inch-wide (914 mm) sheets of underlayment, overlapping successive sheets 19 inches (483 mm), and fastened with 1 inch (25 mm) round plastic cap, metal cap nails or nails and tin-tabs attached to a nailable deck with one row in the field of the sheet with a maximum fastener spacing of 12 in. o.c. (305 mm), and one row at the overlaps fastened 6 in. o.c. (152 mm). Synthetic underlayment shall be fastened in accordance with this section and the manufacturer’s recommendations.

2.      One layer underlayment shall comply with ASTM D 226, Type II or ASTM D 4869, Type IV or ASTM D 6757: Underlayment shall be applied shingle fashion, parallel to and starting from the eave and lapped 2 inches (51 mm), fastened with 1 inch (25 mm) round plastic cap, metal cap nails or nails and tin-tabs attached to a nailable deck with two staggered rows in the field of the sheet with a maximum fastener spacing of 12 in. o.c. (305 mm), and one row at the overlaps fastened 6 in. o.c. (152 mm). Synthetic underlayment shall be fastened in accordance with this section and the manufacturer’s recommendations End laps shall be offset by 6 feet (1829 mm).

3.      As an alternative, the entire roof deck shall be covered with an approved self-adhering polymer modified bitumen sheet meeting ASTM D 1970 or an approved self-adhering synthetic underlayment installed in accordance with the manufacturer’s installation instructions.

1507.6.4 Ice barrier. In areas where there has been a history of ice forming along the eaves causing a backup of water, an ice barrier that consists of at least two layers of underlayment cemented together or of a self-adhering polymer-modified bitumen sheet shall be used in lieu of normal underlayment and extend from the lowest edges of all roof surfaces to a point at least 24 inches (610 mm) inside the exterior wall line of the building. 

Exception: Detached accessory structures that contain no conditioned floor area. Reserved.

1507.6.5 Material standards. Mineral-surfaced roll roofing shall conform to ASTM D 3909 or ASTM D 6380 Class M or Class WS.

(Mod R5278 / AM)

Section 1507 – Requirements for Roof Coverings

Change Section 1507.7 to read as shown:

1507.7 Slate shingles. The installation of slate shingles shall comply with the provisions of this section.

1507.7.1 Deck requirements. Slate shingles shall be fastened to solidly sheathed roofs.

1507.7.2 Deck slope. Slate shingles shall only be used on slopes of four units vertical in 12 units horizontal (4:12) or greater.

1507.7.3 Underlayment. Underlayment shall comply with ASTM D 226, Type I or Type II, ASTM D 4869, Type II or Type IV or ASTM D 1970 or ASTM D 6757.

1507.7.3.1 Underlayment and high wind. Reserved.
Underlayment applied in areas subject to high winds [Vasd greater than 110 mph (49 m/s) as determined in accordance with Section 1609.3.1] shall be applied with corrosion-resistant fasteners in accordance with the manufacturer's installation instructions. Fasteners are to be applied along the overlap not farther apart than 36 inches (914 mm) on center. 

Underlayment installed where Vasd, in accordance with Section 1609.3.1, equals or exceeds 120 mph (54 m/s) shall comply with ASTM D 226 Type II or ASTM D 4869 Type IV. The underlayment shall be attached in a grid pattern of 12 inches (305 mm) between side laps with a 6-inch spacing (152 mm) at the side laps. Underlayment shall be applied in accordance with the manufacturer's installation instructions except all laps shall be a minimum of 4 inches (102 mm). Underlayment shall be attached using metal or plastic cap nails with a head diameter of not less than 1 inch (25 mm) with a thickness of at least 32-gauge [0.0134 inch (0.34 mm)] sheet metal. The cap nail shank shall be a minimum of 12 gauge [0.105 inch (2.67 mm)] with a length to penetrate through the roof sheathing or a minimum of 3/4 inch (19.1 mm) into the roof sheathing. 
Exception: As an alternative, adhered underlayment complying with ASTM D 1970 shall be permitted.

1507.7.3.2 Underlayment Application. Underlayment shall be installed using one of the following methods:

1.      Two layer underlayment shall comply with ASTM D 226, Type I or Type II or ASTM D 4869, Type II or Type IV or ASTM D 6757: Apply a 19-inch (483 mm) strip of underlayment felt parallel to and starting at the eaves, fastened sufficiently to hold in place. Starting at the eave, apply 36-inch-wide (914 mm) sheets of underlayment, overlapping successive sheets 19 inches (483 mm), and fastened with 1 inch (25 mm) round plastic cap, metal cap nails or nails and tin-tabs attached to a nailable deck with one row in the field of the sheet with a maximum fastener spacing of 12 in. o.c. (305 mm), and one row at the overlaps fastened 6 in. o.c. (152 mm). Synthetic underlayment shall be fastened in accordance with this section and the manufacturer’s recommendations.

2.      One layer underlayment shall comply with ASTM D 226, Type II or ASTM D 4869, Type IV or ASTM D 6757: Underlayment shall be applied shingle fashion, parallel to and starting from the eave and lapped 2 inches (51 mm), fastened with 1 inch (25 mm) round plastic cap, metal cap nails or nails and tin-tabs attached to a nailable deck with two staggered rows in the field of the sheet with a maximum fastener spacing of 12 in. o.c. (305 mm), and one row at the overlaps fastened 6 in. o.c. (152 mm). Synthetic underlayment shall be fastened in accordance with this section and the manufacturer’s recommendations End laps shall be offset by 6 feet (1829 mm).

3.      As an alternative, the entire roof deck shall be covered with an approved self-adhering polymer modified bitumen sheet meeting ASTM D 1970 or an approved self-adhering synthetic underlayment installed in accordance with the manufacturer’s installation instructions.

1507.7.4 Ice barrier. Reserved.
In areas where the average daily temperature in January is 25°F (-4°C) or less or where there is a possibility of ice forming along the eaves causing a backup of water, an ice barrier that consists of at least two layers of underlayment cemented together or of a self-adhering polymer-modified bitumen sheet shall extend from the lowest edges of all roof surfaces to a point at least 24 inches (610 mm) inside the exterior wall line of the building. 

Exception: Detached accessory structures that contain no conditioned floor area.

1507.7.5 Material standards. Slate shingles shall comply with ASTM C 406.

1507.7.6 Application. Minimum headlap for slate shingles shall be in accordance with Table 1507.7.6. Slate shingles shall be secured to the roof with two fasteners per slate.

TABLE 1507.7.6

SLATE SHINGLE HEADLAP

| SLOPE | HEADLAP (inches) |
| --- | --- |
| 4:12 < slope < 8:12 | 4 |
| 8:12 < slope < 20:12 | 3 |
| slope = 20:12 | 2 |
| For SI: 1 inch = 25.4 mm. |  |

1507.7.7 Flashing. Flashing and counterflashing shall be made with sheet metal. Valley flashing shall be a minimum of 15 16 inches (381 mm) wide. Valley and flashing metal shall be a minimum uncoated thickness of 0.0179-inch (0.455 mm) zinc-coated G90 thickness provided in Table 1503.2 nonferrous metal or stainless steel. Chimneys, stucco or brick walls shall have a minimum of two plies of felt for a cap flashing consisting of a 4-inch-wide (102 mm) strip of felt set in plastic cement and extending 1 inch (25 mm) above the first felt and a top coating of plastic cement. The felt shall extend over the base flashing 2 inches (51 mm).

(Mod R5281-R1 / AM)

Section 1507 – Requirements for Roof Coverings

Change Section 1507.8 to read as shown:

1507.8 Wood shingles. The installation of wood shingles shall comply with the provisions of this section and Table 1507.8. TABLE 1507.8 WOOD SHINGLE AND SHAKE INSTALLATION ROOF ITEM; WOOD SHINGLES; WOOD SHAKES. 1. Roof slope; Wood shingles shall be installed on slopes of three units vertical in 12 units horizontal (3:12) or greater.; Wood shakes shall be installed on slopes of four units vertical in 12 units horizontal (4:12) or greater.. 2. Deck requirement. Temperate climate; Shingles shall be applied to roofs with solid or spaced sheathing. Where spaced sheathing is used, sheathing boards shall not be less than 1” × 4” nominal dimensions and shall be spaced on center equal to the weather exposure to coincide with the placement of fasteners.; Shakes shall be applied to roofs with solid or spaced sheathing. Where spaced sheathing is used, sheathing boards shall not be less than 1” × 4” nominal dimensions and shall be spaced on center equal to the weather exposure to coincide with the placement of fasteners. When 1” × 4” spaced sheathing is installed at 10 inches, boards must be installed between the sheathing boards.. In areas where the average daily temperature in January is 25°F or less or where there is a possibility of ice forming along the eaves causing a backup of water.; Solid sheathing required.; Solid sheathing is required.. 3. Interlayment; No requirements.; Interlayment shall comply with ASTM D 226, Type 1.. 4. Underlayment. Temperate climate; Underlayment shall comply with ASTM D 226, Type 1.; Underlayment shall comply with ASTM D 226, Type 1.. In areas where there is a possibility of ice forming along the eaves causing a backup of water.; An ice barrier that consists of at least two layers of underlayment cemented together or of a self-adhering polymer-modified bitumen sheet shall extend from the eave's edge to a point at least 24 inches inside the exterior wall line of the building.; An ice barrier that consists of at least two layers of underlayment cemented together or of a self-adhering polymer-modified bitumen sheet shall extend from the lowest edges of all roof surfaces to a point at least 24 inches inside the exterior wall line of the building.. 5. Application. Attachment; Fasteners for wood shingles shall be hot-dipped galvanized or Type 304 (Type 316 for coastal areas) stainless steel with a minimum penetration of 0.75 inch into the sheathing. For sheathing less than 0.5 inch thick, the fasteners shall extend through the sheathing.; Fasteners for wood shakes shall be hot-dipped galvanized or Type 304 (Type 316 for coastal areas) with a minimum penetration of 0.75 inch into the sheathing. For sheathing less than 0.5 inch thick, the fasteners shall extend through the sheathing.. No. of fasteners; Two per shingle.; Two per shake.. Exposure; Weather exposures shall not exceed those set forth in Table 1507.8.7.; Weather exposures shall not exceed those set forth in Table 1507.9.8.. Method; Shingles shall be laid with a side lap of not less than 1.5 inches between joints in courses, and no two joints in any three adjacent courses shall be in direct alignment. Spacing between shingles shall be 0.25 to 0.375 inch.; Shakes shall be laid with a side lap of not less than 1.5 inches between joints in adjacent courses. Spacing between shakes shall not be less than 0.375 inch or more than 0.625 inch for shakes and taper sawn shakes of naturally durable wood and shall be 0.25 to 0.375 inch for preservative-treated taper sawn shakes.. Flashing; In accordance with Section 1507.8.8.; In accordance with Section 1507.9.9.. For SI: 1 inch = 25.4 mm, °C = [(°F) - 32]/1.8. 1507.8.1 Deck requirements. Wood shingles shall be installed on solid or spaced sheathing. Where spaced sheathing is used, sheathing boards shall not be less than 1-inch by 4-inch (25 mm by 102 mm) nominal dimensions and shall be spaced on centers equal to the weather exposure to coincide with the placement of fasteners. 1507.8.1.1 Solid sheathing required. Reserved. Solid sheathing is required in areas where the average daily temperature in January is 25°F (-4°C) or less or where there is a possibility of ice forming along the eaves causing a backup of water. 1507.8.2 Deck slope. Wood shingles shall be installed on slopes of three units vertical in 12 units horizontal (25-percent slope) or greater. 1507.8.3 Underlayment. Underlayment shall comply with ASTM D 226, Type I or Type II or ASTM D 4869 Type II or IV. 1507.8.3.1 Underlayment and high wind. Reserved. Underlayment applied in areas subject to high winds [Vasd greater than 110 mph (49 m/s) as determined in accordance with Section 1609.3.1] shall be applied with corrosion-resistant fasteners in accordance with the manufacturer's installation instructions. Fasteners are to be applied along the overlap not farther apart than 36 inches (914 mm) on center. Underlayment installed where Vasd, in accordance with Section 1609.3.1, equals or exceeds 120 mph (54 m/s) shall comply with ASTM D 226 Type II or ASTM D 4869 Type IV. The underlayment shall be attached in a grid pattern of 12 inches (305 mm) between side laps with a 6-inch spacing (152 mm) at the side laps. Underlayment shall be applied in accordance with the manufacturer's installation instructions except all laps shall be a minimum of 4 inches (102 mm). Underlayment shall be attached using metal or plastic cap nails with a head diameter of not less than 1 inch (25 mm) with a thickness of at least 32-gauge [0.0134 inch (0.34 mm)] sheet metal. The cap nail shank shall be a minimum of 12 gauge [0.105 inch (2.67 mm)] with a length to penetrate through the roof sheathing or a minimum of 3/4 inch (19.1 mm) into the roof sheathing. Exception: As an alternative, adhered underlayment complying with ASTM D 1970 shall be permitted. 1507.8.3.2 Underlayment Application. Underlayment shall be installed using one of the following methods: 1. Two layer underlayment shall comply with ASTM D 226, Type I or Type II or ASTM D 4869, Type II or Type IV: Apply a 19-inch (483 mm) strip of underlayment felt parallel to and starting at the eaves, fastened sufficiently to hold in place. Starting at the eave, apply 36-inch-wide (914 mm) sheets of underlayment, overlapping successive sheets 19 inches (483 mm), and fastened with 1 inch (25 mm) round plastic cap, metal cap nails or nails and tin-tabs attached to a nailable deck with one row in the field of the sheet with a maximum fastener spacing of 12 in. o.c. (305 mm), and one row at the overlaps fastened 6 in. o.c. (152 mm). 2. One layer underlayment shall comply with ASTM D 226, Type II or ASTM D 4869, Type IV: Underlayment shall be applied shingle fashion, parallel to and starting from the eave and lapped 2 inches (51 mm), fastened with 1 inch (25 mm) round plastic cap, metal cap nails or nails and tin-tabs attached to a nailable deck with two staggered rows in the field of the sheet with a maximum fastener spacing of 12 in. o.c. (305 mm), and one row at the overlaps fastened 6 in. o.c. (152 mm). End laps shall be offset by 6 feet (1829 mm). 1507.8.4 Ice barrier. Reserved. In areas where there has been a history of ice forming along the eaves causing a backup of water, an ice barrier that consists of at least two layers of underlayment cemented together or of a self-adhering polymer-modified bitumen sheet shall be used in lieu of normal underlayment and extend from the lowest edges of all roof surfaces to a point at least 24 inches (610 mm) inside the exterior wall line of the building. Exception: Detached accessory structures that contain no conditioned floor area. 1507.8.5 Material standards. Wood shingles shall be of naturally durable wood and comply with the requirements of Table 1507.8.5. TABLE 1507.8.5 WOOD SHINGLE MATERIAL REQUIREMENTS MATERIAL; APPLICABLE MINIMUM GRADES; GRADING RULES. Wood shingles of naturally durable wood; 1, 2 or 3; CSSB. CSSB = Cedar Shake and Shingle Bureau. 1507.8.6 Attachment. Fasteners for wood shingles shall be corrosion resistant with a minimum penetration of 3/4 inch (19.1 mm) into the sheathing. For sheathing less than 1/2 inch (12.7 mm) in thickness, the fasteners shall extend through the sheathing. Each shingle shall be attached with a minimum of two fasteners. 1507.8.7 Application. Wood shingles shall be laid with a side lap not less than 11/2 inches (38 mm) between joints in adjacent courses, and not be in direct alignment in alternate courses. Spacing between shingles shall be 1/4 to 3/8 inches (6.4 to 9.5 mm). Weather exposure for wood shingles shall not exceed that set in Table 1507.8.7. TABLE 1507.8.7 WOOD SHINGLE WEATHER EXPOSURE AND ROOF SLOPE ROOFING MATERIAL; LENGTH (inches); GRADE; EXPOSURE (inches). 3:12 pitch to < 4:12; 4:12 pitch or steeper. Shingles of naturally durable wood; 16; No. 1 No. 2 No. 3; 3.75 3.5 3; 5 4 3.5. 18; No. 1 No. 2 No. 3; 4.25 4 3.5; 5.5 4.5 4. 24; No. 1 No. 2 No. 3; 5.75 5.5 5; 7.5 6.5 5.5. For SI: 1 inch = 25.4 mm.. 1507.8.8 Flashing. At the juncture of the roof and vertical surfaces, flashing and counterflashing shall be provided in accordance with the manufacturer's installation instructions, and where of metal, shall not be less than 0.019-inch (0.48 mm) (No. 26 galvanized sheet gage) corrosion-resistant metal comply with Table 1503.2. The valley flashing shall extend at least 11 inches (279 mm) from the centerline each way and have a splash diverter rib not less than 1 inch (25 mm) high at the flow line formed as part of the flashing. Sections of flashing shall have an end lap of not less than 4 inches (102 mm). For roof slopes of three units vertical in 12 units horizontal (25-percent slope) and over, the valley flashing shall have a 36-inch-wide (914 mm) layer of underlayment of either one layer of Type I underlayment running the full length of the valley or a self-adhering polymer-modified bitumen sheet complying with ASTM D 1970, in addition to other required underlayment. In areas where the average daily temperature in January is 25°F (-4°C) or less or where there is a possibility of ice forming along the eaves causing a backup of water, the metal valley flashing underlayment shall be solidly cemented to the roofing underlayment for slopes under seven units vertical in 12 units horizontal (58-percent slope) or self-adhering polymer-modified bitumen sheet shall be installed.

(Mod R5286-R1 / AM)

Section 1507 – Requirements for Roof Coverings

Change Section 1507.9 to read as shown:

1507.9 Wood shakes. The installation of wood shakes shall comply with the provisions of this section and Table 1507.8.

1507.9.1 Deck requirements. Wood shakes shall only be used on solid or spaced sheathing. Where spaced sheathing is used, sheathing boards shall not be less than 1-inch by 4-inch (25 mm by 102 mm) nominal dimensions and shall be spaced on centers equal to the weather exposure to coincide with the placement of fasteners. Where 1-inch by 4-inch (25 mm by 102 mm) spaced sheathing is installed at 10 inches (254 mm) o.c., additional 1-inch by 4-inch (25 mm by 102 mm) boards shall be installed between the sheathing boards.

1507.9.1.1 Solid sheathing required. Reserved.
Solid sheathing is required in areas where the average daily temperature in January is 25°F (-4°C) or less or where there is a possibility of ice forming along the eaves causing a backup of water.

1507.9.2 Deck slope. Wood shakes shall only be used on slopes of four units vertical in 12 units horizontal (33-percent slope) or greater.

1507.9.3 Underlayment. Underlayment shall comply with ASTM D 226, Type I or Type II or ASTM D 4869, Type II or IV.

1507.9.3.1 Underlayment and high wind. Reserved.
Underlayment applied in areas subject to high winds [Vasd greater than 110 mph (49 m/s) as determined in accordance with Section 1609.3.1] shall be applied with corrosion-resistant fasteners in accordance with the manufacturer's installation instructions. Fasteners are to be applied along the overlap not farther apart than 36 inches (914 mm) on center. 

Underlayment installed where Vasd, in accordance with Section 1609.3.1, equals or exceeds 120 mph (54 m/s) shall comply with ASTM D 226 Type II or ASTM D 4869 Type IV. The underlayment shall be attached in a grid pattern of 12 inches (305 mm) between side laps with a 6-inch spacing (152 mm) at the side laps. Underlayment shall be applied in accordance with the manufacturer's installation instructions except all laps shall be a minimum of 4 inches (102 mm). Underlayment shall be attached using metal or plastic cap nails with a head diameter of not less than 1 inch (25 mm) with a thickness of at least 32-gauge [0.0134 inch (0.34 mm)] sheet metal. The cap nail shank shall be a minimum of 12 gauge [0.105 inch (2.67 mm)] with a length to penetrate through the roof sheathing or a minimum of 3/4 inch (19.1 mm) into the roof sheathing. 
Exception: As an alternative, adhered underlayment complying with ASTM D 1970 shall be permitted.

1507.9.3.2 Underlayment Application. Underlayment shall be installed using one of the following methods:

1.      Two layer underlayment shall comply with ASTM D 226, Type I or Type II or ASTM D 4869, Type II or Type IV: Apply a 19-inch (483 mm) strip of underlayment felt parallel to and starting at the eaves, fastened sufficiently to hold in place. Starting at the eave, apply 36-inch-wide (914 mm) sheets of underlayment, overlapping successive sheets 19 inches (483 mm), and fastened with 1 inch (25 mm) round plastic cap, metal cap nails or nails and tin-tabs attached to a nailable deck with one row in the field of the sheet with a maximum fastener spacing of 12 in. o.c. (305 mm), and one row at the overlaps fastened 6 in. o.c. (152 mm).

2.      One layer underlayment shall comply with ASTM D 226, Type II or ASTM D 4869, Type IV: Underlayment shall be applied shingle fashion, parallel to and starting from the eave and lapped 2 inches (51 mm), fastened with 1 inch (25 mm) round plastic cap, metal cap nails or nails and tin-tabs attached to a nailable deck with two staggered rows in the field of the sheet with a maximum fastener spacing of 12 in. o.c. (305 mm), and one row at the overlaps fastened 6 in. o.c. (152 mm). End laps shall be offset by 6 feet (1829 mm).

1507.9.4 Ice barrier. Reserved.
In areas where there has been a history of ice forming along the eaves causing a backup of water, an ice barrier that consists of at least two layers of underlayment cemented together or of a self-adhering polymer-modified bitumen sheet shall be used in lieu of normal underlayment and extend from the lowest edges of all roof surfaces to a point at least 24 inches (610 mm) inside the exterior wall line of the building. 
Exception: Detached accessory structures that contain no conditioned floor area.

1507.9.5 Interlayment. Interlayment shall comply with ASTM D 226, Type I.

1507.9.6 Material standards. Wood shakes shall comply with the requirements of Table 1507.9.6.

TABLE 1507.9.6

WOOD SHAKE MATERIAL REQUIREMENTS

| MATERIAL | MINIMUM GRADES |  | APPLICABLE GRADING RULES |  |
| --- | --- | --- | --- | --- |
| Wood shakes of naturally durable wood | 1 |  | CSSB |  |
| Taper sawn shakes of naturally durable wood | 1 or 2 |  | CSSB |  |
| Preservative-treated shakes and shingles of naturally durable wood | 1 |  | CSSB |  |
| Fire-retardant-treated shakes and shingles of naturally durable wood | 1 |  | CSSB |  |
| Preservative-treated taper sawn shakes of Southern pine treated in accordance with AWPA U1 (Commodity Specification A, Use Category 3B and Section 5.6) | 1 or 2 |  | TFS |  |
| CSSB = Cedar Shake and Shingle Bureau. |  |  |  |  |
| TFS = Forest Products Laboratory of the Texas Forest Services. |  |  |  |  |

1507.9.7 Attachment. Fasteners for wood shakes shall be corrosion resistant with a minimum penetration of 3/4 inch (19.1 mm) into the sheathing. For sheathing less than1/2 inch (12.7 mm) in thickness, the fasteners shall extend through the sheathing. Each shake shall be attached with a minimum of two fasteners.

1507.9.8 Application. Wood shakes shall be laid with a side lap not less than 11/2 inches (38 mm) between joints in adjacent courses. Spacing between shakes in the same course shall be 3/8 to 5/8 inches (9.5 to 15.9 mm) for shakes and taper sawn shakes of naturally durable wood and shall be 1/4 to 3/8 inch (6.4 to 9.5 mm) for preservative taper sawn shakes. Weather exposure for wood shakes shall not exceed those set in Table 1507.9.8.

1507.9.9 Flashing. At the juncture of the roof and vertical surfaces, flashing and counterflashing shall be provided in accordance with the manufacturer's installation instructions, and where of metal, shall not be less than 0.019-inch (0.48 mm) (No. 26 galvanized sheet gage) corrosion-resistant metal comply with Table 1503.2. The valley flashing shall extend at least 11 inches (279 mm) from the centerline each way and have a splash diverter rib not less than 1 inch (25 mm) high at the flow line formed as part of the flashing. Sections of flashing shall have an end lap of not less than 4 inches (102 mm). For roof slopes of three units vertical in 12 units horizontal (25-percent slope) and over, the valley flashing shall have a 36-inch-wide (914 mm) layer of underlayment of either one layer of Type I underlayment running the full length of the valley or a self-adhering polymer-modified bitumen sheet complying with ASTM D 1970, in addition to other required underlayment. In areas where the average daily temperature in January is 25°F (-4°C) or less or where there is a possibility of ice forming along the eaves causing a backup of water, the metal valley flashing underlayment shall be solidly cemented to the roofing underlayment for slopes under seven units vertical in 12 units horizontal (58-percent slope) or self-adhering polymer-modified bitumen sheet shall be installed.

(Mod R5284 – R1 / AM)

Section 1507 – Requirements for Roof Coverings

Change Section 1507.10 to read as shown:

1507.10 Built-up roofs. The installation of built-up roofs shall comply with the provisions of this section.

1507.10.1 Slope. Built-up roofs shall have a design slope of a minimum of one-fourth unit vertical in 12 units horizontal (2-percent slope) for drainage, except for coal-tar built-up roofs that shall have a design slope of a minimum one-eighth unit vertical in 12 units horizontal (1-percent slope).

1507.10.2 Material standards. Built-up roof covering materials shall comply with the standards in Table 1507.10.2 or UL 55A.

TABLE 1507.10.2

BUILT-UP ROOFING MATERIAL STANDARDS

| MATERIAL STANDARD | STANDARD |
| --- | --- |
| Acrylic coatings used in roofing | ASTM D 6083 |
| Aggregate surfacing | ASTM D 1863 |
| Asphalt adhesive used in roofing | ASTM D 3747 |
| Asphalt cements used in roofing | ASTM D 3019; D 2822; D 4586 |
| Asphalt-coated glass fiber base sheet | ASTM D 4601 |
| Asphalt coatings used in roofing | ASTM D 1227; D 2823; D 2824; D 4479 |
| Asphalt glass felt | ASTM D 2178 |
| Asphalt primer used in roofing | ASTM D 41 |
| Asphalt-saturated and asphalt-coated organic felt base sheet | ASTM D 2626 |
| Asphalt-saturated organic felt (perforated) | ASTM D 226 |
| Asphalt used in roofing | ASTM D 312 |
| Coal-tar cements used in roofing | ASTM D 4022; D 5643 |
| Coal-tar saturated organic felt | ASTM D 227 |
| Coal-tar pitch used in roofing | ASTM D 450; Type I or II |
| Coal-tar primer used in roofing, dampproofing and waterproofing | ASTM D 43 |
| Glass mat, coal tar | ASTM D 4990 |
| Glass mat, venting type | ASTM D 4897 |
| Mineral-surfaced inorganic cap sheet | ASTM D 3909 |
| Thermoplastic fabrics used in roofing | ASTM D 5665, D 5726 |

1507.10.3 Red rosin paper. Red rosin paper shall be used when the membrane is applied directly to a wood deck or cementitious fiber decks.

(Mod R5270 / AS)

Section 1507 – Requirements for Roof Coverings

Change Section 1507.17 to read as shown:

Section 1507.17 Photovoltaic modules/shingles. Change to read as shown:

1507.17 Photovoltaic modules/shingles. The installation Building integrated P photovoltaic roofing modules/shingles. The installation of building integrated P photovoltaic roofing modules/shingles shall comply with the provisions of this section.

1507.17.1 Material standards. Building integrated P photovoltaic roofing modules/shingles shall be listed and labeled in accordance with UL 1703.

1507.17.2 Attachment. Building integrated P photovoltaic roofing modules/shingles shall be attached in accordance with the manufacturer's installation instructions.

1507.17.3 Wind resistance. Building integrated P photovoltaic roofing modules/shingles shall be tested in accordance with procedures and acceptance criteria in ASTM D 3161 or TAS 107. Building integrated P photovoltaic roofing modules/shingles shall comply with the classification requirements of Table 1507.2.7.1(2) for the appropriate maximum nominal design basic wind speed. Building integrated P photovoltaic roofing modules/shingle packaging shall bear a label to indicate compliance with the procedures in ASTM D 3161 or TAS 107 and the required classification from Table 1507.2.7.1(2) .

(Mod R5280 / AS)

Section 1508 – Roof Insulation

Change Section 1508.1 to read as shown:

Section 1508.1 General. Change to read as shown:

1508.1 General. The use of above-deck thermal insulation shall be permitted provided such insulation is covered with an approved roof covering and passes the tests of FM 4450, FM 4454 or UL 1256 (for wind uplift resistance), and ANSI/UL 263 or ASTM E119 (for fire resistance), when tested as an assembly. (No change to the remainder of text)

(Mod R5738-R1 / AM)

Section 1508 – Roof Insulation

Change Section 1508.2 to read as shown:

Section 1508.2 Material standards. Change to read as shown:

1508.2 Material standards. Above-deck thermal insulation board shall comply with the standards in Table 1508.2.

TABLE 1508.2

MATERIAL STANDARDS FOR ROOF INSULATION

| Cellular glass board | ASTM C 552 |
| --- | --- |
| Composite boards | ASTM C 1289, Type III, IV, V or VI |
| Expanded polystyrene | ASTM C 578 |
| Extruded polystyrene board | ASTM C 578 |
| Lightweight insulating concrete | ASTM C 495, C513, C796, C869 |
| Perlite board | ASTM C 728 |
| Polyisocyanurate board | ASTM C 1289, Type I or Type II |
| Wood fiberboard | ASTM C 208 |

(Mod R5739 / AS)

Section 1509 – Rooftop Structures

Change Section 1509 to read as shown:

1509.1 General. The provisions of this section shall govern the construction of rooftop structures.

1509.2 Penthouses. Penthouses in compliance with Sections 1509.2.1 through 1509.2.5 shall be considered as a portion of the story directly below the roof deck on which such penthouses are located. All other penthouses shall be considered as an additional story of the building.

1509.2.1 Height above roof deck.  Penthouses constructed on buildings of other than Type I construction shall not exceed 18 feet (5486 mm) in height above the roof deck as measured to the average height of the roof of the penthouse.

Exceptions:

1. Where used to enclose tanks or elevators that travel to the roof level, penthouses shall be permitted to have a maximum height of 28 feet (8534 mm) above the roof deck.

2. Penthouses located on the roof of buildings of Type I construction shall not be limited in height.

1509.2.2 Area limitation. The aggregate area of penthouses and other enclosed rooftop structures shall not exceed one-third the area of the supporting roof deck. Such penthouses and other enclosed rooftop structures shall not be required to be included in determining the building area or number of stories as regulated by Section 503.1. The area of such penthouses shall not be included in determining the fire area specified in Section 901.7.

1509.2.3 Use limitations. Penthouses shall not be used for purposes other than the shelter of mechanical or electrical equipment, tanks, or vertical shaft openings in the roof assembly.

1509.2.4 Weather protection. Provisions such as louvers, louver blades or flashing shall be made to protect the mechanical and electrical equipment and the building interior from the elements.

1509.2.5 Type of construction. Penthouses shall be constructed with walls, floors and roofs as required for the type of construction of the building on which such penthouses are built.

Exceptions:

1. On buildings of Type I construction, the exterior walls and roofs of penthouses with a fire separation distance greater than 5 feet (1524 mm) and less than 20 feet (6096 mm) shall be permitted to have not less than a 1-hour fire-resistance rating. The exterior walls and roofs of penthouses with a fire separation distance of 20 feet (6096 mm) or greater shall not be required to have a fire-resistance rating.

2. On buildings of Type I construction two stories or less in height above grade plane or of Type II construction, the exterior walls and roofs of penthouses with a fire separation distance greater than 5 feet (1524 mm) and less than 20 feet (6096 mm) shall be permitted to have not less than a 1-hour fire-resistance rating or a lesser fire-resistance rating as required by Table 602 and be constructed of fire-retardant-treated wood. The exterior walls and roofs of penthouses with a fire separation distance of 20 feet (6096 mm) or greater shall be permitted to be constructed of fire-retardant-treated wood and shall not be required to have a fire-resistance rating. Interior framing and walls shall be permitted to be constructed of fire-retardant-treated wood.

3. On buildings of Type III, IV or V construction, the exterior walls of penthouses with a fire separation distance greater than 5 feet (1524 mm) and less than 20 feet (6096 mm) shall be permitted to have not less than a 1-hour fire-resistance rating or a lesser fire-resistance rating as required by Table 602. On buildings of Type III, IV or VA construction, the exterior walls of penthouses with a fire separation distance of 20 feet (6096 mm) or greater shall be permitted to be of Type IV or noncombustible construction or fire-retardant-treated wood and shall not be required to have a fire-resistance rating.

1509.3 Tanks. Tanks having a capacity of more than 500 gallons (2 m3) located on the roof deck of a building shall be supported on masonry, reinforced concrete, steel or Type IV construction provided that, where such supports are located in the building above the lowest story, the support shall be fire-resistance rated as required for Type IA construction.

1509.3.1 Valve and drain. In the bottom or on the side near the bottom of the tank, a pipe or outlet, fitted with a suitable quick-opening valve for discharging the contents into a drain in an emergency shall be provided.

1509.3.2 Location. Tanks shall not be placed over or near a stairway or an elevator shaft, unless there is a solid roof or floor underneath the tank.

1509.3.3 Tank cover. Unenclosed roof tanks shall have covers sloping toward the perimeter of the tanks.

1509.4 Cooling towers. Cooling towers located on the roof deck of a building and greater than 250 square feet (23.2 m2) in base area or greater than 15 feet (4572 mm) in height above the roof deck, as measured to the highest point on the cooling tower, where the roof is greater than 50 feet (15 240 mm) in height above grade plane shall be constructed of noncombustible materials. The base area of cooling towers shall not exceed one-third the area of the supporting roof deck.

Exception: Drip boards and the enclosing construction shall be permitted to be of wood not less than 1 inch (25 mm) nominal thickness, provided the wood is covered on the exterior of the tower with noncombustible material.

1509.5 Towers, spires, domes and cupolas. Towers, spires, domes and cupolas shall be of a type of construction having fire-resistance ratings not less than required for the building on top of which such tower, spire, dome or cupola is built. Towers, spires, domes and cupolas greater than 85 feet (25 908 mm) in height above grade plane as measured to the highest point on such structures, and either greater than 200 square feet (18.6 m2) in horizontal area or used for any purpose other than a belfry or an architectural embellishment, shall be constructed of and supported on Type I or II construction.

1509.5.1 Noncombustible construction required. Towers, spires, domes and cupolas greater than 60 feet (18 288 mm) in height above the highest point at which such structure contacts the roof as measured to the highest point on such structure, or that exceeds 200 square feet (18.6 m2) in area at any horizontal section, or which is intended to be used for any purpose other than a belfry or architectural embellishment, or is located on the top of a building greater than 50 feet (1524 mm) in building height shall be constructed of and supported by noncombustible materials and shall be separated from the building below by construction having a fire-resistance rating of not less than 1.5 hours with openings protected in accordance with Section 712. Such structures located on the top of a building greater than 50 feet (15 240 mm) in building height shall be supported by noncombustible construction.

1509.5.2 Towers and spires. Enclosed towers and spires shall have exterior walls constructed as required for the building on top of which such towers and spires are built. The roof covering of spires shall not be less than the same class of roof covering required for the building on top of which the spire is located.

1509.6 Mechanical equipment screens. Mechanical equipment screens shall be constructed of the materials specified for the exterior walls in accordance with the type of construction of the building. Where the fire separation distance is greater than 5 feet (1524 mm), mechanical equipment screens shall not be required to comply with the fire-resistance rating requirements.

1509.6.1 Height limitations. Mechanical equipment screens shall not exceed 18 feet (5486 mm) in height above the roof deck, as measured to the highest point on the mechanical equipment screen. 

Exception: Where located on buildings of Type IA construction, the height of mechanical equipment screens shall not be limited.

1509.6.2 Types I, II, III and IV construction. Regardless of the requirements in Section 1509.6, mechanical equipment screens shall be permitted to be constructed of combustible materials where located on the roof decks of building of Type I, II, III or IV construction in accordance with any one of the following limitations:

1. The fire separation distance shall not be less than 20 feet (6096 mm) and the height of the mechanical equipment screen above the roof deck shall not exceed 4 feet (1219 mm) as measured to the highest point on the mechanical equipment screen.

2. The fire separation distance shall not be less than 20 feet (6096 mm) and the mechanical equipment screen shall be constructed of fire-retardant-treated wood complying with Section 2303.2 for exterior installation.

3. Where exterior wall covering panels are used, the panels shall have a flame spread index of 25 or less when tested in the minimum and maximum thicknesses intended for use with each face tested independently in accordance with ASTM E 84 or UL 723. The panels shall be tested in the minimum and maximum thicknesses intended for use in accordance with, and shall comply with the acceptance criteria of, NFPA 285 and shall be installed as tested. Where the panels are tested as part of an exterior wall assembly in accordance with NFPA 285, the panels shall be installed on the face of the mechanical equipment screen supporting structure in the same manner as they were installed on the tested exterior wall assembly.

1509.6.3 Type V construction. The height of mechanical equipment screens located on the roof decks of buildings of Type V construction, as measured from grade plane to the highest point on the mechanical equipment screen, shall be permitted to exceed the maximum building height allowed for the building by other provisions of this code where complying with any one of the following limitations, provided the fire separation distance is greater than 5 feet (1524 mm):

1. Where the fire separation distance is not less than 20 feet (6096 mm), the height above grade plane of the mechanical equipment screen shall not exceed 4 feet (1219 mm) more than the maximum building height allowed;

2. The mechanical equipment screen shall be constructed of noncombustible materials;

3. The mechanical equipment screen shall be constructed of fire-retardant-treated wood complying with Section 2303.2 for exterior installation; or

4. Where the fire separation distance is not less than 20 feet (6096 mm), the mechanical equipment screen shall be constructed of materials having a flame spread index of 25 or less when tested in the minimum and maximum thicknesses intended for use with each face tested independently in accordance with ASTM E 84 or UL 723.

1509.6.4 Equipment and appliances on roofs or elevated structures. Where equipment and appliances requiring access are installed on roofs or elevated structures at a height exceeding 16 feet (4877 mm), such access shall be provided by a permanent approved means of access, the extent of which shall be from grade or floor level to the equipment and appliances' level service space. Such access shall not require climbing over obstructions greater than 30 inches (762 mm) high or walking on roofs having a slope greater than 4 units vertical in 12 units horizontal (33-percent slope). 

Permanent ladders installed to provide the required access shall comply with the following minimum design criteria:

1. The side railing shall extend above the parapet or roof edge not less than 30 inches (762 mm).

2. Ladders shall have rung spacing not to exceed 14 inches (356 mm) on center.

3. Ladders shall have a toe spacing not less than 6 inches (152 mm) deep.

4. There shall be a minimum of 18 inches (457 mm) between rails.

5. Rungs shall have a minimum 0.75-inch (19 mm) diameter and be capable of withstanding a 300-pound (136.1 kg) load.

6. Ladders over 30 feet (9144 mm) in height shall be provided with offset sections and landings capable of withstanding 100 pounds (488.2 kg/m2) per square foot.

7. Ladders shall be protected against corrosion by approved means. Catwalks installed to provide the required access shall be not less than 24 inches (610 mm) wide and shall have railings as required for service platforms. 

Exception: This section shall not apply to Group R-3 occupancies.

1509.6.5 Mechanical units. Roof mounted mechanical units shall be mounted on curbs raised a minimum of 8 inches (203 mm) above the roof surface, or where roofing materials extend beneath the unit, on raised equipment supports providing a minimum clearance height in accordance with Table 1509.7.

TABLE 1509.6.5

CLEARANCE BELOW RAISED ROOF MOUNTED MECHANICAL UNITS

| WIDTH OF MECHANICAL UNIT (inches) | MINIMUM CLEARANCE ABOVE SURFACES (inches) |
| --- | --- |
| < 24 | 14 |
| 24 < 36 | 18 |
| 36 < 48 | 24 |
| 48 < 60 | 30 |
| > 60 | 48 |
| For SI: 1 inch = 25.4 mm. |  |

Exception: In buildings where the existing rooftop equipment, in the opinion of the building official, provides sufficient clearance to repair, recover, replace and/or maintain the roofing system or any of its components, such existing equipment need not comply with Table 1509.6.5

1509.7 Photovoltaic systems. Rooftop mounted photovoltaic systems shall be designed in accordance with this section.

1509.7.1 Wind resistance. Rooftop mounted photovoltaic systems shall be designed for wind loads for component and cladding in accordance with Chapter 16 using an effective wind area based on the dimensions of a single unit frame.

1509.7.2 Fire classification. Rooftop mounted photovoltaic systems shall have the same fire classification as the roof assembly required by Section 1505.

1509.7.3 Installation. Rooftop mounted photovoltaic systems shall be installed in accordance with the manufacturer's installation instructions.

1509.7.4 Photovoltaic panels and modules. Photovoltaic panels and modules mounted on top of a roof shall be listed and labeled in accordance with UL 1703 and shall be installed in accordance with the manufacturer's installation instructions.

1509.8 Other rooftop structures. Rooftop structures not regulated by Sections 1509.2 through 1509.7 shall comply with Sections 1509.8.1 through 1509.8.5 as applicable.

1509.8.1 Aerial supports. Aerial supports shall be constructed of noncombustible materials.

Exception: Aerial supports not greater than 12 feet (3658 mm) in height as measured from the roof deck to the highest point on the aerial supports shall be permitted to be constructed of combustible materials.

1509.8.2 Bulkheads. Bulkheads used for the shelter of mechanical or electrical equipment or vertical shaft openings in the roof assembly shall comply with Section 1509.2 as penthouses. Bulkheads used for any other purpose shall be considered as an additional story of the building.

1509.8.3 Dormers. Dormers shall be of the same type of construction as required for the roof in which such dormers are located or the exterior walls of the building.

1509.8.4 Fences. Fences and similar structures shall comply with Section 1509.6 as mechanical equipment screens.

1509.8.5 Flagpoles. Flagpoles and similar structures shall not be required to be constructed of noncombustible materials and shall not be limited in height or number.

(Mod R5288 / AS)

SECTION 1510

REROOFING

Section 1510 – Reroofing

Change Section 1510.3 to read as shown:

1510.3 Recovering versus replacement.  New roof coverings shall not be installed without first removing all existing layers of roof coverings down to the roof deck where any of the following conditions occur:

1. Where the existing roof or roof covering is water soaked or has deteriorated to the point that the existing roof or roof covering is not adequate as a base for additional roofing.

2. Where the existing roof covering is wood shake, slate, clay, cement or asbestos-cement tile.

3. Where the existing roof has two or more applications of any type of roof covering.

4. When blisters exist in any roofing, unless blisters are cut or scraped open and remaining materials secured down before applying additional roofing.

5. Where the existing roof is to be used for attachment for a new roof system and compliance with the securement provisions of Section 1504.1 cannot be met. 

Exceptions:

1. Complete and separate roofing systems, such as standing-seam metal roof systems, that are designed to transmit the roof loads directly to the building's structural system and that do not rely on existing roofs and roof coverings for support, shall not require the removal of existing roof coverings.

2. Reserved. Metal panel, metal shingle and concrete and clay tile roof coverings shall be permitted to be installed over existing wood shake roofs when applied in accordance with Section 1510.4.

3. The application of a new protective coating over an existing spray polyurethane foam roofing system shall be permitted without tear-off of existing roof coverings.

4. Where the existing roof assembly includes an ice barrier membrane that is adhered to the roof deck, the existing ice barrier membrane shall be permitted to remain in place and covered with an additional layer of ice barrier membrane in accordance with Section 1507.

(Mod R5413 / AS)

Chapter 16 – Structural Design

Florida Specific Amendment

Section 1601 General

Change Section 1601.1 to read as shown.

- 1601.1 Scope.  The provisions of this chapter shall govern the structural design of buildings, structures and portions thereof regulated by this code.

Exception: Buildings and structures located within the high-velocity hurricane zone shall comply with the provisions of   Section 1605, 1607, 1611, Sections 1616 through 1626, and, as applicable in flood hazard areas, Section 1612.

(Mod S5425 / AS) (Mod S5263 / AS)

Section 1603 – Construction Documents

Change Section 1603.1.7 to read as shown:

1603.1.7 Flood design data. For buildings located in whole or in part in flood hazard areas as established in Section 1612.3, the documentation pertaining to design, if required in Section 1612.5, shall be included and the following information, referenced to the datum on the community’s Flood Insurance Rate Map (FIRM), shall be shown, regardless of whether flood loads govern the design of the building:

1. In flood hazard areas not subject to high-velocity wave action other than coastal high hazard areas, the elevation of the proposed lowest floor, including basement.

2. In flood hazard areas subject to high-velocity wave action coastal high hazard areas, the elevation to which any non-residential building will be dry floodproofed.

3. In flood hazard areas subject to high-velocity wave action coastal high hazard areas, the proposed elevation of the bottom of the lowest horizontal structural member of the lowest floor, including basement.

(Mod SP5274 / AS)

Section 1604 – General Design Requirements

Change Table 1604.3 to read as shown:

TABLE 1604.3
DEFLECTION LIMITS a, b, c, h, i

| CONSTRUCTION | L | S or W f | D + Ld,g,j |
| --- | --- | --- | --- |
| Roof members:e Supporting plaster or stucco ceiling Supporting nonplaster ceiling Not supporting ceiling Members supporting screen surface | l/360 l/240 l/180 — | l/360 l/240 l/180 — | l/240 l/180 l/120 l/60 |
| Floor members | l/360 | — | l/240 |
| Exterior walls and interior partitions: With plaster or stucco finishes With other brittle finishes With flexible finishes | — — — | l/360 l/240 l/120 | — — — |
| Farm buildings | — | — | l/180 |
| Greenhouses | — | — | l /120 |

For SI: 1 foot = 304.8 mm.

a.- i. (No Change)

j. Screen surfaces shall be permitted to include a maximum of 25% solid flexible finishes.

(Mod S5729 / AS)

Section 1604 – General Design Requirements

Change Table 1604.5 to read as shown:

TABLE 1604.5
RISK CATEGORY OF BUILDINGS AND OTHER STRUCTURES

| RISK CATEGORY | NATURE OF OCCUPANCY |
| --- | --- |
| I | Buildings and other structures that represent a low hazard to human life in the event of failure, including but not limited to: • Agricultural facilities. • Certain temporary facilities. • Minor storage facilities. • Screen enclosures. |
| II | Buildings and other structures except those listed in Risk Categories I, III and IV |
| III | Buildings and other structures that represent a substantial hazard to human life in the event of failure, including but not limited to: • Buildings and other structures whose primary occupancy is public assembly with an occupant load greater than 300. • Buildings and other structures containing elementary school, secondary school or day care facilities with an occupant load greater than 250. • Buildings and other structures containing adult education facilities, such as colleges and universities, with an occupant load greater than 500. • Group I-2 occupancies with an occupant load of 50 or more resident care recipients but not having surgery or emergency treatment facilities. • Group I-3 occupancies. • Any other occupancy with an occupant load greater than 5,000a. • Power-generating stations, water treatment facilities for potable water, waste water treatment facilities and other public utility facilities not included in Risk Category IV. • Buildings and other structures not included in Risk Category IV containing quantities of toxic or explosive materials that: Exceed maximum allowable quantities per control area as given in Table 307.1(1) or 307.1(2) or per outdoor control area in accordance with the International Florida Fire Prevention Code; and Are sufficient to pose a threat to the public if releasedb. |
| IV | Buildings and other structures designated as essential facilities, including but not limited to: • Group I-2 occupancies having surgery or emergency treatment facilities. • Fire, rescue, ambulance and police stations and emergency vehicle garages. • Designated earthquake, hurricane or other emergency shelters. • Designated emergency preparedness, communications and operations centers and other facilities required for emergency response. • Power-generating stations and other public utility facilities required as emergency backup facilities for Risk Category IV structures. • Buildings and other structures containing quantities of highly toxic materials that: Exceed maximum allowable quantities per control area as given in Table 307.1(2) or per outdoor control area in accordance with the International Florida Fire Prevention Code; and Are sufficient to pose a threat to the public if releasedb. • Aviation control towers, air traffic control centers and emergency aircraft hangars. • Buildings and other structures having critical national defense functions. • Water storage facilities and pump structures required to maintain water pressure for fire suppression. |

a.     For purposes of occupant load calculation, occupancies required by Table 1004.1.2 to use gross floor area calculations shall be permitted to use net floor areas to determine the total occupant load.

b.     Where approved by the building official, the classification of buildings and other structures as Risk Category III or IV based on their quantities of toxic, highly toxic or explosive materials is permitted to be reduced to Risk Category II, provided it can be demonstrated by a hazard assessment in accordance with Section 1.5.3 of ASCE 7 that a release of the toxic, highly toxic or explosive materials is not sufficient to pose a threat to the public.

(Mod S5949 / AS)

Section 1607 – Live Loads

Change Table 1607.1 to read as shown:

TABLE 1607.1

MINIMUM UNIFORMLY DISTRIBUTED LIVE LOADS, Lo, AND

MINIMUM CONCENTRATED LIVE LOADSg

(No change to body of Table 1607.1)

Footnotes a. – g. (No change)

h. See Section 1604.8.3 (HVHZ shall comply with Section 1616.5) for decks attached to exterior walls.

Footnotes i. – m. (No change)

(Mod S5431 / AS)

Section 1609 – Wind loads

Change Section 1609.1 to read as shown:

1609.1 Applications. Buildings, structures and parts thereof shall be designed to withstand the minimum wind loads prescribed herein. Decreases in wind loads shall not be made for the effect of shielding by other structures. All exterior wall coverings and soffits shall be capable of resisting the design pressures specified for walls for components and cladding loads in accordance with Section 1609.1.1. Manufactured soffits shall be labeled in accordance with Section 1710.9 of this code.

(Mod S5734 / AS)

Section 1609 – Wind loads

Change Section 1609.1.1 to read as shown:

1609.1.1 Determination of wind loads. Wind loads on every building or structure shall be determined in accordance with Chapters 26 to 30 of ASCE 7 or provisions of the alternate all-heights method in Section 1609.6. The type of opening protection required, the ultimate design wind speed, Vult, and the exposure category for a site is permitted to be determined in accordance with Section 1609 or ASCE 7. Wind shall be assumed to come from any horizontal direction and wind pressures shall be assumed to act normal to the surface considered.

Exceptions:

- Subject to the limitations of Section 1609.1.1.1, the provisions of ICC 600 shall be permitted for applicable Group R-2 and R-3 buildings.

- Subject to the limitations of Section 1609.1.1.1, residential structures using the provisions of AF&PA WFCM.

- Subject to the limitations of Section 1609.1.1.1, residential structures using the provisions of AISI S230.

- Designs using NAAMM FP 1001.

- Designs using TIA-222 for antenna-supporting structures and antennas, provided the horizontal extent of Topographic Category 2 escarpments in Section 2.6.6.2 of TIA-222 shall be 16 times the height of the escarpment. Design using this standard shall be permitted for communication tower and steel antenna support structures.

- Wind tunnel tests in accordance with Chapter 31 of ASCE 7.

- Wind loads for screened enclosures shall be determined in accordance with Section 2002.4.

The wind speeds in Figures 1609A, 1609B and 1609C are ultimate design wind speeds, Vult, and shall be converted in accordance with Section 1609.3.1 to nominal design wind speeds, Vasd, when the provisions of the standards referenced in Exceptions 1,3,4 through and 5 are used unless the wind provisions in the standards are based on Ultimate Wind Speeds as specified in Figures 1609A, 1609B, or 1609C or Chapter 26 of ASCE 7.

(Mod S5608 / AS)

(Mod S5121-R1 / AM)

(Mod S5732 / AS)

Section 1609 – Wind Loads

Change Figures 1609A – 1609C to read as shown:

(Mod S5118 / AM)

Section 1609 – Wind Loads

Change Section 1609.1.2 to read as shown:

1609.1.2 Protection of openings. In wind-borne debris regions, glazing glazed openings in buildings shall be impact resistant or protected with an impact-resistant covering meeting the requirements of , an approved impact-resistant standard or ASTM E 1996 and ASTM E 1886 referenced herein as follows: , SSTD 12, ANSI/DASMA 115 (for garage doors and rolling doors) or TAS 201, 202 and 203, AAMA 506. ASTM E 1996 and ASTM E 1886 referenced herein, or an approved impact-resistant standard as follows:

1. Glazed openings located within 30 feet (9.1 m) of grade shall meet the requirements of the Large Missile Test of ASTM E 1996.

2. Glazed openings located more than 30 feet (9.1 m) above grade shall meet the provisions of the Small Missile Test of ASTM E 1996.

3. Storage sheds that are not designed for human habitation and that have a floor area of 720 square feet (67 m2) or less are not required to comply with the mandatory windborne debris impact standards of this code.

4. Openings in sunrooms, balconies or enclosed porches constructed under existing roofs or decks are not required to be protected provided the spaces are separated from the building interior by a wall and all openings in the separating wall are protected in accordance with Section 1609.1.2 above. Such spaces shall be permitted to be designed as either partially enclosed or enclosed structures.

Exceptions: 1. – 3. (No change)

(Mod S5707-R1 / AM)

Section 1609 – Wind Loads

Change Table 1609.1.2 to read as shown:

TABLE 1609.1.2

WIND-BORNE DEBRIS PROTECTION FASTENING SCHEDULE FOR WOOD STRUCTURAL PANELSa, b, c, d

(Table Contents – No Change)

a.  This table is based on a Vasd determined in accordance with Section 1609.3.1, of 140 mph wind speeds and a 45-foot mean roof height.

b. – d. (No Change)

(Mod S5610 / AS)

Section 1609 – Wind loads

Change Sections 1609.1.2.1 and 1609.1.2.2 to read as shown:

1609.1.2.1 Louvers. Louvers protecting intake and exhaust ventilation ducts not assumed to be open that are located within 30 feet (9144 mm) of grade shall meet requirements of AMCA 540 or shall be protected by an impact resistant cover complying with the large missile test of ASTM E 1996 or an approved impact-resistance standard. Louvers required to be open for life safety purposes such as providing a breathable atmosphere shall meet the requirements of AMCA 540.

(S5667 AM R1) (S5951 AS)

1609.1.2.2. Application of ASTM E 1996. The text of Section 6.2.2 of ASTM E 1996 shall be substituted as follows:

6.2.2 Unless otherwise specified, select the wind zone based on the strength design wind speed, Vult, as follows:

6.2.2.1 Wind Zone 1—130 mph < ultimate design wind speed, Vult < 140 mph.

6.2.2.2 Wind Zone 2—140 mph < ultimate design wind speed, Vult < 150 mph at greater than one mile (1.6 km) from the coastline. The coastline shall be  measured from the mean high water mark.

6.2.2.3 Wind Zone 3—150 mph (58 m/s) <ultimate design wind speed, Vult < 160 170 mph (63 m/s), or 140 mph (54 m/s) <  ultimate design wind speed, Vult <  160 170 mph (63 m/s) and within one mile(1.6 km) of the coastline. The coastline shall be measured from the mean high water mark.

6.2.2.4 Wind Zone 4— ultimate design wind speed, Vult > 160 170 mph (63 m/s)

(S5668 AS)

Add Section 1609.1.2.4 to read as shown:

1609.1.2.4 Impact resistant coverings.

1609.1.2.4.1 Impact resistant coverings shall be tested at 1.5 times the design pressure (positive or negative) expressed in pounds per square feet as determined by the Florida Building Code, Building Section 1609 or ASCE 7, for which the specimen is to be tested. The design pressures, as determined from ASCE 7, are permitted to be multiplied by 0.6.

1609.1.2.4.2 Impact resistant coverings. Impact resistant coverings shall be labeled in accordance with the provisions of Section 1710.8.

(Mod S5669 / AS)

Section 1609 – Wind loads

Change Section 1609.4.2 to read as shown:

1609.4.2 Surface roughness categories.
A ground surface roughness within each 45-degree (0.79 rad) sector shall be determined for a distance upwind of the site as defined in Section 1609.4.3 from the categories defined below, for the purpose of assigning an exposure category as defined in Section 1609.4.3.

Surface Roughness B. Urban and suburban areas, wooded areas or other terrain with numerous closely spaced obstructions having the size of single-family dwellings or larger.

Surface Roughness C. Open terrain with scattered obstructions having heights generally less than 30 feet (9144 mm). This category includes flat open country, and grasslands.  This surface roughness shall also apply to any building located within surface roughness B-type terrain where the building is within 100 feet horizontally in any direction of open areas of surface roughness C or D-type terrain that extends more than 600 feet (182.9 m) in the upwind direction and a width greater than 150 feet.

Surface Roughness D. Flat, unobstructed areas and water surfaces. This category includes smooth mud flats, salt flats and unbroken ice.

(Mod S5613 / AS)

Section 1609 – Wind loads

Add Section 1609.7 to read as shown:

1609.7 Garage doors and rolling doors. Pressures from Table 1609.7(1) for wind loading actions on garage doors and rolling doors for buildings designed as enclosed shall be permitted.

| TABLE 1609.7(1) NOMINAL (ASD) GARAGE DOOR AND ROLLING DOOR WIND LOADS FOR A BUILDING WITH A MEAN ROOF HEIGHT OF 30 FEET LOCATED IN EXPOSURE B (PSF)1,2,3,4,5 ULTIMATE DESIGN WIND SPEED (Vult) DETERMINED IN ACCORDANCE WITH SECTION 1609.3 (MPH - 3 SECOND GUST) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Width (ft) |  | Height (ft) |  |  |  | 100 MPH |  |  |  | 110 MPH |  |  |  | 120 MPH |  |  |  | 130 MPH |  |  |  | 140 MPH |  | 150 MPH |  |  |  | 160 MPH |  |  |  | 170 MPH |  |  |  | 180 MPH |  |  |  | 190 MPH |  |  |  | 200 MPH |  |
| Roof Angle 0 - 10 degrees |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 8 | 8 |  | 8.7 |  | -9.8 |  | 10.5 |  | -11.9 |  | 12.5 |  | -14.2 |  | 14.7 |  | -16.6 |  | 17.1 |  | -19.3 |  | 19.6 |  | -22.2 |  | 22.3 |  | -25.2 |  | 25.1 |  | -28.5 |  | 28.2 |  | -31.9 |  | 31.4 |  | -35.5 |  | 34.8 |  | -39.4 |
| 10 | 10 |  | 8.4 |  | -9.4 |  | 10.2 |  | -11.4 |  | 12.1 |  | -13.6 |  | 14.2 |  | -16.0 |  | 16.5 |  | -18.5 |  | 18.9 |  | -21.2 |  | 21.5 |  | -24.2 |  | 24.3 |  | -27.3 |  | 27.3 |  | -30.6 |  | 30.4 |  | -34.1 |  | 33.7 |  | -37.8 |
| 14 | 14 |  | 8.0 |  | -8.9 |  | 9.7 |  | -10.8 |  | 11.5 |  | -12.8 |  | 13.5 |  | -15.0 |  | 15.7 |  | -17.4 |  | 18.0 |  | -20.0 |  | 20.5 |  | -22.8 |  | 23.1 |  | -25.7 |  | 25.9 |  | -28.8 |  | 28.9 |  | -32.1 |  | 32.0 |  | -35.6 |
| Roof Angle > 10 degrees |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 9 | 7 |  | 9.6 |  | -10.9 |  | 11.4 |  | -12.9 |  | 13.7 |  | -15.5 |  | 16.1 |  | -18.2 |  | 18.5 |  | -20.9 |  | 21.3 |  | -24.1 |  | 24.3 |  | -27.5 |  | 27.6 |  | -31.2 |  | 30.6 |  | -34.6 |  | 34.2 |  | -38.6 |  | 38.0 |  | -43.0 |
| 16 | 7 |  | 9.2 |  | -10.3 |  | 10.9 |  | -12.2 |  | 13.1 |  | -14.6 |  | 15.5 |  | -17.2 |  | 17.7 |  | -19.7 |  | 20.4 |  | -22.7 |  | 23.3 |  | -26.0 |  | 26.4 |  | -29.4 |  | 29.3 |  | -32.6 |  | 32.7 |  | -36.5 |  | 36.4 |  | -40.6 |
| 78 MPH |  |  |  | 85 MPH |  |  |  | 93 MPH |  |  |  | 101 MPH |  |  |  | 108 MPH |  |  |  | 116 MPH |  |  |  |  |  | 124 MPH |  |  |  | 132 MPH |  |  |  | 139 MPH |  |  |  | 147 MPH |  |  |  | 155 MPH |  |  |  |
| Nominal Design Wind Speed (Vasd) converted from Ultimate Design Wind Speed per Section 1609.3.1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

For SI: 1 foot = 304.8 mm, 1 mile per hour = 1.609 km/h, 1 psf = 47.88 N/m2

1. For effective areas or wind speeds between those given above the load may be interpolated, otherwise use the load associated with the lower effective area.

2. Table values shall be adjusted for height and exposure by multiplying by the adjustment coefficient in Table 1609.7(2)

3. Plus and minus signs signify pressures acting toward and away from the building surfaces.

4. Negative pressures assume door has 2 feet of width in building's end zone.

5. Table values include the 0.6 load reduction factor.

(Mod S5321 –R1 / AM)

Section 1612 – Flood Loads

Add Section 1612.1.1 to read as shown:

1612.1.1 Cross references. See Table 1612.1.

| Table 1612.1 CROSS REFERENCES DEFINING FLOOD RESISTANT PROVISIONS OF THE FLORIDA BUILDING CODE |  |  |  |
| --- | --- | --- | --- |
| Florida Building Code – Building |  |  |  |
| Section |  | Section |  |
| Chapter 1 | Administration | Chapter 14 | Exterior Walls |
| 102 | Applicability | 1403 | Performance Requirements |
| 107 | Construction Documents |  |  |
| 110 | Inspections | Chapter 16 | Structural Design |
| 111 | Certificates of Occupancy and Completion | 1601 | General |
|  |  | 1603 | Construction Documents |
| Chapter 2 | Definitions | 1605 | Load Combinations |
| 202 | Definitions | 1612 | Flood Loads |
| Chapter 4 | Special Detailed Requirements Based on Use and Occupancy | Chapter 18 | Soils and Foundations |
| 419 | Hospitals | 1804 | Excavation, Grading and Fill |
| 420 | Nursing Homes | 1805 | Dampproofing and Waterproofing |
| 424 | Swimming Pools and Bathing Places (Public And Private) |  |  |
| Chapter 8 | Interior Finishes | Chapter 30 | Elevators and Conveying Systems |
| 801 | General | 3001 | General |
| Chapter 12 | Interior Environment | Chapter 31 | Special Construction |
| 1203 | Ventilation | 3102 | Membrane Structures |
| Florida Building Code – Residential |  |  |  |
| Section |  | Section |  |
| Chapter 2 | Definitions | Chapter 22 | Special Piping and Storage Systems |
| 202 | Definitions | M2201 | Oil Tanks |
| Chapter 3 | Building Planning | Chapter 24 | Fuel Gas |
| R301 | Design Criteria | G2404 (301) | General |
| R309 | Garages and Carports |  |  |
| R322 | Flood Resistant Construction | Chapter 26 | General Plumbing Requirements |
|  |  | P2601 | General |
| Chapter 4 | Foundations |  |  |
| R401 | General | Chapter 27 | Plumbing Fixtures |
| R404 | Foundation and Retaining Walls | P2705 | Installation |
| R408 | Under-Floor Space |  |  |
| Chapter 13 | General Mechanical System Requirements | Chapter 30 | Sanitary Drainage |
| M1301 | General | P3001 | General |
| Chapter 14 | Heating and Cooling Equipment | Chapter 31 | Vents |
| M1401 | General | P3101 | Vent Systems |
| Chapter 16 | Duct Systems | Chapter 41 | Swimming Pools |
| M1601 | Duct Construction | R4101 | Private Swimming Pools |
| Chapter 17 | Combustion Air | Chapter 44 | High-Velocity Hurricane Zones |
| M1701 | General | R4403 | High-Velocity Hurricane Zones – General |
| Chapter 20 | Boilers and Water Heaters |  |  |
| M2001 | Boilers |  |  |
| Florida Building Code – Existing |  |  |  |
| Section |  | Section |  |
| Chapter 1 | Administration | Chapter 11 | Additions |
| 101 | General | 1103 | Structural |
| Chapter 2 | Definitions |  |  |
| 202 | Definitions | Chapter 12 | Historic Buildings |
| Chapter 3 | Compliance Methods | 1201 | General |
| 301.1 | General |  |  |
| Chapter 4 | Prescriptive Compliance Method |  |  |
| 402 | Additions |  |  |
| 403 | Alterations | Chapter 13 | Relocated or Moved Buildings |
| 404 | Repairs | 1302 | Requirements |
| Chapter 6 | Repairs |  |  |
| 601 | General | Chapter 14 | Performance Compliance Methods |
| 606 | Structural | 1401 | General |
| Chapter 7 | Alterations – Level I |  |  |
| 701 | General |  |  |
| Florida Building Code – Mechanical |  |  |  |
| Section |  | Section |  |
| Chapter 3 | General Regulations | Chapter 6 | Duct Systems |
| M301 | General | M602 | Plenums |
|  |  | M603 | Duct Construction and Installation |
| Chapter 4 | Ventilation |  |  |
| M401 | General | Chapter 12 | Hydronic Piping |
|  |  | M1206 | Piping Installation |
| Chapter 5 | Exhaust Systems |  |  |
| M501 | General | Chapter 13 | Fuel Oil Piping and Storage |
|  |  | M1305 | Fuel Oil System Installation |
| Florida Building Code – Plumbing |  |  |  |
| Section |  |  |  |
| Chapter 3 | General Regulations |  |  |
| P309 | Flood Hazard Resistance |  |  |
| Florida Building Code – Fuel Gas |  |  |  |
| Section |  |  |  |
| Chapter 3 | General Regulations |  |  |
| FG301 | General |  |  |

(Mod SP5265 / AS)

Section 1612 – Flood Loads

Change Section 1612.3 to read as shown:

1612.3 Establishment of flood hazard areas. To establish flood hazard areas, the applicable governing authority shall, by local floodplain management ordinance, adopt a flood hazard map and supporting data. Remainder unchanged The flood hazard map shall include, at a minimum, areas of special flood hazard as identified by the Federal Emergency Management Agency in an engineering report entitled "The Flood Insurance Study for [INSERT NAME OF JURISDICTION],” dated [INSERT DATE OF ISSUANCE], as amended or revised with the accompanying Flood Insurance Rate Map (FIRM) and Flood Boundary and Floodway Map (FBFM) and related supporting data along with any revisions thereto. The adopted flood hazard map and supporting data are hereby adopted by reference and declared to be part of this section.

(Mod SP5259 / AS)

Section 1612 – Flood Loads

Change Sections 1612.4 and 1612.5 to read as shown:

Add Section 1612.4.1 to read as shown:

1612.4 Design and construction. The design and construction of buildings and structures located in flood hazard areas, including flood hazard areas subject to high-velocity wave action coastal high hazard areas, shall be in accordance with Chapter 5 of ASCE 7 and with ASCE 24.

1612.4.1 Modification of ASCE 24.  Table 6-1 and Section 6.2.1 in ASCE 24 shall be 	modified as follows:

1.      The title of Table 6.1 shall be “Minimum Elevation of Floodproofing, Relative to Base Flood Elevation (BFE) or Design Flood Elevation (DFE), in Coastal A Zones and in Other Flood Hazard Areas that are not  – Outside of High Risk Flood Hazard Areas.”

2. 	Section 6.2.1 shall be modified to permit dry floodproofing in Coastal A Zones, as follows: “Dry floodproofing of nonresidential structures and nonresidential areas of mixed-use structures shall not be allowed unless such structures are located outside of High Risk Flood Hazard areas and Coastal High Hazard Areas, and Coastal A Zones. Dry floodproofing shall be permitted in Coastal A Zones provided wave loads and the potential for erosion and local scour are accounted for in the design. Dry floodproofing of residential structures or residential areas of mixed-use structures shall not be permitted.”

1612.5 Flood hazard documentation. The following documentation shall be prepared and sealed by a registered design professional and submitted to the building official:

1. For construction in flood hazard areas not subject to high-velocity wave action other than coastal high hazard areas:

1.1. The elevation of the lowest floor, including the basement, as required by the lowest floor elevation foundation inspection and the final inspection in Section 110.3.3.

1.2. For fully enclosed areas below the design flood elevation where provisions to allow for the automatic entry and exit of floodwaters do not meet the minimum requirements in Section 2.6.2.1, ASCE 24, construction documents shall include a statement that the design will provide for equalization of hydrostatic flood forces in accordance with Section 2.6.2.2 of ASCE 24.

1.3. For dry floodproofed nonresidential buildings, construction documents shall include a statement that the dry floodproofing is designed in accordance with ASCE 24.

2.   For construction in flood hazard areas subject to high-velocity wave action coastal high hazard areas:

2.1. The elevation of the bottom of the lowest horizontal structural member as required by the lowest floor elevation foundation inspection and the final inspection in Section 110.3. 3.

2.2. Construction documents shall include a statement that the building is designed in accordance with ASCE 24, including that the pile or column foundation and building or structure to be attached thereto is designed to be anchored to resist flotation, collapse and lateral movement due to the effects of wind and flood loads acting simultaneously on all building components, and other load requirements of Chapter 16.

2.3. For breakaway walls designed to have a resistance of more than 20 psf (0.96 kN/m2) determined using allowable stress design, construction documents shall include a statement that the breakaway wall is designed in accordance with ASCE 24.

(Mod SP5274 / AS)	(Mod SP5267 / AS)    (Mod SP5254 / AS)

Chapter 17 – Structural Tests and Special Inspection

Section 1702 – Definitions

Change Section 1702 to add or revise the following terms as shown:

GARAGE DOOR MANUFACTURER

SPECIAL INSPECTION. Reserved.

Continuous special inspection. Reserved.

Periodic special inspection. Reserved.

SPECIAL INSPECTOR. Reserved.

STRUCTURAL OBSERVATION. Reserved.

(Mod S5324 / AS)

(Mod S5149-R1 / AM)

Section 1703 Approvals.

Change Section 1703.6.1 to read as shown:

1703.6.1 Follow-up inspection. The applicant shall provide for special inspections of fabricated items in accordance with Section 1704.2.5. Reserved.

(Mod S5149-R1 / AM)

Section 1704 Special Inspections, Contractor Responsibility and Structural Observations

Change Section 1704 to read as shown:

SECTION 1704

SPECIAL INSPECTIONS, CONTRACTOR RESPONSIBILITY AND STRUCTURAL OBSERVATIONS 
Reserved

1704.1 General. This section provides minimum requirements for special inspections, the statement of special inspections, contractor responsibility and structural observations. 

1704.2 Special inspections. Where application is made for construction as described in this section, the owner or the registered design professional in responsible charge acting as the owner’s agent shall employ one or more approved agencies to perform inspections during construction on the types of work listed under Section 1705. These inspections are in addition to the inspections identified in Section 110.

Exceptions:

1. Special inspections are not required for construction of a minor nature or as warranted 	by conditions in the jurisdiction as approved by the building official.

2. Unless otherwise required by the building official, special inspections are not required 	for Group U occupancies that are accessory to a residential occupancy including, but not 	limited to, those listed in Section 312.1.

3. Special inspections are not required for portions of structures designed and constructed 	in accordance with the cold-formed steel light-frame construction provisions of Section 	2211.7 or the conventional light-frame construction provisions of Section 2308.

1704.2.1 Special inspector qualifications. The special inspector shall provide written 	documentation to the building official demonstrating his or her competence and relevant 	experience or training. Experience or training shall be considered relevant when the 	documented experience or training is related in complexity to the same type of special 	inspection activities for projects of similar complexity and material qualities. These 	qualifications are in addition to qualifications specified in other sections of this code. 

	The registered design professional in responsible charge and engineers of record 	involved in the design of the project are permitted to act as the approved agency and their 	personnel are permitted to act as the special inspector for the work designed by them, 	provided they qualify as special inspectors.

1704.2.2 Access for special inspection. The construction or work for which special 	inspection is required shall remain accessible and exposed for special inspection purposes 	until completion of the required special inspections.

1704.2.3 Statement of special inspections. The applicant shall submit a statement of 	special inspections in accordance with Section 107.1 as a condition for permit issuance. 	This statement shall be in accordance with Section 1704.3. 

		Exception: A statement of special inspections is not required for portions of 			structures designed and constructed in accordance with the cold-formed steel 			light-frame construction provisions of Section 2211.7 or the conventional light-			frame construction provisions of Section 2308.

1704.2.4 Report requirement. Special inspectors shall keep records of inspections. The 	special inspector shall furnish inspection reports to the building official, and to the 	registered design professional in responsible charge. Reports shall indicate that work 	inspected was or was not completed 	in conformance to approved construction 	documents. Discrepancies shall be brought to the immediate attention of the contractor 	for correction. If they are not corrected, the discrepancies shall be brought to the attention 	of the building official and to the registered design professional in responsible charge 	prior to the completion of that phase of the work. A final report documenting required 	special inspections and correction of 	any discrepancies noted in the inspections shall be 	submitted at a point in time agreed 	upon prior to the start of work by the applicant and 	the building official.

1704.2.5 Inspection of fabricators. Where fabrication of structural load-bearing 	members and assemblies is being performed 	on the premises of a fabricator’s shop, 	special inspection of the fabricated items shall be required by this section and as required 	elsewhere in this code.

1704.2.5.1 Fabrication and implementation procedures. 
		The special inspector shall verify that the fabricator maintains detailed fabrication 		and quality control procedures that provide a basis for inspection control of the 			workmanship and the fabricator’s ability to conform to approved construction 			documents and referenced standards. The special inspector shall review the 			procedures for completeness and adequacy relative to the code requirements for 			the fabricator’s scope of work. 

			Exception: Special inspections as required by Section 1704.2.5 shall not 				be required where the fabricator is approved in accordance with Section 				1704.2.5.2.

1704.2.5.2 Fabricator approval. 
		Special inspections required by Section 1705 are not required where the work is 			done on the premises of a fabricator registered and approved to perform such 			work without special inspection. Approval shall be based upon review of the 			fabricator’s written procedural and quality control manuals and periodic auditing 			of fabrication practices by an approved special inspection agency. At completion 			of fabrication, the approved fabricator shall submit a certificate of compliance to 			the building official stating that the work was performed in accordance with the 			approved construction documents.

1704.3 Statement of special inspections. Where special inspection or testing is required by Section 1705, the registered design professional in responsible charge shall prepare a statement of special inspections in accordance with Section 1704.3.1 for submittal by the applicant in accordance with Section 1704.2.3. 

	Exception: The statement of special inspections is permitted to be prepared by a 	qualified person approved by the building official for construction not designed by a 	registered design professional.

1704.3.1 Content of statement of special inspections. The statement of special 	inspections shall identify the following:

1. The materials, systems, components and work required to have special inspection or 	testing by the building official or by the registered design professional responsible for 	each portion of the work.

2. The type and extent of each special inspection.

3. The type and extent of each test.

4. Additional requirements for special inspection or testing for seismic or wind resistance 	as specified in Sections 1705.10, 1705.11 and 1705.12.

5. For each type of special inspection, identification as to whether it will be continuous 	special inspection or periodic special inspection.

1704.3.2 Seismic requirements in the statement of special inspections. 
	Where Section 1705.11 or 1705.12 specifies special inspection, testing or qualification 	for seismic resistance, the statement of special inspections shall identify the designated 	seismic systems and seismic force- resisting systems that are subject to special 	inspections.

1704.3.3 Wind requirements in the statement of special inspections. 
	Where Section 1705.10 specifies special inspection for wind requirements, the statement 	of special inspections shall identify the main windforce-resisting systems and wind-	resisting components subject to special inspection.

1704.4 Contractor responsibility. Each contractor responsible for the construction of a main wind- or seismic force-resisting system, designated seismic system or a wind- or seismic-resisting component listed in the statement of special inspections shall submit a written statement of responsibility to the building official and the owner prior to the commencement of work on the system or component. The contractor’s statement of responsibility shall contain acknowledgement of awareness of the special requirements contained in the statement of special inspection. 

1704.5 Structural observations. Where required by the provisions of Section 1704.5.1 or 1704.5.2, the owner shall employ a registered design professional to perform structural observations as defined in Section 1702. 

Prior to the commencement of observations, the structural observer shall submit to the building official a written statement identifying the frequency and extent of structural observations. 

At the conclusion of the work included in the permit, the structural observer shall submit to the building official a written statement that the site visits have been made and identify any reported deficiencies which, to the best of the structural observer’s knowledge, have not been resolved.

1704.5.1 Structural observations for seismic resistance. 
	Structural observations shall be provided for those structures assigned to Seismic Design 	Category D, E or F where one or more of the following conditions exist:

1. The structure is classified as Risk Category III or IV in accordance with Table 			1604.5.

2. The height of the structure is greater than 75 feet (22 860 mm) above the base.

3. The structure is assigned to Seismic Design Category E, is classified as Risk 			Category I or II in accordance with Table 1604.5, and is greater than two stories 			above grade plane.

4. When so designated by the registered design professional responsible for the 			structural design.

5. When such observation is specifically required by the building official.

1704.5.2 Structural observations for wind requirements. 
	Structural observations shall be provided for those structures sited where Vasd as 	determined in accordance with Section 1609.3.1 exceeds 110 mph (49 m/sec), where one 	or more of the following conditions exist:

1. The structure is classified as Risk Category III or IV in accordance with Table 			1604.5.

2. The building height of the structure is greater than 75 feet (22 860 mm).

3. When so designated by the registered design professional responsible for the 			structural design.

4. When such observation is specifically required by the building official.

(Mod S5149-R1 / AM)

Section 1705 Required Verification and Inspection 
Change Section 1705 to read as shown:

SECTION 1705

REQUIRED VERIFICATION AND INSPECTION

Reserved

1705.1 General. Verification and inspection of elements of buildings and structures shall be as required by this section.

1705.1.1 Special cases. Special inspections shall be required for proposed work that is, in 	the opinion of the building official, unusual in its nature, such as, but not limited to, the 	following examples:

1. Construction materials and systems that are alternatives to materials and systems 	prescribed by this code.

2. Unusual design applications of materials described in this code.

3. Materials and systems required to be installed in accordance with additional 	manufacturer’s instructions that prescribe requirements not contained in this code or in 	standards referenced by this code.

1705.2 Steel construction. The special inspections for steel elements of buildings and structures shall be as required in this section. 

	Exception: Special inspection of the steel fabrication process shall not be required where 	the fabricator does not perform any welding, thermal cutting or heating operation of any 	kind as part of the fabrication process. In such cases, the fabricator shall be required to 	submit a detailed procedure for material control that demonstrates the fabricator’s ability 	to maintain suitable records and procedures such that, at any time during the fabrication 	process, the material specification, and grade for the main stress-carrying elements are 	capable of being determined. Mill test reports shall be identifiable to the main stress-	carrying elements when required by the approved construction documents.

1705.2.1 Structural steel. Special inspection for structural steel shall be in accordance 	with the quality assurance inspection requirements of AISC 360.

1705.2.2 Steel construction other than structural steel. Special inspection for steel 	construction other than structural steel shall be in accordance with Table 1705.2.2 and 	this section.

TABLE 1705.2.2

REQUIRED VERIFICATION AND INSPECTION OF STEEL CONSTRUCTION OTHER THAN STRUCTURAL STEEL

| VERIFICATION AND INSPECTION | CONTINUOUS |  | PERIODIC | REFERENCED STANDARDa |
| --- | --- | --- | --- | --- |
| 1. Material verification of cold-formed steel deck: |  |  |  |  |
| a. Identification markings to conform to ASTM standards specified in the approved construction documents. | — |  | X | Applicable ASTM material standards |
| b. Manufacturer’s certified test reports. | — |  | X |  |
| 2. Inspection of welding: |  |  |  |  |
| a. Cold-formed steel deck: |  |  |  |  |
| 1) Floor and roof deck welds. | — |  | X | AWS D1.3 |
| b. Reinforcing steel: |  |  |  |  |
| 1) Verification of weldability of reinforcing steel other than ASTM A 706. | — |  | X | AWS D1.4 ACI 318: Section 3.5.2 |
| 2) Reinforcing steel resisting flexural and axial forces in intermediate and special moment frames, and boundary elements of special structural walls of concrete and shear reinforcement. | X | — |  |  |
| 3) Shear reinforcement. | X | — |  |  |
| 4) Other reinforcing steel. | — | X |  |  |

For SI: 1 inch = 25.4 mm.

a. Where applicable, see also Section 1705.11, Special inspections for seismic resistance.

1705.2.2.1 Welding. Welding inspection and welding inspector qualification shall 		be in accordance with this section.

1705.2.2.1.1 Cold-formed steel. Welding inspection and welding 					inspector qualification for cold-formed steel floor and roof decks shall be 				in accordance with AWS D1.3.

1705.2.2.1.2 Reinforcing steel. Welding inspection and welding inspector 			qualification for reinforcing steel shall be in accordance with AWS D1.4 				and ACI 318.

1705.2.2.2 Cold-formed steel trusses spanning 60 feet or greater. Where a 			cold-formed steel truss clear span is 60 feet (18 288 mm) or greater, the special 			inspector shall verify that the temporary installation restraint/bracing and the 			permanent individual truss member restraint/bracing are installed in accordance 			with the approved truss submittal package.

1705.3 Concrete construction. The special inspections and verifications for concrete construction shall be as required by this section and Table 1705.3. 

	Exception:  Special inspections shall not be required for:

1. Isolated spread concrete footings of buildings three stories or less above grade plane 	that are fully supported on earth or rock.

2. Continuous concrete footings supporting walls of buildings three stories or less above 	grade plane that are fully supported on earth or rock where:

2.1. The footings support walls of light-frame construction;

2.2. The footings are designed in accordance with Table 1809.7; or

2.3. The structural design of the footing is based on a specified compressive 			strength, f 'c, no greater than 2,500 pounds per square inch (psi) (17.2 MPa), 			regardless of the compressive strength specified in the construction documents or 			used in the footing construction.

3. Nonstructural concrete slabs supported directly on the ground, including prestressed 	slabs on grade, where the effective prestress in the concrete is less than 150 psi (1.03 	MPa).

4. Concrete foundation walls constructed in accordance with Table 1807.1.6.2.

5. Concrete patios, driveways and sidewalks, on grade.

TABLE 1705.3

REQUIRED VERIFICATION AND INSPECTION OF CONCRETE CONSTRUCTION

| VERIFICATION AND INSPECTION | CONTINUOUS | PERIODIC | REFERENCED STANDARDa | IBC REFERENCE |
| --- | --- | --- | --- | --- |
| 1. Inspection of reinforcing steel, including prestressing tendons, and placement. | — | X | ACI 318: 3.5, 7.1-7.7 | 1910.4 |
| 2. Inspection of reinforcing steel welding in accordance with Table 1705.2.2, Item 2b. | — | — | AWS D1.4 ACI 318: 3.5.2 | — |
| 3. Inspection of anchors cast in concrete where allowable loads have been increased or where strength design is used. | — | X | ACI 318: 8.1.3, 21.2.8 | 1908.5, 1909.1 |
| 4. Inspection of anchors post-installed in hardened concrete membersb. | — | X | ACI 318: 3.8.6, 8.1.3, 21.2.8 | 1909.1 |
| 5. Verifying use of required design mix. | — | X | ACI 318: Ch. 4, 5.2-5.4 | 1904.2, 1910.2, 1910.3 |
| 6. At the time fresh concrete is sampled to fabricate specimens for strength tests, perform slump and air content tests, and determine the temperature of the concrete. | X | — | ASTM C 172 ASTM C 31 ACI 318: 5.6, 5.8 | 1910.10 |
| 7. Inspection of concrete and shotcrete placement for proper application techniques. | X | — | ACI 318: 5.9, 5.10 | 1910.6, 1910.7, 1910.8 |
| 8. Inspection for maintenance of specified curing temperature and techniques. | — | X | ACI 318: 5.11-5.13 | 1910.9 |
| 9. Inspection of prestressed concrete: |  |  |  |  |
| a.Application of prestressing forces. b.Grouting of bonded prestressing ten-dons in the seismic force-resisting system. | X X | — | ACI 318: 18.20 ACI 318: 18.18.4 | — |
| 10. Erection of precast concrete members. | — | X | ACI 318: Ch. 16 | — |
| 11. Verification of in-situ concrete strength, prior to stressing of tendons in post-tensioned concrete and prior to removal of shores and forms from beams and structural slabs. | — | X | ACI 318: 6.2 | — |
| 12. Inspect formwork for shape, location and dimensions of the concrete member being formed. | — | X | ACI 318: 6.1.1 | — |

For SI: 1 inch = 25.4 mm.

a. Where applicable, see also Section 1705.11, Special inspections for seismic resistance.

b. Specific requirements for special inspection shall be included in the research report for the anchor issued by an approved source in accordance with ACI 355.2 or other qualification procedures. Where specific requirements are not provided, special inspection requirements shall be specified by the registered design professional and shall be approved by the building official prior to the commencement of the work.

1705.3.1 Materials. In the absence of sufficient data or documentation providing 	evidence of conformance to quality standards for materials in Chapter 3 of ACI 318, the 	building official shall require testing of materials in accordance with the appropriate 	standards and criteria for the material in Chapter 3 of ACI 318. Weldability of 	reinforcement, except that which conforms to ASTM A 706, shall be determined in 	accordance with the requirements of Section 3.5.2 of ACI 318.

1705.4 Masonry construction. Masonry construction shall be inspected and verified in accordance with TMS 402/ACI 530/ASCE 5 and TMS 602/ACI 530.1/ASCE 6 quality assurance program requirements.

Exception: Special inspections shall not be required for:

1. Empirically designed masonry, glass unit masonry or masonry veneer designed by 	Section 2109, 2110 or Chapter 14, respectively, where they are part of structures 	classified as Risk Category I, II or III in accordance with Section 1604.5.

2. Masonry foundation walls constructed in accordance with Table 1807.1.6.3(1), 	1807.1.6.3(2), 1807.1.6.3(3) or 1807.1.6.3(4).

3. Masonry fireplaces, masonry heaters or masonry chimneys installed or constructed in 	accordance with Section 2111, 2112 or 2113, respectively.

1705.4.1 Empirically designed masonry, glass unit masonry and masonry veneer in 	Risk Category IV. The minimum special inspection program for empirically designed 	masonry, glass unit masonry or masonry veneer designed by Section 2109, 2110 or 	Chapter 14, respectively, in structures classified as Risk Category IV, in accordance with 	Section 1604.5, shall comply with TMS 402/ACI 530/ASCE 5 Level B Quality 	Assurance.

1705.4.2 Vertical masonry foundation elements. Special inspection shall be performed 	in accordance with Section 1705.4 for vertical masonry foundation elements.

1705.5 Wood construction. Special inspections of the fabrication process of prefabricated wood structural elements and assemblies shall be in accordance with Section 1704.2.5. Special inspections of site-built assemblies shall be in accordance with this section.

1705.5.1 High-load diaphragms. High-load diaphragms designed in accordance with 	Section 2306.2 shall be installed with special inspections as indicated in Section 1704.2. 	The special inspector shall inspect the wood structural panel sheathing to ascertain 	whether it is of the grade and thickness shown on the approved building plans. 	Additionally, the special inspector must verify the nominal size of framing members at 	adjoining panel edges, the nail or staple diameter and length, the number of fastener lines 	and that the spacing between fasteners in each line and at edge margins agrees with the 	approved building plans.

1705.5.2 Metal-plate-connected wood trusses spanning 60 feet or greater. Where a 	truss clear span is 60 feet (18 288 mm) or greater, the special inspector shall verify that 	the temporary installation restraint/bracing and the permanent individual truss member 	restraint/bracing are installed in accordance with the approved truss submittal package.

1705.6 Soils. Special inspections for existing site soil conditions, fill placement and load-bearing requirements shall be as required by this section and Table 1705.6. The approved geotechnical report, and the construction documents prepared by the registered design professionals shall be used to determine compliance. During fill placement, the special inspector shall determine that proper materials and procedures are used in accordance with the provisions of the approved geotechnical report. 

	Exception: Where Section 1803 does not require reporting of materials and procedures 	for fill placement, the special inspector shall verify that the in-place dry density of the 	compacted fill is not less than 90 percent of the maximum dry density at optimum 	moisture content determined in accordance with ASTM D 1557.

TABLE 1705.6

REQUIRED VERIFICATION AND INSPECTION OF SOILS

| VERIFICATION AND INSPECTION TASK | CONTINUOUS DURING TASK LISTED | PERIODICALLY DURING TASK LISTED |
| --- | --- | --- |
| 1. Verify materials below shallow foundations are adequate to achieve the design bearing capacity. | — | X |
| 2. Verify excavations are extended to proper depth and have reached proper material. | — | X |
| 3. Perform classification and testing of compacted fill materials. | — | X |
| 4. Verify use of proper materials, densities and lift thicknesses during placement and compaction of compacted fill. | X | — |
| 5. Prior to placement of compacted fill, observe subgrade and verify that site has been prepared properly. | — | X |

1705.7 Driven deep foundations. Special inspections shall be performed during installation and testing of driven deep foundation elements as required by Table 1705.7. The approved instruction documents prepared by the registered design professionals, shall be used to determine compliance.

TABLE 1705.7

REQUIRED VERIFICATION AND INSPECTION OF DRIVEN DEEP FOUNDATION ELEMENTS

| VERIFICATION AND INSPECTION TASK | CONTINUOUS DURING TASK LISTED | PERIODICALLY DURING TASK LISTED |
| --- | --- | --- |
| 1. Verify element materials, sizes and lengths comply with the requirements. | X | — |
| 2. Determine capacities of test elements and conduct additional load tests, as required. | X | — |
| 3. Observe driving operations and maintain complete and accurate records for each element. | X | — |
| 4. Verify placement locations and plumbness, confirm type and size of hammer, record number of blows per foot of penetration, determine required penetrations to achieve design capacity, record tip and butt elevations and document any damage to foundation element. | X | — |
| 5. For steel elements, perform additional inspections in accordance with Section 1705.2 . | — | — |
| 6. For concrete elements and concrete-filled elements, perform additional inspections in accordance with Section 1705.3 . | — | — |
| 7. For specialty elements, perform additional inspections as determined by the registered design professional in responsible charge. | — | — |

1705.8 Cast-in-place deep foundations. Special inspections shall be performed during installation and testing of cast-in-place deep foundation elements as required by Table 1705.8. The approved geotechnical report, and the construction documents prepared by the registered design professionals, shall be used to determine compliance.

TABLE 1705.8

REQUIRED VERIFICATION AND INSPECTION OF CAST-IN-PLACE DEEP FOUNDATION ELEMENTS

| VERIFICATION AND INSPECTION TASK | CONTINUOUS DURING TASK LISTED | PERIODICALLY DURING TASK LISTED |
| --- | --- | --- |
| 1. Observe drilling operations and maintain complete and accurate records for each element. | X | — |
| 2. Verify placement locations and plumbness, confirm element diameters, bell diameters (if applicable), lengths, embedment into bedrock (if applicable) and adequate end-bearing strata capacity. Record concrete or grout volumes. | X | — |
| 3. For concrete elements, perform additional inspections in accordance with Section 1705.3 . | — | — |

1705.9 Helical pile foundations. Special inspections shall be performed continuously during installation of helical pile foundations. The information recorded shall include installation equipment used, pile dimensions, tip elevations, final depth, final installation torque and other pertinent installation data as required by the registered design professional in responsible charge. The approved geotechnical report and the construction documents prepared by the registered design professional shall be used to determine compliance.

1705.10 Special inspections for wind resistance. Special inspections itemized in Sections 1705.10.1 through 1705.10.3, unless exempted by the exceptions to Section 1704.2, are required for buildings and structures constructed in the following areas:

1. In wind Exposure Category B, where Vasd as determined in accordance with Section 	1609.3.1 is 120 miles per hour (52.8 m/sec) or greater.

2. In wind Exposure Category C or D, where Vasd as determined in accordance with 	Section 1609.3.1 is 110 mph (49 m/sec) or greater.

1705.10.1 Structural wood. Continuous special inspection is required during field gluing 	operations of elements of the main windforce-resisting system. Periodic special 	inspection is required for nailing, bolting, anchoring and other fastening of components 	within the main windforce-resisting system, including wood shear walls, wood 	diaphragms, drag struts, braces and hold-downs. 

	Exception: Special inspection is not required for wood shear walls, shear panels and 	diaphragms, including nailing, bolting, anchoring and other fastening to other 	components of the main windforce-resisting system, where the fastener spacing of the 	sheathing is more than 4 inches (102 mm) on center.

1705.10.2 Cold-formed steel light-frame construction. Periodic special inspection is 	required during welding operations of elements of the main windforce-resisting system. 	Periodic special inspection is required for screw attachment, bolting, anchoring and other 	fastening of components within the main windforce-resisting system, including shear 	walls, braces, diaphragms, collectors (drag struts) and hold-downs. 

	Exception: Special inspection is not required for cold-formed steel light-frame shear 	walls, braces, diaphragms, collectors (drag struts) and hold-downs where either of the 	following apply:

1. The sheathing is gypsum board or fiberboard.

2. The sheathing is wood structural panel or steel sheets on only one side of the shear 	wall, shear panel or diaphragm assembly and the fastener spacing of the sheathing is 	more than 4 inches (102 mm) on center (o.c.).

1705.10.3 Wind-resisting components. Periodic special inspection is required for the 	following systems and components:

1. Roof cladding.

2. Wall cladding.

1705.11 Special inspections for seismic resistance. Special inspections itemized in Sections 1705.11.1 through 1705.11.8, unless exempted by the exceptions of Section 1704.2, are required for the following:

1. The seismic force-resisting systems in structures assigned to Seismic Design Category 	C, D, E or F in accordance with Sections 1705.11.1 through 1705.11.3, as applicable.

2. Designated seismic systems in structures assigned to Seismic Design Category C, D, E 	or F in accordance with Section 1705.11.4.

3. Architectural, mechanical and electrical components in accordance with Sections 	1705.11.5 and 1705.11.6.

4. Storage racks in structures assigned to Seismic Design Category D, E or F in 	accordance with Section 1705.11.7.

5. Seismic isolation systems in accordance with Section 1705.11.8.

Exception: Special inspections itemized in Sections 1705.11.1 through 1705.11.8 are not 	required for structures designed and constructed in accordance with one of the following:

1. The structure consists of light-frame construction; the design spectral response 	acceleration at short periods, SDS, as determined in Section 1613.3.4, does not exceed 0.5; 	and the building height of the structure does not exceed 35 feet (10 668 mm).

2. The seismic force-resisting system of the structure consists of reinforced masonry or 	reinforced concrete; the design spectral response acceleration at short periods, SDS, as 	determined in Section 1613.3.4, does not exceed 0.5; and the building height of the 	structure does not exceed 25 feet (7620 mm).

3. The structure is a detached one- or two-family dwelling not exceeding two stories 	above grade plane and does not have any of the following horizontal or vertical 	irregularities in accordance with Section 12.3 of ASCE 7:

3.1. Torsional or extreme torsional irregularity.

3.2. Nonparallel systems irregularity.

3.3. Stiffness-soft story or stiffness-extreme soft story irregularity.

3.4. Discontinuity in lateral strength-weak story irregularity.

1705.11.1 Structural steel. Special inspection for structural steel shall be in accordance 	with the quality assurance requirements of AISC 341. 

	Exception: Special inspections of structural steel in structures assigned to Seismic 		Design Category C that are not specifically detailed for seismic resistance, with a 	response modification coefficient, R, of 3 or less, excluding cantilever column systems.

1705.11.2 Structural wood. Continuous special inspection is required during field gluing 	operations of elements of the seismic force-resisting system. Periodic special inspection 	force-resisting system, including wood shear walls, wood diaphragms, drag struts, braces, 	shear panels and hold-downs. 

	Exception: Special inspection is not required for wood shear walls, shear panels and 	diaphragms, including nailing, bolting, anchoring and other fastening to other 	components of the seismic force-resisting system, where the fastener spacing of the 	sheathing is more than 4 inches (102 mm) on center (o.c.).

1705.11.3 Cold-formed steel light-frame construction. Periodic special inspection is 	required during welding operations of elements of the seismic force-resisting system. 	Periodic special inspection is required for screw attachment, bolting, anchoring and other 	fastening of components within the seismic force-resisting system, including shear walls, 	braces, diaphragms, collectors (drag struts) and hold-downs.

Exception: Special inspection is not required for cold-formed steel light-frame shear 	walls, braces, diaphragms, collectors (drag struts) and hold-downs where either of the 	following apply:

1. The sheathing is gypsum board or fiberboard.

2. The sheathing is wood structural panel or steel sheets on only one side of the shear 	wall, shear panel or diaphragm assembly and the fastener spacing of the sheathing is 	more than 4 inches (102 mm) o.c.

1705.11.4 Designated seismic systems. The special inspector shall examine designated 	seismic systems requiring seismic qualification in accordance with Section 1705.12.3 and 	verify that the label, anchorage or mounting conforms to the certificate of compliance.

1705.11.5 Architectural components. Periodic special inspection is required during the 	erection and fastening of exterior cladding, interior and exterior nonbearing walls and 	interior and exterior veneer in structures assigned to Seismic Design Category D, E or F. 

	Exceptions:

1. Special inspection is not required for exterior cladding, interior and exterior 	nonbearing walls and interior and exterior veneer 30 feet (9144 mm) or less in height 	above grade or walking surface.

2. Special inspection is not required for exterior cladding and interior and exterior veneer 	weighing 5 psf (24.5 N/m2) or less.

3. Special inspection is not required for interior nonbearing walls weighing 15 psf (73.5 	N/m2) or less.

1705.11.5.1 Access floors. Periodic special inspection is required for the 				anchorage of access floors in structures assigned to Seismic Design Category D, E 		or F.

1705.11.6 Mechanical and electrical components. Special inspection for mechanical 	and electrical components shall be as follows:

1. Periodic special inspection is required during the anchorage of electrical equipment for 	emergency or standby power systems in structures assigned to Seismic Design Category 	C, D, E or F;

2. Periodic special inspection is required during the anchorage of other electrical 	equipment in structures assigned to Seismic Design Category E or F;

3. Periodic special inspection is required during the installation and anchorage of piping 	systems designed to carry hazardous materials and their associated mechanical units in 	structures assigned to Seismic Design Category C, D, E or F;

4. Periodic special inspection is required during the installation and anchorage of 	ductwork designed to carry hazardous materials in structures assigned to Seismic Design 	Category C, D, E or F; and

5. Periodic special inspection is required during the installation and anchorage of 	vibration isolation systems in structures assigned to Seismic Design Category C, D, E or 	F where the construction documents require a nominal clearance of 1/4 inch (6.4 mm) or 	less between the equipment support frame and restraint.

1705.11.7 Storage racks. Periodic special inspection is required during the anchorage of 	storage racks 8 feet (2438 mm) or greater in height in structures assigned to Seismic 	Design Category D, E or F.

1705.11.8 Seismic isolation systems. Periodic special inspection shall be provided for 	seismic isolation systems during the fabrication and installation of isolator units and 	energy dissipation devices.

1705.12 Testing and qualification for seismic resistance. The testing and qualification specified in Sections 1705.12.1 through 1705.12.4, unless exempted from special inspections by the exceptions of Section 1704.2 are required as follows:

1. The seismic force-resisting systems in structures assigned to Seismic Design Category 	C, D, E or F shall meet the requirements of Sections 1705.12.1 and 1705.12.2, as 	applicable.

2. Designated seismic systems in structures assigned to Seismic Design Category C, D, E 	or F and subject to the certification requirements of ASCE 7 Section 13.2.2 shall comply 	with Section 1705.12.3.

3. Architectural, mechanical and electrical components in structures assigned to Seismic 	Design Category C, D, E or F and where the requirements of ASCE 7 Section 13.2.1 are 	met by submittal of manufacturer’s certification, in accordance with Item 2 therein, shall 	comply with Section 1705.12.3.

4. The seismic isolation system in seismically isolated structures shall meet the testing 	requirements of Section 1705.12.4.

1705.12.1 Concrete reinforcement. Where reinforcement complying with ASTM A 615 	is used to resist earthquake-induced flexural and axial forces in special moment frames, 	special structural walls and coupling beams connecting special structural walls, in 	structures assigned to Seismic Design Category B, C, D, E or F, the reinforcement shall 	comply with Section 21.1.5.2 of ACI 318. Certified mill test reports shall be provided for 	each shipment of such reinforcement. Where reinforcement complying with ASTM A 	615 is to be welded, chemical tests shall be performed to determine weldability in 	accordance with Section 3.5.2 of ACI 318.

1705.12.2 Structural steel. Testing for structural steel shall be in accordance with the 	quality assurance requirements of AISC 341. 

	Exception: Testing for structural steel in structures assigned to Seismic Design Category 	C that are not specifically detailed for seismic resistance, with a response modification 	coefficient, R, of 3 or less, excluding cantilever column systems.

1705.12.3 Seismic certification of nonstructural components. The registered design 	professional shall specify on the construction documents the requirements for 	certification by analysis, testing or experience data for nonstructural components and 	designated seismic systems in accordance with Section 13.2 of ASCE 7, where such 	certification is required by Section 1705.12.

1705.12.4 Seismic isolation systems. Seismic isolation systems shall be tested in 	accordance with Section 17.8 of ASCE 7.

1705.13 Sprayed fire-resistant materials. Special inspections for sprayed fire-resistant materials applied to floor, roof and wall assemblies and structural members shall be in accordance with Sections 1705.13.1 through 1705.13.6. Special inspections shall be based on the fire-resistance design as designated in the approved construction documents. The tests set forth in this section shall be based on samplings from specific floor, roof and wall assemblies and structural members. Special inspections shall be performed after the rough installation of electrical, automatic sprinkler, mechanical and plumbing systems and suspension systems for ceilings, where applicable.

1705.13.1 Physical and visual tests. The special inspections shall include the following 	tests and observations to demonstrate compliance with the listing and the fire-resistance 	rating:

1. Condition of substrates.

2. Thickness of application.

3. Density in pounds per cubic foot (kg/m3).

4. Bond strength adhesion/cohesion.

5. Condition of finished application.

1705.13.2 Structural member surface conditions. The surfaces shall be prepared in 	accordance with the approved fire-resistance design and the written instructions of 	approved manufacturers. The prepared surface of structural members to be sprayed shall 	be inspected before the application of the sprayed fire-resistant material.

1705.13.3 Application. The substrate shall have a minimum ambient temperature before 	and after application as specified in the written instructions of approved manufacturers. 	The area for application shall be ventilated during and after application as required by the 	written instructions of approved manufacturers.

1705.13.4 Thickness. No more than 10 percent of the thickness measurements of the 	sprayed fire-resistant materials applied to floor, roof and wall assemblies and structural 	members shall be less than the thickness required by the approved fire-resistance design, 	but in no case less than the minimum allowable thickness required by Section 	1705.13.4.1.

1705.13.4.1 Minimum allowable thickness. For design thicknesses 1 inch (25 			mm) or greater, the minimum allowable individual thickness shall be the design 			thickness minus 1/4 inch (6.4 mm). For design thicknesses less than 1 inch (25 			mm), the minimum allowable individual thickness shall be the design thickness 			minus 25 percent. Thickness shall be determined in accordance with ASTM E 			605. Samples of the sprayed fire-resistant materials shall be selected in 				accordance with Sections 1705.13.4.2 and 1705.13.4.3.

1705.13.4.2 Floor, roof and wall assemblies. The thickness of the sprayed fire-			resistant material applied to floor, roof and wall assemblies shall be determined in 		accordance with ASTM E 605, making not less than four measurements for each 			1,000 square feet (93 m2) of the sprayed area, or portion thereof, in each story.

1705.13.4.3 Cellular decks. Thickness measurements shall be selected from a 			square area, 12 inches by 12 inches (305 mm by 305 mm) in size. A minimum of 			four measurements shall be made, located symmetrically within the square area.

1705.13.4.4 Fluted decks. Thickness measurements shall be selected from a 			square area, 12 inches by 12 inches (305 mm by 305 mm) in size. A minimum of 			four measurements shall be made, located symmetrically within the square area, 			including one each of the following: valley, crest and sides. The average of the 			measurements shall be reported.

1705.13.4.5 Structural members. The thickness of the sprayed fire-resistant 			material applied to structural members shall be determined in accordance with 			ASTM E 605. Thickness testing shall be performed on not less than 25 percent of 			the structural members on each floor.

1705.13.4.6 Beams and girders. At beams and girders thickness measurements 			shall be made at nine locations around the beam or girder at each end of a 12-inch 		(305 mm) length.

1705.13.4.7 Joists and trusses. At joists and trusses, thickness measurements 			shall be made at seven locations around the joist or truss at each end of a 12-inch 			(305 mm) length.

1705.13.4.8 Wide-flanged columns. At wide- flanged columns, thickness 				measurements shall be made at 12 locations around the column at each end of a 			12-inch (305 mm) length.

1705.13.4.9 Hollow structural section and pipe columns. At hollow structural 			section and pipe columns, thickness measurements shall be made at a minimum of 		four locations around the column at each end of a 12-inch (305 mm) length.

1705.13.5 Density. The density of the sprayed fire-resistant material shall not be less than 	the density specified in the approved fire-resistance design. Density of the sprayed fire-	resistant material shall be determined in accordance with ASTM E 605. The test samples 	for determining the density of the sprayed fire-resistant materials shall be selected as 	follows:

1. From each floor, roof and wall assembly at the rate of not less than one sample 			for every 2,500 square feet (232 m2) or portion thereof of the sprayed area in each 		story.

2. From beams, girders, trusses and columns at the rate of not less than one 			sample for each type of structural member for each 2,500 square feet (232 m2) of 			floor area or portion thereof in each story.

1705.13.6 Bond strength. The cohesive/adhesive bond strength of the cured sprayed fire-	resistant material applied to floor, roof and wall assemblies and structural members shall 	not be less than 150 pounds per square foot (psf) (7.18 kN/m2). The cohesive/adhesive 	bond strength shall be determined in accordance with the field test specified in ASTM E 	736 by testing in-place samples of the sprayed fire-resistant material selected in 	accordance with Sections 1705.13.6.1 through 1705.13.6.3.

1705.13.6.1 Floor, roof and wall assemblies. The test samples for determining 			the cohesive/adhesive bond strength of the sprayed fire-resistant 					materials shall be selected from each floor, roof and wall assembly at the rate of 			not less than one sample for every 2,500 square feet (232 m2) of the sprayed area, 			or portion thereof, in each story.

1705.13.6.2 Structural members. The test samples for determining the				cohesive/adhesive bond strength of the sprayed fire-resistant materials shall be 			selected from beams, girders, trusses, columns and other structural members at the 		rate of not less than one sample for each type of structural member for each 2,500 			square feet (232 m2) of floor area or portion thereof in each story.

1705.13.6.3 Primer, paint and encapsulant bond tests. Bond tests to qualify a 			primer, paint or encapsulant shall be conducted when the sprayed fire-resistant 			material is applied to a primed, painted or encapsulated surface for which 				acceptable bond-strength performance between these coatings and the fire-				resistant material has not been determined. A bonding agent approved by the 			SFRM manufacturer shall be applied to a primed, painted or encapsulated surface 			where the bond strengths are found to be less than required values.

1705.14 Mastic and intumescent fire-resistant coatings. Special inspections for mastic and intumescent fire-resistant coatings applied to structural elements and decks shall be in accordance with AWCI 12-B. Special inspections shall be based on the fire-resistance design as designated in the approved construction documents. 

1705.15 Exterior insulation and finish systems (EIFS). Special inspections shall be required for all EIFS applications. 
Exceptions:

1. Special inspections shall not be required for EIFS applications installed over a water-	resistive barrier with a means of draining moisture to the exterior.

2. Special inspections shall not be required for EIFS applications installed over masonry 	or concrete walls.

1705.15.1 Water-resistive barrier coating. A water-resistive barrier coating complying 	with ASTM E 2570 requires special inspection of the water-resistive barrier coating 	when installed over a sheathing substrate.

1705.16 Fire-resistant penetrations and joints. In high-rise buildings or in buildings assigned to Risk Category III or IV in accordance with Section 1604.5, special inspections for through-penetrations, membrane penetration firestops, fire-resistant joint systems, and perimeter fire barrier systems that are tested and listed in accordance with Sections 714.3.1.2, 714.4.1.2, 715.3 and 715.4 shall be in accordance with Section 1705.16.1 or 1705.16.2.

1705.16.1 Penetration firestops. Inspections of penetration firestop systems that are 	tested and listed in accordance with Sections 714.3.1.2 and 714.4.1.2 shall be conducted 	by an approved inspection agency in accordance with ASTM E 2174.

1705.16.2 Fire-resistant joint systems. Inspection of fire-resistant joint systems that are 	tested and listed in accordance with Sections 715.3 and 715.4 shall be conducted by an 	approved inspection agency in accordance with ASTM E 2393.

1705.17 Special inspection for smoke control. Smoke control systems shall be tested by a special inspector.

1705.17.1 Testing scope. The test scope shall be as follows:

1. During erection of ductwork and prior to concealment for the purposes of leakage 	testing and recording of device location.

2. Prior to occupancy and after sufficient completion for the purposes of pressure 	difference testing, flow measurements and detection and control verification.

1705.17.2 Qualifications. Special inspection agencies for smoke control shall have 	expertise in fire protection engineering, mechanical engineering and certification as air 	balancers.

(Mod S5149-R1 / AM)

Section 1710 Preconstruction Load Tests 
Change Section 1710 to read as shown:

1710.1 General. In evaluating the physical properties of materials and methods of construction that are not capable of being designed by approved engineering analysis or do not comply with the applicable referenced standards, the structural adequacy shall be predetermined based on the load test criteria established in this section. (Mod S5024-R1 / AM )

1710.2 Load test procedures specified. Where specific load test procedures, load factors and acceptance criteria are included in the applicable referenced standards, such test procedures, load factors and acceptance criteria shall apply. In the absence of specific test procedures, load factors or acceptance criteria, the corresponding provisions in Section 1710.3 shall apply. (Mod S5024-R1 / AM )

1710.3 Load test procedures not specified. Where load test procedures are not specified in the applicable referenced standards, the load-bearing and deformation capacity of structural components and assemblies shall be determined on the basis of a test procedure developed by a registered design professional that simulates applicable loading and deformation conditions. For components and assemblies that are not a part of the seismic force-resisting system, the test shall be as specified in Section 1710.3.1. Load tests shall simulate the applicable loading conditions specified in Chapter 16. (Mod S5024-R1 / AM )

1710.3.1 Test procedure.  The test assembly shall be subjected to an increasing superimposed load equal to not less than two times the superimposed design load. The test load shall be left in place for a period of 24 hours. The tested assembly shall be considered to have successfully met the test requirements if the assembly recovers not less than 75 percent of the maximum deflection within 24 hours after the removal of the test load. The test assembly shall then be reloaded and subjected to an increasing superimposed load until either structural failure occurs or the superimposed load is equal to two and one-half times the load at which the deflection limitations specified in Section 1710.3.2 were reached, or the load is equal to two and one-half times the superimposed design load. In the case of structural components and assemblies for which deflection limitations are not specified in Section 1710.3.2, the test specimen shall be subjected to an increasing superimposed load until structural failure occurs or the load is equal to two and one-half times the desired superimposed design load. The allowable superimposed design load shall be taken as the lesser of:

1. The load at the deflection limitation given in Section 1710.3.2.

2. The failure load divided by 2.5.

3. The maximum load applied divided by 2.5. (Mod S5024-R1 / AM )

1710.3.2 Deflection. The deflection of structural members under the design load shall not exceed the limitations in Section 1604.3. The HVHZ shall comply with Section 1616.3.1. (Mod S5024-R1 / AM )

1710.4 Wall and partition assemblies. Load-bearing wall and partition assemblies shall sustain the test load both with and without window framing. The test load shall include all design load components. Wall and partition assemblies shall be tested both with and without door and window framing. (Mod S5024-R1 / AM )

1710.5 Exterior window and door assemblies. The design pressure rating of exterior windows and doors in buildings shall be determined in accordance with Section 1710.5.1 or 1710.5.2.  The design pressures, as determined from ASCE 7, are permitted to be multiplied by 0.6.

For the purposes of this section, the required design pressure shall be determined using the allowable stress design load combinations of Section 1605.3 or 1618.9 for HVHZ.

(Mod S5024-R1 / AM )  (Mod S5615 / AS)  (Mod S5582 AM R1)

Exceptions:

1.  Structural wind load design pressures for window and door units smaller other than the size tested in accordance with Section 1710.5.1 or 1710.5.2 shall be permitted to be higher different than the design value of the tested unit provided such higher different pressures are determined by accepted engineering analysis, or Sections 1710.5.3 or 1710.5.4, or validated by an additional test of the window or door unit to the different design pressure in accordance with section 1710.5.2. All components of the small alternate size unit shall be the same as the tested or labeled unit. Where such calculated design pressures are used, they shall be validated by an additional test of the window unit having the highest allowable design pressure.

i. Operable windows and doors rated in this manner shall comply with the following:

1.    The frame area of the alternate size unit shall not exceed the frame area of the tested approved unit.

2.    Shall vary from the tested approved unit only in width, height or load requirements.

3.    Shall not exceed 100 percent of the proportional deflection for fiber stress of the intermediate members of

the approved unit.

4.    Shall not exceed 100 percent of the concentrated load at the juncture of the

intermediate members and the frame of the approved unit.

5.    Shall not exceed the air and water infiltration resistance of the tested approved unit.

6.    Shall not exceed the maximum cyclic pressure of the tested approved unit when tested

per TAS 203 or ASTM E 1886 and ASTM E 1996 where applicable.

ii. Non-operable windows and doors rated in this manner shall comply with the following:

1. The frame area of the alternate size unit shall not exceed the frame area of the tested approved unit.

2. Shall vary from the tested approved unit only in width, height or load requirements.

3. The maximum uniform load distribution (ULD) of any side shall be equal to the uniform load carried by the side

divided by the length of the side.

4. The ULD of any member shall not exceed the ULD of the corresponding member of the tested approved unit.

5. The ULD of each member shall be calculated in accordance with standard engineering analysis.

6. Shall not exceed the air and water infiltration resistance of the tested approved unit.

7. Shall not exceed the maximum cyclic pressure of the tested approved unit when tested per TAS 203 or  ASTM E 1886 and ASTM E 1996 where applicable.

(Mod S5582 AM R1)

2. For window and door units tested in accordance with Section 1710.5.2, structural wind load design pressures for window and door units other than the size tested in accordance with Section 1710.5.2 shall be permitted to be different than the design value of the tested unit provided such different pressures are determined by accepted engineering analysis or validated by an additional test of the window or door unit to the different design pressure in accordance with Section 1710.5.2. All components of the alternate size unit shall be the same as the tested unit. Where engineering analysis is used, the glass shall comply with Section 2403.      (Mod S5582 AM R1)  (Mod S5024-R1 / AM )

3. Custom doors.  Custom (one-of-a-kind) exterior door assemblies shall be tested by an approved testing laboratory or be engineered in accordance with accepted engineering practices.    (Mod S6007 / AS)

1710.5.1 Exterior windows and doors.  Exterior windows and sliding doors shall be tested by an approved independent testing laboratory, and shall be labeled to indicate compliance with the requirements of one on the following specifications: as conforming to ANSI/AAMA/NWWDA 101/I.S. 2 or ANSI/AAMA/WDMA/101/I.S.2/NAFS or WDMA/CSA101/I.S.2/A440 or TAS 202(HVHZ shall comply with TAS 202 utilizing ASTME 1300-98 or ASTME 1300-04 or Section 2404). The label shall state the name of the manufacturer, the approved labeling agency and the product designation as specified in AAMA/WDMA/CSA101/I.S.2/A440.  Exterior side-hinged doors shall be tested and labeled as conforming to AAMA/WDMA/CSA101/I.S.2/A440 or comply with Section 1710.5.2. Products tested and labeled as conforming to AAMA/WDMA/CSA 101/I.S.2/A440 shall not be subject to the requirements of Sections 2403.2 and 2403.3.  Exterior windows and doors shall be labeled with a permanent label, marking, or etching providing traceability to the manufacturer and product. The following shall also be required either on a permanent label or on a temporary supplemental label applied by the manufacturer: information identifying the manufacturer, the product model/series number, positive and negative design pressure rating, product maximum size, glazing thickness, impact-resistance rating if applicable, Florida Product Approval number or Miami-Dade Product Approval number, applicable test standard(s), and approved product certification agency, testing laboratory, evaluation entity or Miami-Dade Product Approval. 

The labels are limited to one design pressure rating per reference standard. The temporary supplemental label shall remain on the window or door until final approval by the building official.

Exceptions:

1. Door assemblies installed in nonhabitable areas where the door assembly and area are designed to accept water infiltration need not be tested for water infiltration.

2. Door assemblies installed where the overhang (OH) ratio is equal to or more than 1 need not be tested for water infiltration. The overhang ratio shall be calculated by the following equation: 
OH ratio = OH Length/OH Height

Where:

OH length = The horizontal measure of how far an overhang over a door projects out from door surface.

OH height = The vertical measure of the distance from the door sill to the bottom of the overhang over a door.

3. Pass-through windows for serving from a single-family kitchen, where protected by a roof overhang of 5 feet (1.5 m) or more shall be exempted from the requirements of the water infiltration test.

Glass Strength: Products tested and labeled as conforming to ANSI/AAMA/NWWDA 101/ I.S.2 or ANSI/AAMA/WDMA/101/ I.S.2/NAFS or AAMA/WDMA/CSA 101/I.S.2/A440 or TAS 202 shall not be subject to the requirements of Sections 2403.2 or 2403.3 or 2404.1. Determination of load resistance of glass for specific loads of products not tested and certified in accordance with Section 1710.5.2.1 shall be designed to comply with ASTM E 1300 in accordance with Section 2404. The temporary supplemental label shall designate the type and thickness of glass or glazing material. (Mod S5623 / AM) (Mod S5024-R1 / AM )

1710.5.2 Exterior windows and door assemblies not provided for in Section 1710.5.1. 
Exterior window and door assemblies shall be tested in accordance with ASTM E 330 or TAS202. HVHZ shall comply with TAS202. Structural performance of garage doors and rolling doors shall be determined in accordance with either ASTM E 330 or ANSI/DASMA 108, and shall meet the acceptance criteria of ANSI/DASMA 108. HVHZ shall comply with TAS202. Exterior window and door assemblies containing glass shall comply with Section 2403. The design pressure for testing shall be calculated in accordance with Chapter 16. Each assembly shall be tested for 10 seconds at a load equal to 1.5 times the design pressure (HVHZ shall comply with TAS202).

Exceptions:

1. Door assemblies installed in nonhabitable areas where the door assembly and area are designed to accept water infiltration, need not be tested for water infiltration.

2. Door assemblies installed where the overhang (OH) ratio is equal to or more than 1 need not be tested for water infiltration. The overhang ratio shall be calculated by the following equation:

OH ratio = OH Length/OH Height

where:

OH Length = The horizontal measure of how far an overhang over a door projects out from the door’s surface.

OH Height = The vertical measure of the distance from the door’s sill to the bottom of the overhang over a door.

3. Structural wind load design pressures for window and door units other than the size tested in accordance with Section 1710.5.1 shall be permitted to be different than the design value of the tested unit provided such different pressures are determined by accepted engineering analysis or validated by an additional test of the window or door unit to the different design pressure in accordance with section 1710.5.1. All components of the  alternate size unit shall be the same as the tested or labeled unit.

i. Operable windows and doors rated in this manner shall comply with the following:

1. The frame area of the alternate size unit shall not exceed the frame area of the tested approved unit.

2. Shall vary from the tested approved unit only in width, height or load requirements.

3. Shall not exceed 100 percent of the proportional deflection for fiber stress of the intermediate members of the approved unit.

4. Shall not exceed 100 percent of the concentrated load at the juncture of the intermediate members and the frame of the approved unit.

5. Shall not exceed the air and water infiltration resistance of the tested approved unit.

6. Shall not exceed the maximum cyclic pressure of the tested approved unit when tested per TAS 201 and TAS 203 or ASTM E 1886 and ASTM E 1996 where applicable.

ii. Non-operable windows and doors rated in this manner shall comply with the following:

1. The frame area of the alternate size unit shall not exceed the frame area of the tested approved unit.

2. Shall vary from the tested approved unit only in width, height or load requirements.

3. The maximum uniform load distribution (ULD) of any side shall be equal to the uniform load carried by the side divided by the length of the side.

4. The ULD of any member shall not exceed the ULD of the corresponding member of the tested approved unit.

5. The ULD of each member shall be calculated in accordance with standard engineering analysis.

6. Shall not exceed the air and water infiltration resistance of the tested approved unit.

7. Shall not exceed the maximum cyclic pressure of the tested approved unit when tested per TAS 201 and 203 or ASTM E 1886 and ASTM E 1996 where applicable.

4. For window and door units tested in accordance with Section 1710.5.2, structural wind load design pressures for window and door units other than the size tested in accordance with Section 1710.5.2 shall be permitted to be different than the design value of the tested unit provided such different pressures are determined by accepted engineering analysis or validated by an additional test of the window or door unit to the different design pressure in accordance with Section 1710.5.2. All components of the alternate size unit shall be the same as the tested unit. Where engineering analysis is used, the glass shall comply with Section 2403, and sub-section i and ii of section 3) above.

(Mod S5024-R1 / AM ) (Mod S5325 / AS)

1710.5.2.1 Sectional garage doors and rolling doors. Sectional garage doors and rolling doors shall be tested for determination of structural performance under uniform static air pressure difference in accordance with ANSI/DASMA 108, ASTM E 330 Procedure A, or TAS 202. For sectional garage doors and rolling doors tested in accordance with ASTM E 330, acceptance criteria shall be in accordance with ANSI/DASMA 108. (HVHZ shall comply with TAS 202.) Design pressures shall be determined from Table 1609.7(1) or ASCE 7. The design pressures, as determined from ASCE 7, are permitted to be multiplied by 0.6.    (Mod S5325 / AS)

1710.5.5 2.1.1 Garage door labeling. Garage doors shall be labeled with a permanent label provided by the garage door manufacturer. The label shall identify the garage door manufacturer, the garage door model/series number, the positive and negative design pressure rating, indicate impact rated if applicable, the installation instruction drawing reference number, the Florida Product Approval or Miami-Dade Product Approval number if applicable, and the applicable test standards. The required garage door components for an approved garage door assembly may be indicated using a checklist form on the label. If a checklist format is used on the label, the door installer or the garage door manufacturer shall mark the selected components on the checklist that are required to assemble an approved garage door system. (Mod S5324 / AS)

1710.5.3 Comparative analysis of operative windows and glazed doors may be made, provided the proposed unit complies with the following:

1. Shall always be compared with a tested and currently approved unit.

2. Varies only in width, height and/or load requirements.

3. Shall not exceed 100 percent of the proportional deflection for fiber stress of the intermediate members of the approved unit.

4. Shall conform as to extruded members, reinforcement and in all other ways with the tested approved unit.

5. Shall not exceed 100 percent of the concentrated load at the juncture of the intermediate members and the frame of the approved unit.

6. Shall not permit more air and water infiltration than the approved unit based on the height above grade.

7. Compared unit shall not exceed the maximum cyclic pressure when tested per TAS201 and TAS 203 or ASTM E 1886 and ASTM E 1996. (Mod S5024-R1 / AM )

1710.5.4 Comparative analysis of fixed glass windows may be made provided the proposed unit complies with the following:

1. Shall always be compared with a tested and currently approved unit.

2. Varies only in width, height and/or load requirements.

3. The design is identical in all respects. e.g., extrusions, glazing system, joinery, fasteners, etc.

4. Shall not permit more air and water infiltration than the approved unit based on height above grade.

5. The maximum uniform load distribution (ULD) of any side is equal to the uniform load carried by the side divided by the length of the side.

6. The ULD of any member must not exceed the ULD of the corresponding member of the tested window.

7. The uniform load distribution on each member shall be calculated in accordance to Section 2, Engineering Design Rules, of the AAMA 103.3 Procedural Guide.

8.  Compared unit shall not exceed the maximum cyclic pressure when tested per TAS 201 and TAS 203 or ASTM E 1886 and ASTM E 1996. (Mod S5024-R1 / AM )

1710.5.5 Mullions. Mullions or mulled fenestration assemblies shall be tested by an approved testing laboratory in accordance with either ASTM E 330, or TAS 202 (HVHZ shall comply with TAS 202), or shall be engineered using accepted engineering practice. Mullions tested as stand-alone units or qualified by engineering shall use performance criteria cited in Sections 1710.5.3.1, 1710.5.3.2 and 1710.5.3.3. (Mod S5024-R1 / AM )

1710.5.5.1 Load transfer. Mullions shall be designed to transfer the design pressure loads applied by the window and door assemblies to the rough opening substrate. (Mod S5024-R1 / AM )

1710.5.5.2 Deflection. Mullions shall be capable of resisting the design pressure loads applied by the window and door assemblies to be supported without deflecting more than L/175, where L is the span of the mullion in inches. (Mod S5024-R1 / AM )

1710.5.5.3 Structural safety factor. Mullions that are tested by an approved testing laboratory shall be capable of resisting a load of 1.5 times the design pressure loads applied by the window and door assemblies to be supported. Mullions that are qualified by engineering shall be capable of resisting the design pressure loads applied by the window and door assemblies to be supported without exceeding the allowable stress of the mullion elements. (Mod S5024-R1 / AM )

1710.5.6 Glazed curtain wall, window wall and storefront systems shall be tested in accordance with the requirements of this section and the Laboratory Test requirements of the American Architectural Manufacturers Association (AAMA) Standard 501, HVHZ shall comply with Section 2411.3.2.1.1. (Mod S5024-R1 / AM )

1710.5.7 Door components evaluated by an approved product evaluation entity, certification agency, testing laboratory or engineer may be interchangeable in exterior door assemblies provided that the door components provide equal or greater structural performance as demonstrated by accepted engineering practices.   (Mod S6012 / AS)

1710.6 Skylights and sloped glazing. Unit skylights and tubular daylighting devices (TDDs) shall comply with the requirements of Section 2405. All other Skylights and sloped glazing shall comply with the requirements of Chapter 24. All skylights and sloped glazing in the HVHZ shall comply with TAS202. (Mod S5636-R1 / AM) (Mod S5635 / AS)

1710.7 Test specimens. Test specimens and construction shall be representative of the materials, workmanship and details normally used in practice. The properties of the materials used to construct the test assembly shall be determined on the basis of tests on samples taken from the load assembly or on representative samples (when TAS202 is used, a minimum of three specimens) of the materials used to construct the load test assembly. Required tests shall be conducted or witnessed by an approved agency. (Mod S5024-R1 / AM )

Section 1710 – Preconstruction Load Tests

Add Section 1710.8 to read as shown:

1710.8 Impact resistant coverings.

1710.8.1 Labels. A permanent label shall be provided by the product approval holder on all impact resistant coverings.

1710.8.2 The following information shall be included on the labels on impact resistant coverings:

1. Product approval holder name and address.

2. All applicable methods of approval. Methods of approval include, but are not limited to Miami-Dade NOA; Florida Building Commission, TDI Product Evaluation; ICC-ES.

3. The test standard or standards specified at Section 1609.1.2, including standards referenced within the test standards specified at Section 1609.1.2 used to demonstrate code compliance.

4. For products with a Florida Product Approval Number or a Miami-Dade County Building and Neighborhood Compliance Department Notice of Acceptance Number (NOA), such numbers shall be included on the label.

1710.8.3 Location of label. The location of the label on the impact resistant covering shall be as follows:

1. Accordions: Bottom of the locking bar or center mate facing the exterior or outside.

2. Rollup: On the bottom of the hood facing the exterior or outside or on the bottom slat facing the exterior or outside.

3. Bahama Awning or Colonial Hinged: On the bottom, placed on the back of the shutter.

4. Panels: For metal and plastic panels the label may be embossed or printed spaced not more than every three (3) lineal feet on each panel. The label shall be applied by the holder of the product approval and shall face the exterior or outside.

5.Framed products: The label shall be on the side or bottom facing the exterior or outside.

6. Labels on all other products shall face the exterior or outside.

1710.8.4 Installation. All impact resistant coverings shall be installed in accordance with the manufacturer’s installation instructions and in accordance with the product approval. Installation instructions shall be provided and shall be available to inspection personnel on the job site. Opening protection components, fasteners, and other parts evaluated by an approved product evaluation entity, certification agency, testing laboratory, architect, or engineer and approved by the holder of the product approval may be interchangeable in opening protection assemblies provided that the opening protection component(s) provide equal or greater structural performance and durability as demonstrated by testing in accordance with approved test standards.

(Mod S5712 / AS)

Section 1710 – Preconstruction Load Tests

Add Section 1710.9 to read as shown:

1710.9 Soffit.

1710.9.1 Product Approval. Manufactured soffit materials and systems shall be subject to statewide or local product approval as specified in FAC Rule 61G-20. The net free area of the manufactured soffit material or system shall be included in the product approval submittal documents.

1710.9.2 Labels. Individual manufactured soffit pieces shall be marked at not more than four feet on center with a number or marking that ties the product back to the manufacturer.

1710.9.3 The following information shall be included on the manufactured soffit material packaging or on the individual manufactured soffit material or system pieces:

1. Product approval holder and/or manufacturer name and city and state of manufacturing plant.

2. Product model number or name.

3. Method of approval and approval numbers as applicable. Methods of approval include, but are not limited to: Florida Building Commission FL #; Miami-Dade NOA; TDI Product Evaluation; and, ICC-ES.

4.  The test standard or standards specified in Chapter 14 used to demonstrate code compliance.

5.  The net free area shall be included on the packaging or label.

(Mod S5736 / AS)

Section 1710 – Preconstruction Load Tests

Add Section 1710.9.4 to read as shown:

1710.9.4  Installation. All manufactured soffit materials shall be installed in accordance with the manufacturer’s installation instructions and in accordance with the product approval. Installation instructions shall be provided and shall be available to inspection personnel on the job site. Soffit pieces, components, fasteners, and other parts evaluated by an approved product evaluation entity, certification agency, testing laboratory, architect, or engineer and approved by the holder of the product approval may be interchangeable in manufactured soffit systems provided that the soffit system component or components provide equal or greater structural performance and durability as demonstrated by testing in accordance with approved test standards.

All exterior wall coverings and soffits shall be capable of resisting the design pressures specified for walls for components and cladding loads in accordance with Section 1609.1. Manufactured soffits shall be tested at 1.5 times the design pressure.

(Mod S5737 / AS)

Section 1710 – Preconstruction Load Tests

Add Section 1710.10 to read as shown:

1710.10 1715.5.4.2 Masonry, concrete or other structural substrate. Where the wood shim or buck thickness is less than 11/2 inches (38 mm), window and door assemblies shall be anchored through the main frame or by jamb clip or subframe system, in accordance with the manufacturer’s published installation instructions. Anchors shall be securely fastened directly into the masonry, concrete or other structural substrate material. Unless otherwise tested, bucks shall extend beyond the interior face of the window or door frame such that full support of the frame is provided. Shims shall be made from materials capable of sustaining applicable loads, located and applied in a thickness capable of sustaining applicable loads. Anchors shall be provided to transfer load from the window or door frame to the rough opening substrate.

Where the wood buck thickness is 11/2 inches (38 mm) or greater, the buck shall be securely fastened to transfer load to the masonry, concrete or other structural substrate and the buck shall extend beyond the interior face of the window or door frame. Window and door assemblies shall be anchored through the main frame or by jamb clip or subframe system or through the flange to the secured wood buck in accordance with the manufacturer’s published installation instructions. Unless otherwise tested, bucks shall extend beyond the interior face of the window or door frame such that full support of the frame is provided. Shims shall be made from materials capable of sustaining applicable loads, located and applied in a thickness capable of sustaining applicable loads. Anchors shall be provided to transfer load from the window or door frame assembly to the secured wood buck.

(Mod S5760-R1 / AM)

Section 1711 Material and Test Standards 
Change Section 1711 to read as shown:

1711.1 Joist hangers and connectors. Testing of joist hangers and similar connectors shall be in accordance with either Sections 1711.1.1 through or 1711.1.32, as applicable.

1711.1.1 Test Procedure Using ASTM D 7147. The allowable load of joist hangers and similar connectors shall be permitted to be determined using ASTM D 7147.

1711.1.1.2 Test Procedure using ASTM D 1761 General. The allowable vertical load-bearing capacity, torsional moment capacity and deflection characteristics of joist hangers and similar connectors  shall be permitted to be determined in accordance with ASTM D 1761 using lumber having a specific gravity of 0.49 or greater, but not greater than 0.55, as determined in accordance with AF&PA NDS for the joist and headers.

Exception: The joist length shall not be required to exceed 24 inches (610 mm).

1711.1.2.1 Vertical load capacity for joist hangers and similar connectors. The vertical load-bearing capacity for the joist hanger or connector shall be determined by testing a minimum of three joist hanger or connector  assemblies as specified in ASTM D 1761. If the ultimate vertical load for any one of the tests varies more than 20 percent from the average ultimate vertical load, at least three additional tests shall be conducted. The allowable vertical load-bearing of the joist hanger shall be the lowest value determined from the following:

1. The lowest ultimate vertical load for a single hanger or connector from any test divided by three (where three tests are conducted and each ultimate vertical load does not vary more than 20 percent from the average ultimate vertical load).

2. The average ultimate vertical load for a single hanger or connector from all tests divided by three (where six or more tests are conducted).

3. The average from all tests of the vertical loads that produce a vertical movement of the joist with respect to the header of 1/8 inch (3.2 mm).

4. The sum of the allowable design loads for nails or other fasteners utilized to secure the joist hanger or connector to the wood members and allowable bearing loads that contribute to the capacity of the hanger.

5. The allowable design load for the wood members forming the connection.

1711.1.2.1.2 Design value modifications for joist hangers and connectors. Allowable design values for joist hangers and connectors  that are determined by Item 4 or 5 in Section 1711.1.2.1 shall be permitted to be modified by the appropriate load duration factors as specified in AF&PA NDS but shall not exceed the direct loads as determined by Item 1, 2 or 3 in Section 1711.1.2.1. Allowable design values determined by Item 1, 2 or 3 in Section 1711.1.2.1 shall not be modified by load duration factors.

1711.1.2.3 Torsional moment capacity for joist hangers. The torsional moment capacity for the joist hanger shall be determined by testing at least three joist hanger assemblies as specified in ASTM D 1761. The allowable  torsional moment of the joist hanger shall be the average torsional moment at which the lateral movement of the top or bottom of the joist with respect to the original position of the joist is 1/8 inch (3.2 mm).

1711.2 Concrete and clay roof tiles. Testing of concrete and clay roof tiles shall be in accordance with Sections 1711.2.1 and 1711.2.2, as applicable.

1711.2.1 Overturning resistance. Concrete and clay roof tiles shall be tested to determine their resistance to overturning due to wind in accordance with SBCCI SSTD 11 or TAS 108 (high-velocity hurricane zones shall comply with TAS 108) and Chapter 15.

1711.2.2 Wind tunnel testing. Where concrete and clay roof tiles do not satisfy the limitations in Chapter 16 for rigid tile, a wind tunnel test shall be used to determine the wind characteristics of the concrete or clay tile roof covering in accordance with SBCCI SSTD 11 or TAS 108 (high-velocity hurricane zones shall comply with TAS 108) and Chapter 15.

(Mod S6023-R1 / AM)

(Mod S5024-R1 / AM )

Chapter 18 – Soils and Foundations

Section 1801 – General

Change Section 1801.1 to read as shown:

1801.1 Scope. The provisions of this chapter shall apply to building and foundation systems.

Exception: Buildings and structures located within the high-velocity hurricane zone shall comply with the provisions of Section 1805, and Sections 1816 through 1834.

Exception: Buildings and structures located within the high-velocity hurricane zone shall comply with the provisions of Section 1805, and Sections 1816 through 1834.and as applicable in flood hazard areas, Section 1612.

(Mod S4930 / AS)

(Mod SP5263 / AS)

Section 1801 – General

Change Section 1801.2 to read as shown:

1801.2 Design basis. Allowable bearing pressures, allowable stresses and design formulas provided in this chapter shall be used with the allowable stress design load combinations specified in Section 1605.3 the HVHZ shall comply with Section 1618.9. The quality and design of materials used structurally in excavations and foundations shall comply with the requirements specified in Chapters 16, 19, 21, 22 and 23 of this code. Excavations and fills shall also comply with Chapter 33.

(Mod S4934 / AS)

Section 1804 – Excavation, Grading and Fill

Change Section 1804.4 to read as shown:

1804.4 Grading and fill in flood hazard areas. In flood hazard areas established in Section 1612.3, grading and/or fill shall not be approved:

1. Unless such fill is placed, compacted and sloped to minimize shifting, slumping and erosion during the rise and fall of flood water and, as applicable, wave action.

2. In floodways, unless it has been demonstrated through hydrologic and hydraulic analyses performed by a registered design professional in accordance with standard engineering practice that the proposed grading or fill, or both, will not result in any increase in flood levels during the occurrence of the design flood.

3. In flood hazard areas subject to high-velocity wave action coastal high hazard areas, unless such fill is conducted and/or placed to avoid diversion of water and waves toward any building or structure.

4. Where design flood elevations are specified but floodways have not been designated, unless it has been demonstrated that the cumulative effect of the proposed flood hazard area encroachment, when combined with all other existing and anticipated flood hazard area encroachment, will not increase the design flood elevation more than 1 foot (305 mm) at any point.

(Mod SP5274 / AS)

Section 1806 – Presumptive Load Bearing Values of Soils

Change Section 1806.1 to read as shown:

1806.1 Load combinations. The presumptive load-bearing values provided in Table 1806.2 shall be used with the allowable stress design load combinations specified in Section 1605.3; the HVHZ shall comply with Section 1618.9. The values of vertical foundation pressure and lateral bearing pressure given in Table 1806.2 shall be permitted to be increased by one-third where used with the alternative basic load combinations of Section 1605.3.2; the HVHZ shall comply with Section 1618.9 that include wind or earthquake loads.

(Mod S4935 / AS)

Section 1807 – Foundation Walls, Retaining Walls and Embedded Posts and Poles

Change Section 1807.2 to read as shown:

1807.2 Retaining walls. Retaining walls shall be designed in accordance with Sections 1807.2.1 through 1807.2.3 4.

1807.2.1 - 1807.2.3 (No change)

1807.2.4 Reinforced masonry retaining walls. Vertical reinforcement for masonry retaining walls shall comply with Table 1807.2.4 or shall be designed in accordance with TMS 402/ACI 530/ASCE 5. Masonry shall be fully grouted with a minimum f'm of 1,500 psi (10 343 kPa). Mortar for masonry shall be Type M or S and laid in running bond. The specified location of the reinforcement shall equal or exceed the effective depth distance, d, noted in Table 1807.2.4 and shall be measured from the exposed side of the wall to the center of the vertical reinforcement. Footings for reinforced masonry retaining walls shall be designed in accordance with ACI 318.

TABLE 1807.2.4
REINFORCEMENT FOR MASONRY RETAINING WALLSa

| Nominal Wall thickness [(in.) (mm)] | Wall depth, H, ft. (m) | Reinforcement size & spacing for equivalent fluid weight of soil, pcf (kN/m3), of: |  |  |
| --- | --- | --- | --- | --- |
|  |  | 30 (4.7) | 45 (7.1) | 60 (9.4) |
|  | 4.0 (1.2) | #4 at 64 in. | #4 at 40 in. | #4 at 32 in. |
|  | 4.7 (1.4) | #4 at 40 in. | #4 at 24 in. | #4 at 16 in. |
| 8 (203) | 5.3 (1.6) | #4 at 24 in. | #4 at 16 in. | #5 at 16 in. |
|  | 6.0 (1.8) | #5 at 24 in. | #6 at 16 in. | #8 at 16 in. |
|  | 6.7 (2.0) | #5 at 16 in. | #6 at 8 in. | — |
|  | 4.0 (1.2) | #4 at 72 in. | #4 at 64 in. | #4 at 48 in. |
|  | 4.7 (1.4) | #4 at 56 in. | #4 at 40 in. | #4 at 24 in. |
|  | 5.3 (1.6) | #4 at 40 in. | #4 at 24 in. | #4 at 16 in. |
| 10 (254) | 6.0 (1.8) | #4 at 24 in. | #4 at 16 in. | #5 at 16 in. |
|  | 6.7 (2.0) | #4 at 16 in. | #5 at 16 in. | #6 at 16 in. |
|  | 7.3 (2.2) | #5 at 24 in. | #6 at 16 in. | #6 at 8 in. |
|  | 8.0 (2.4) | #5 at 16 in. | #6 at 8 in. | — |
|  | 4.0 (1.2) | #4 at 72 in. | #4 at 72 in. | #4 at 64 in. |
|  | 4.7 (1.4) | #4 at 72 in. | #4 at 48 in. | #4 at 40 in. |
|  | 5.3 (1.6) | #4 at 48 in. | #4 at 32 in. | #4 at 24 in. |
|  | 6.0 (1.8) | #4 at 32 in. | #4 at 24 in. | #4 at 16 in. |
| 12 (305) | 6.7 (2.0) | #4 at 24 in. | #4 at 16 in. | #5 at 16 in. |
|  | 7.3 (2.2) | #4 at 16 in. | #5 at 16 in. | #6 at 16 in. |
|  | 8.0 (2.4) | #5 at 24 in. | #5 at 16 in. | #7 at 16 in. |
|  | 8.7 (2.7) | #5 at 16 in. | #7 at 16 in. | #7 at 8 in. |
|  | 9.3 (2.8) | #6 at 16 in. | #7 at 8 in. | — |

- Based on fully grouted masonry; f'm = 1500 psi (10.3 MPa); d = 5 in., 7 in. and 9 in. (127, 178 and 229 mm) for wall thicknesses of 8, 10, and 12 in. (203, 254, and 305 mm), respectively; level backfill to top of wall.

(Mod S5958 / AS)

Section 1808 – Foundations

Change Section 1808.3 to read as shown:

1808.3 Design loads. Foundations shall be designed for the most unfavorable effects due to the combinations of loads specified in Section 1605.2 or 1605.3; the HVHZ shall comply with Section 1618.9. The dead load is permitted to include the weight of foundations and overlying fill. Reduced live loads, as specified in Sections 1607.10 and 1607.12 shall be permitted to be used in the design of foundations.

(Mod S5007 / AS)

Florida Specific Amendment / Proposed Modification

Section 1816 – Termite Protection

Add Section 1816 to read as shown:

1816.1 Termite protection.  Termite protection shall be provided by registered termiticides, including soil applied pesticides, baiting systems, and pesticides applied to wood, or other approved methods of termite protection labeled for use as a preventative treatment to new construction. See Section 202, Registered Termiticide. Upon completion of the application of the termite protective treatment, a certificate of compliance shall be issued to the building department by the licensed pest control company that contains the following statement: “The building has received a complete treatment for the prevention of subterranean termites. Treatment is in accordance with rules and laws established by the Florida Department of Agriculture and Consumer Services.”

1816.1.1 If soil treatment is used for subterranean termite prevention, the initial chemical soil treatment inside the foundation perimeter shall be done after all excavation, backfilling and compaction is complete.

1816.1.2 If soil treatment is used for subterranean termite prevention, soil area disturbed after initial chemical soil treatment shall be retreated with a chemical soil treatment, including spaces boxed or formed.

1816.1.3 If soil treatment is used for subterranean termite prevention, space in concrete floors boxed out or formed for the subsequent installation of plumbing traps, drains or any other purpose shall be created by using plastic or metal permanently placed forms of sufficient depth to eliminate any planned soil disturbance after initial chemical soil treatment.

1816.1.4 If soil treatment is used for subterranean termite prevention, chemically treated soil shall be protected with a minimum 6 millimeter vapor retarder to protect against rainfall dilution. If rainfall occurs before vapor retarder placement, retreatment is required. Any work, including placement of reinforcing steel, done after chemical treatment until the concrete floor is poured, shall be done in such manner as to avoid penetrating or disturbing treated soil.

1816.1.5 If soil treatment is used for subterranean termite prevention, concrete overpour or mortar accumulated along the exterior foundation perimeter shall be removed prior to exterior chemical soil treatment, to enhance vertical penetration of the chemicals.

1816.1.6 If soil treatment is used for subterranean termite prevention, chemical soil treatments shall also be applied under all exterior concrete or grade within 1 foot (305 mm) of the primary structure sidewalls. Also, a vertical chemical barrier shall be applied promptly after construction is completed, including initial landscaping and irrigation/sprinkler installation. Any soil disturbed after the chemical vertical barrier is applied shall be promptly retreated.

1816.1.7 If a registered termiticide formulated and registered as a bait system is used for 	subterranean termite prevention, Sections 1816.1.1 through 1816.1.6 do not apply; 	however, a signed contract assuring the installation, maintenance and monitoring of the 	baiting system that is in compliance with the requirements of Chapter 482, F.S.  for a 	minimum of five years from the issue of the certificate of occupancy shall be provided to 	the building official prior to the pouring of the slab, and the system must be installed 	prior to 	final building approval. If the baiting system directions for use require a monitoring phase 	prior to installation of the pesticide active ingredient, the installation of the monitoring phase 	components shall be deemed to constitute installation of the system.    (Mod SP5801 / AS)

1816.1.8   If a registered termiticide formulated and registered as a wood treatment is used for subterranean termite prevention, Sections 1816.1.1 through 1816.1.6 do not apply.  Application of a wood treatment termiticide shall be as required by label directions for use, and must be completed prior to final building approval.  Changes in framing or additions to  framing in areas of the structure requiring treatment that occur after the initial wood treatment must be treated prior to final building approval.

1816.2 Penetration. Protective sleeves around piping penetrating concrete slab-on-grade floors shall not be of cellulose-containing materials. If soil treatment is used for subterranean termite protection, the sleeve shall have a maximum wall thickness of 0.010 inch, and be sealed within the slab using a non-corrosive clamping device to eliminate the annular space between the pipe and the sleeve. No termiticides shall be applied inside the sleeve.

Chapter 19 - Concrete

Section 1901.1 Scope

Change Section 1901.1 to read as shown:

- 1901.1 Scope.  The provisions of this chapter shall govern the materials, quality control, design and construction of concrete used in structures.

Exception: Buildings and structures located within the high-velocity hurricane zone shall comply with the provisions of Sections 1917 and 1919 through 1929.

(Mod S4943 / AS)

Section 1908 – Anchorage to Concrete – Allowable Stress Design

Change Section 1908.4 to read as shown:

1908.4 Increase in allowable load. Increase of the values in Table 1908.2 by one-third is permitted where the provisions of Section 1605.3.2; the HVHZ shall comply with Section 1618.9 permit an increase in allowable stress for wind loading.

(Mod S4942 / AS)

Section 1913 – Special Wind Provisions for Concrete

Add Section 1913 to read as shown:

SECTION 1913

SPECIAL WIND PROVISIONS FOR CONCRETE

1913.1 Reinforced concrete components. The design and construction of reinforced concrete components for buildings sited in areas where the ultimate design wind speed, Vult, is greater than 115  (45 m/s) in accordance with Figure 1609A, 1609B, or 1609C shall conform to the requirements of ACI 318 or with Section 1609.1.1, Exception 1, as applicable, except as modified in this section.

1913.2 Insulated concrete form wall. Insulated concrete form (ICF) wall construction for buildings shall be in accordance with ACI 318 or with Section 1609.1.1, Exception 1, as applicable.

1913.3 Gable endwalls.

1913.3.1 General. Gable endwalls shall be structurally continuous between points of lateral support.

1913.3.2 Cathedral endwalls. Gable endwalls adjacent to cathedral ceilings shall be structurally continuous from the uppermost floor to ceiling diaphragm or to the roof diaphragm.

(Mod S5619 / AS)

Florida Specific Amendment

Sections 1914 – 1916

Add Sections 1914 – 1916 to read as shown:

SECTIONS 1914 - 1916

RESERVED

Section 1917 – Lightweight Insulating Concrete

Add Section 1917 to read as shown:

SECTION 1917

LIGHTWEIGHT INSULATING CONCRETE ROOFS

1917.1   Lightweight insulating concrete. Material produced with or without aggregate additions to portland cement, water and air to form a hardened material possessing insulating qualities, which, when oven dried shall have a unit weight no greater than 50 pcf (801 kg/m3).

1917.1.1   Aggregate lightweight insulating concrete. Insulating concrete formulated predominantly with perlite or vermiculite aggregate having a minimum compressive strength of 125 psi (861.8 kPa) when tested in compliance with ASTM C 495.

1917.1.2   Cellular lightweight insulating concrete. Insulating concrete formulated by mixing a hydrated cementitious matrix around non-interconnecting air cells created by the addition of preformed foam formed from hydrolyzed proteins or synthetic surfactants. The cured cellular lightweight insulating concrete shall have minimum compressive strength of 160 psi (1103 kPa) when tested in compliance with ASTM C 495 and C 796.

1917.1.3   Cellular/aggregate (hybrid) lightweight insulating concrete. Insulated concrete formulated by combining preformed foam with low density aggregates to impart properties of both aggregate and cellular lightweight insulating concrete. It shall have a minimum compressive strength of 200 psi (1379 kPa) when tested in compliance with ASTM C 495 and C 796.

1917.2   Inspection.

1917.2.1  Application of all lightweight insulating concrete roof decks shall be by applicators approved by the lightweight insulating concrete deck manufacturer. Product Approval shall be required for all lightweight insulating concrete systems.

1917.2.2 The permit holder shall notify the building official 48 hours prior to the pouring of lightweight insulating concrete.

1917.2.3 The permit holder shall make available to the building official a job log with the following minimum items.

1. Cast density recordings/hour.

2. Product evaluation for application.

3. Date and job locations identified.

4. Results of any field test conducted.

1917.2.4 Once the roof deck system can support foot traffic, the building official shall have clear access and clear path at his option for inspection of lightweight insulating concrete.

1917.3   Testing.  The building official may require tests of the lightweight insulating concrete to confirm the fastener withdrawal resistance, compressive strength or drainage ability.

1917.3.1   Existing roof assemblies to receive lightweight insulating concrete other than galvanized G-90 steel deck or structural concrete deck shall be tested for uplift for adhesion to the substrate to confirm compliance with design pressure.

1917.4   Materials and limitations of use. Lightweight insulating concrete, in conjunction with galvanized formed steel sheets, shall not be used as a roof deck in areas where highly corrosive chemicals are used or stored.

1917.4.1 Lightweight insulating concrete shall be poured over bottom slotted galvanized (G-90) steel decking as follows; cellular, 0.5 percent open; hybrid, 0.75 percent open, aggregate 1.5 percent open. No lightweight insulating concrete shall be poured over a painted or non-galvanized steel deck.

1. Lightweight insulating concrete over structural concrete slabs, twin tees, precast units or other non-venting substrates shall be vented to allow the escape of excess moisture.

1917.4.2   Minimum thickness of lightweight insulating concrete shall be 2 inches (51 mm) over the top plane of the substrate unless otherwise specified in the Product Approval. Lightweight insulating concrete shall be of sufficient thickness to receive the specified base ply fastener length.

1917.4.3   Galvanized coatings of formed steel sheets shall be in accordance with ASTM A 525 with a minimum coating designation of G-90. Base steel shall conform to ASTM A 446, Grade A, B, C, D or greater and ASTM A 611 C, D or E.

1917.4.4   Chemical admixtures shall be in compliance with ASTM C 494. Calcium chloride or any admixture containing chloride salts shall not be used in insulating concrete. Fiber reinforcement may be used to control cracking. Mineral admixtures shall conform to ASTM C 618.

1917.4.5   Vermiculite or perlite shall be in compliance with ASTM C 332, Group I. Foam concentrates shall be in compliance with ASTM C 796 and ASTM C 869.

1917.4.6   Mixing, placing and finishing shall be in compliance with the deck system Product Approval. Slurry coating, two-density casting and double casting shall be acceptable per the specific manufacturer's recommendations.

1917.4.7   If the lightweight insulating concrete deck is to receive Product Approval for a direct-adhered roofing system, the deck surface shall be prepared to the requirements set forth in the roof system Product Approval.

1917.4.8   All base ply fasteners for use in lightweight insulating concrete roof decks shall have a Product Approval for use with the specific lightweight insulating concrete roof system in compliance with manufacturer's recommendations and the design pressure of Section 1609.

1917.4.9   The lightweight insulating concrete fastener withdrawal shall have a minimum resistance for new pours of

1. 60 pounds (267 N) in 28 days when the fastener is installed and allowed to age in the concrete.

2. 40 pounds (178 N) at time of roofing.

1917.4.10 Insulation board with lightweight insulating concrete shall conform to Type I expanded polystyrene insulation as defined in ASTM C 578.

1. Packaged insulation board delivered to the job site shall comply with the provisions of Section 2603.2 or Section 2613.1.3.

2. Installation of insulating board in conjunction with lightweight insulating concrete shall comply with uplift requirements set forth in Section 1609. Insulation panels shall be placed in a minimum 1/8-inch (3.2 mm) slurry of insulating concrete while the material is still in a plastic state. The insulating concrete shall be cast over the insulation boards according to the insulating concrete manufacturer's Product Approval. Insulation panels shall be provided with holes and/or slots for keying and venting.

1917.4.11 Reinforcing mesh shall be provided as required to meet fire-rating and/or special structural design requirements. Refer to a specific Product Approval for the specific requirements applicable to the product being installed.

(Mod R5742-R1 / AM)

Chapter 20 – Aluminum

Section 2001 – General

Change Section 2001.1 to read as shown:

2001.1 Scope. This chapter shall govern the quality, design, fabrication and erection of aluminum. The quality, design, fabrication and erection of aluminum used structurally in buildings or structures shall conform to good engineering practice, the provisions of this chapter and other applicable requirements of this code.

(Mod S5795 / AS)

Exception: Buildings and structures located within the high-velocity hurricane zone shall comply with the provisions of Section 2003.

Section 2002 – Materials

Change Section 2002 to read as shown:

2002.1 General. Aluminum used for structural purposes in buildings and structures shall comply with AA ASM 35 and AA ADM 1. The nominal loads shall be the minimum design loads required by Chapter 16. The use of aluminum alloys not listed in the manual shall be permitted provided their standard of performance is not less than those required in the manual and the performance is substantiated to the satisfaction of the building official.

2002.2.1 Definitions

PRIMARY MEMBER. Structural framing members providing structural support to other members and/or surfaces of a structure including, but not limited to beams, posts, columns, joists, structural gutters, headers, eave rail, purlins, roof brace.

SECONDARY MEMBERS. Structural framing members which do not provide basic support for the entire structure, generally including, but not limited to, such members as kickplate rails, chair rails, roof or wall panels, wall brace.

STRUCTURAL MEMBERS. Members or sections that provide support to an assembly and/or resist applied loads.

2002.3 Screen enclosures.

2002.3.1 Actual wall thickness of extruded aluminum members shall be not less than 0.040 inch (1 mm).

2002.3.2 Reserved.

2002.3.3 Vinyl and acrylic panels shall be removable. Removable panels shall be identified as removable by a decal. The identification decal shall essentially state “Removable panel SHALL be removed when wind speeds exceed 75 mph (34 m/s).” Decals shall be placed such that the decal is visible when the panel is installed.

2002.4 Loads. Structural members supporting screened enclosures shall be designed for wind in both of two orthogonal directions using the pressures given in Table 2002.4. Each primary member shall also be designed for a 300 pound (1.33 kN) load applied vertically downward along any 1 foot (305 mm) of any member, not occurring simultaneously with wind load.

Exception: In addition to wind pressures, purlins shall also be designed for a 200 pound (0.89 kN) load applied vertically downward along any 1 foot (305 mm) of any member, not occurring simultaneously with wind load.

2002.4.1 Design Guide. The following design guides shall be accepted as conforming to accepted engineering practices:

AAF Guide to Aluminum Construction in High Wind Areas.

2002.5 Wall panels. The minimum thickness for formed sheet aluminum structural wall panels shall be not less than 0.024 inch (0.6 mm), subject to approved tolerances.

(Mod S5795 / AS)

Section 2002 – Materials

Add Table 2002.4 to read as shown:

TABLE 2002.4

DESIGN WIND PRESSURES SCREENED ENCLOSURES a, b, f, g, h

(STRENGTH DESIGN OR LRFD ONLY)

|  | ULTIMATE DESIGN WIND SPEED Vult (mph) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 110 |  |  | 120 |  |  | 130 |  |  | 140 |  |  | 150 |  |  | 160 |  |  | 170 |  |  |
| SURFACE | Design Pressures by Exposure Category (psf) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | B | C | D | B | C | D | B | C | D | B | C | D | B | C | D | B | C | D | B | C | D |
| Horizontal Pressures on Windward Surfacesd | 17 | 24 | 28 | 20 | 28 | 33 | 23 | 32 | 38 | 27 | 38 | 44 | 31 | 43 | 51 | 36 | 49 | 58 | 40 | 56 | 66 |
| Horizontal Pressures on Leeward Surfacesd | 13 | 18 | 21 | 15 | 22 | 26 | 20 | 26 | 31 | 21 | 29 | 34 | 22 | 34 | 40 | 25 | 39 | 46 | 29 | 44 | 52 |
| Vertical Pressures on Screen Surfacesc | 4 | 7 | 8 | 6 | 8 | 9 | 6 | 9 | 11 | 8 | 11 | 12 | 9 | 12 | 14 | 10 | 14 | 16 | 11 | 15 | 18 |
| Vertical Pressures on Solid Surfacese | 14 | 19 | 23 | 17 | 23 | 27 | 20 | 27 | 32 | 23 | 32 | 37 | 25 | 36 | 42 | 29 | 41 | 48 | 33 | 46 | 54 |

For SI: 1 pound per square foot = 9.479 kN/m2.

NOTES:

a. Pressures apply to enclosures with a mean enclosure roof height of 30 feet (10 m). For other heights, multiply the pressures in this table by the factors in Table 2002.4A.

b. Apply horizontal pressures to the area of the enclosure projected on a vertical plane normal to the assumed wind direction, simultaneously inward on the windward side and outward on the leeward side.

c. Apply vertical pressures upward or downward to the area of the enclosure projected on a horizontal plane.

d. Apply horizontal pressures simultaneously with vertical pressures.

e.  Table pressures are MWFRS Loads. The design of solid roof panels and their attachments shall be based on component and cladding loads for enclosed or partially enclosed structures as appropriate.

f. Table pressures apply to 20 × 20 × 0.013" mesh screen. For 18 ×14 × 0.013" mesh screen, pressures on screen surfaces may be multiplied by 0.88. For screen densities greater than 20 × 20 × 0.013", use pressures for enclosed buildings.

g. Table pressures may be interpolated using ASCE 7 methodology.

h. For allowable stress design (ASD) pressures shall be permitted to be multiplied by 0.6.

(Mod S5905 / AS)

Section 2002 – Materials

Add Table 2002.4A to read as shown:

TABLE 2002.4A

HEIGHT ADJUSTMENT FACTORS

| MEAN ROOF HEIGHT | EXPOSURE |  |  |
| --- | --- | --- | --- |
|  | B | C | D |
| 0-15 | 1 | 0.86 | 0.89 |
| 20 | 1 | 0.92 | 0.93 |
| 25 | 1 | 0.96 | 0.97 |
| 30 | 1 | 1 | 1 |
| 35 | 1.05 | 1.03 | 1.03 |
| 40 | 1.09 | 1.06 | 1.05 |
| 45 | 1.12 | 1.09 | 1.07 |
| 50 | 1.16 | 1.11 | 1.09 |
| 55 | 1.19 | 1.14 | 1.11 |
| 60 | 1.22 | 1.16 | 1.13 |

(Mod S5789 / AS)

Section 2002 – Materials

Add Section 2002.6 to read as shown:

2002.6 Sunroom design.

2002.6.1 Sunrooms shall comply with AAMA/NPEA/NSA 2100.

2002.6.2 For the purpose of applying the criteria of the AAMA/NPEA/NSA 2100, sunrooms shall be categorized in one of the following categories by the permit applicant, design professional or the property owner where the sunroom is being constructed.

Category I: A Thermally Isolated Sunroom with walls that are either open or enclosed with insect screening or 0.5 mm (20 mil) maximum thickness plastic film. The space is defined as a non-habitable, non-conditioned sunroom.

Category II: A Thermally Isolated Sunroom with enclosed walls. The openings are permitted to be enclosed with translucent or transparent plastic or glass. The space is defined as a non-habitable, non-conditioned sunroom.

Category III: A Thermally Isolated Sunroom with enclosed walls. The openings are permitted to be enclosed with translucent or transparent plastic or glass. The sunroom fenestration complies with additional requirements for air infiltration resistance and water penetration resistance. The space is defined as a non-habitable, non-conditioned sunroom.

Category IV: A Thermally Isolated Sunroom with enclosed walls. The sunroom is designed to be heated and or cooled by a separate temperature control or system and is thermally isolated from the primary structure. The sunroom fenestration complies with additional requirements for air infiltration resistance, water penetration resistance, and thermal performance. The space is defined as a non-habitable and conditioned sunroom.

Category V: A Sunroom with enclosed walls. The sunroom is designed to be heated and or cooled and is open to the main structure. The sunroom fenestration complies with additional requirements for air infiltration resistance, water penetration resistance, and thermal performance. The space is defined as a habitable and conditioned sunroom.

(Mod S5792 / AS)

Chapter 21 – Masonry

Section 2101 – General

Change Section 2101.1 to read as shown:

2101.1 Scope.  This chapter shall govern the materials, design, construction and quality of masonry.

Exception: Buildings and structures located within the high-velocity hurricane zone shall comply with the provisions of Sections 2103-2105, 2107, 2108, 2110, 2114 and Sections 2119 through 2122.

(Mod S4957-R1 / AM)

Section 2107 – Allowable Stress Design

Section 2107.1. Change to read as shown:

2107.1 General. The design of masonry structures using allowable stress design shall comply with Section 2106 and the requirements of Chapters 1 and 2 of TMS 402/ACI 530/ASCE 5 except as modified by Sections 2107.2 through 2107.4.

Exception: Where plan review and inspections are performed by a local building department in accordance with Sections 107 and 110, the provisions of TMS 402/ACI 530/ASCE 5, Chapter 1, Section 1.19 and TMS 602/ ACI 530.1/ASCE 6 Section 1.6 shall not apply unless specified by the architect or engineer, or the building official.

(Mod S5974-R1 / AM)

Section 2107 – Allowable Stress Design

Change Section 2107.2 to read as shown:

2107.2 TMS 402/ACI 530/ASCE 5, Section 2.1. 8  7 .7.1.1, lap splices. In lieu of addition to Section 2.1. 8 . 7.7.1.1, it shall be permitted to design lap splices in accordance with Section 2107.2.1.

(Mod S5962 / AS)

Section 2107 – Allowable Stress Design

Change Section 2107.4 to read as shown:

2107.4 TMS 402/ACI 530/ASCE 5, Section 2.1.7 .3, Development of bars in tension and compression. Modify Section 2.1.7.3 as follows:

2.1.7.3 The required development length of reinforcing bars shall be determined by Equation (2- 12), but shall not be less than 12 in. (305 mm), but need not be greater than 72 db.

Equation 2-12 from TMS 402/ACI 530/ASCE 5, unchanged. Gamma factors are changed as follows:

y         =          1.0 for No. 3 (M#10) through No. 5 (M#16) bars;

y          =          1.3 1.04 for No. 6 (M#19) through No. 7 (M#22) bars; and

y          =          1.5 1.2 for No. 8 (M#25) through No. 11 (M#36) bars

(Mod S5977 / AS)

(Mod S5975 / AS)

(Mod S5963 / AS)

Section 2107 – Allowable Stress Design

Add Section 2107.5 to read as shown:

2107.5 TMS 402/ACI 530/ASCE 5, Section 2.1.7 .3, Development of bars in tension and compression. Modify Section 2.1.7.3 as follows:

2.1.7.3 The required development length of reinforcing bars shall be determined by Equation (2- 12), but shall not be less than 12 in. (305 mm), but need not be greater than 72 db.

Equation 2-12 from TMS 402/ACI 530/ASCE 5, unchanged. Gamma factors are changed as follows:

y         =          1.0 for No. 3 (M#10) through No. 5 (M#16) bars;

y          =          1.3 1.04 for No. 6 (M#19) through No. 7 (M#22) bars; and

y          =          1.5 1.2 for No. 8 (M#25) through No. 11 (M#36) bars

(Mod S5977 / AS)

Section 2107 – Allowable Stress Design

Add Section 2107.6 to read as shown:

2107.6 TMS 402/ACI 530/ASCE 5, Section 1.15 Pilasters. Modify Section 1.15 as follows:

1.15.1 Where vertical reinforcement is provided to resist axial compressive stress, lateral ties shall meet all applicable requirements of Section 1.14.1.4.

(Mod S5979 / AS)

Section 2108 – Strength Design of Masonry

Change Section 2108.1 to read as shown:

2108.1 General. The design of masonry structures using strength design shall comply with Section 2106 and the requirements of Chapters 1 and 3 of TMS 402/ACI 530/ASCE, except as modified by Section 2108.2 through 2108.3. Exceptions: 1. AAC masonry shall comply with the requirements of Chapters 1 and 8 of TMS 402/ACI 530/ASCE 5. 2. Where plan review and inspections are performed by a local building department in accordance with Sections 107 and 110, the provisions of TMS 402/ACI 530/ASCE 5, Chapter 1, Section 1.19 and TMS 602/ ACI 530.1/ASCE 6 Section 1.6 shall not apply unless specified by the architect or engineer, or the building official. ( Mod S5973-R1 / AM)

Section 2108 – Strength Design of Masonry

Add Section 2108.4 to read as shown:

2108.4 TMS 402/ACI 530/ASCE 5, Section 2.1.7.3, Development of bars in tension and compression. Modify Section 2.1.7.3 as follows:

2.1.7.3 The required development length of reinforcing bars shall be determined by Equation (2- 12), but shall not be less than 12 in. (305 mm),  but need not be greater than 72 db.

Equation 2-12 from TMS 402/ACI 530/ASCE 5, unchanged. Gamma factors are changed as follows:

y          =          1.0 for No. 3 (M#10) through No. 5 (M#16) bars;

y          =          1.3 1.04 for No. 6 (M#19) through No. 7 (M#22) bars; and

y          =          1.5 1.2 for No. 8 (M#25) through No. 11 (M#36) bars

(Mod S5980 / AS)

Section 2109 – Empirical Design of Masonry

Change Section 2109.1.1 to read as shown:

2109.1.1 Limitations. The use of empirical design of masonry shall be limited as noted in Section 5.1.2 of TMS 402/ACI 530/ASCE 5. The use of dry-stacked, surface-bonded masonry shall be prohibited in Risk Category IV structures. In buildings that exceed one or more of the limitations of Section 5.1.2 of TMS 402/ACI 530/ASCE 5, masonry shall be designed in accordance with the engineered design provisions of Section 2101.2.1, 2101.2.2 or 2101.2.3 or the foundation wall provisions of Section 1807.1.5.

Section 5.1.2.2 of TMS 402/ACI 530/ASCE 5 shall be modified as follows:

5.1.2.2 Wind  – Empirical requirements shall not apply to the design or construction of masonry for buildings, parts of buildings, or other structures to be located in areas where Vult Vasd as determined in accordance with Figures 1609A, 1609B, or 1609C Section 1609.3.1 of the Florida Building Code, Building International Building Code exceeds 115 110 mph.

(Mod S5649 / AS)

Florida Specific Amendment

Section 2114 – Termite Inspection

Add Section 2114 to read as shown:

- SECTION 2114

- TERMITE INSPECTION

- 2114.1 Cleaning.  Cells and cavities in masonry units and air gaps between brick, stone or masonry veneers and the structure shall be cleaned of all nonpreservative treated or nonnaturally durable wood, or other cellulose-containing material prior to concrete placement.

- Exception: Inorganic material manufactured for closing cells in foundation concrete masonry unit construction or clean earth fill placed in concrete masonry unit voids below slab level before termite treatment is performed.

- 2114.2 Concrete bearing ledge.  Brick, stone or other veneer shall be supported by a concrete bearing ledge at least equal to the total thickness of the brick, stone or other veneer, which is poured integrally with the concrete foundation. No supplemental concrete foundation pours which will create a hidden cold joint shall be used without supplemental treatment in the foundation unless there is an approved physical barrier. An approved physical barrier shall also be installed from below the wall sill plate or first block course horizontally to embed in a mortar joint. If masonry veneer extends below grade, a termite protective treatment must be applied to the cavity created between the veneer and the foundation, in lieu of a physical barrier.

Exception: Veneer supported by a shelf, angle or lintel secured to the foundation sidewall in accordance with TMS 402/ ACI 530/ASCE 5 /TMS 402, provided at least a 6-inch (152 mm) clear inspection space of the foundation sidewall exterior exist between the veneer and the top of any soil, sod, mulch or other organic landscaping component, deck, apron, porch, walk or any other work immediately adjacent to or adjoining the structure.

Section 2115 – Special Wind Provisions for Masonry

Add Section 2115 to read as shown:

SECTION 2115

SPECIAL WIND PROVISIONS FOR MASONRY

2115.1 Gable endwalls.

2115.1.1 General. Gable endwalls shall be structurally continuous between points of lateral support.

2115.1.2 Cathedral endwalls. Gable endwalls adjacent to cathedral ceilings shall be structurally continuous from the uppermost floor to the ceiling diaphragm or to the roof diaphragm.

(Mod S5649 / AS)

(Mod S5620 / AS)

Chapter 22 - Steel

Section 2201 General

Change Section 2201.1 to read as shown:

2201.1 Scope.  The provisions of this chapter govern the quality, design, fabrication and erection of steel used structurally in buildings or structures.

Exception: Buildings and structures located within the high-velocity hurricane zone shall 	comply with the provision of Sections 2204 through 2208 and 2214 through 2224.

(Mod S4947-R1 / AM)

Section 2204 Connections

Change Section 2204.1 to read as shown:

2204.1 Welding. The details of design, workmanship and technique for welding, inspection of welding and qualification of welding operators shall conform to the requirements of the specifications listed in Sections 2205, 2206, 2207, 2208, 2210 (see Section 2222 for HVHZ) and 2211(see Section 2222 for HVHZ). Special inspection of welding shall be provided where required by Section 1705.

(Mod S4948 / AS)

Section 2210 – Cold-Formed Steel

Add Section 2210.1.1.3 to read as shown:

2210.1.1.3 Composite slabs on steel decks. Composite slabs of concrete and steel deck shall be permitted to be designed and constructed in accordance with SDI-C, Standard for Composite Steel Floor Deck-Slabs

(Mod S4944 / AS)

Section 2212 – Gable End Walls

Add Section 2212 to read as shown:

SECTION 2212

GABLE END WALLS

2212.1 Gable endwalls. Gable endwalls shall be structurally continuous between points of lateral support.

2212.1.2 1 Cathedral endwalls. Gable endwalls adjacent to cathedral ceilings shall be structurally continuous from the uppermost floor to the ceiling diaphragm or to the roof diaphragm.

(Mod S5621 / AS)

Chapter 23 – Wood

Florida Specific Amendment

Section 2301 General

Change Section 2301.1 to read as shown:

- 2301.1 Scope.  The provisions of this chapter shall govern the materials, design, construction and quality of wood members and their fasteners.

Exception: Buildings and structures located within the high-velocity hurricane zone shall comply with the provisions of  Sections 2302, 2303.1 through 2303.1.4, 2303.1.8, 2303.2, 2304.11, 2304.13 and Sections 2314 through 2330.

(Mod S4945 / AS)

Section 2304 – General Construction Requirements

Add Section 2304.3.4 to read as shown:

2304.3.4 Gable endwalls.

2304.3.4.1 General. Gable endwalls shall be structurally continuous between points of lateral support.

2304.3.4.2 Cathedral endwalls. Gable endwalls adjacent to cathedral ceilings shall be structurally continuous from the uppermost floor to the ceiling diaphragm or to the roof diaphragm.

2304.3.4.3 Full height studs. Full height studs may be sized using the bracing at a ceiling diaphragm for determining stud length requirements.

(Mod S5622 / AS)

Florida Specific Amendment

Section 2304 – General Construction Requirements

Add Section 2304.11.10 to read as shown:

2304.11.10 Foam-plastic insulation.

- 2304.11.10.1  The provisions of Section 2603. 9 shall apply to the installation of foam plastic insulation in close proximity to the ground.

- Exception: Materials which are of naturally durable wood or are pressure treated for ground contact, and which are installed with at least 6 inches (152 mm) clear space from the structure to allow for inspection and treatment for termites.

In order to reduce chances of termite infestation, no wood, vegetation, stumps, dead roots, cardboard, trash, or other cellulose-containing material shall be buried on the building lot within 15 feet (4.6 m) of any building or the position of any building proposed to be built.

Florida Specific Amendment

Section 2304 – General Construction Requirements

Add Section 2304.13 to read as shown:

2304.13 Preparation of building site and removal of debris.

- 2304.13.1 All building sites shall be graded to provide drainage under all portions of the building not occupied by basements.

- 2304.13.2 The foundation and the area encompassed within 1 foot (305 mm) therein shall have all vegetation, stumps, dead roots, cardboard, trash, and foreign material removed and the fill material shall be free of vegetation and foreign material. The fill shall be compacted to assure adequate support of the foundation.

2304.13.3 After all work is completed, loose wood and debris shall be completely removed from under the building and within 1 foot (305 mm) thereof. All wood forms and supports shall be completely removed. This includes, but is not limited to: wooden grade stakes, forms, contraction spacers, tub trap boxes, plumbing supports, bracing, shoring, forms, or other cellulose-containing material placed in any location where such materials are not clearly visible and readily removable prior to completion of the work. Wood shall not be stored in contact with the ground under any building.

Section 2308 – Conventional Light-Frame Construction

Change Section 2308.2 to read as shown:

2308.2 Limitations.   Buildings are permitted to be constructed in accordance with the provisions of conventional light-frame construction, subject to the following limitations, and to further limitations of Sections 2308.11 and 2308.12.

1. - 3. (No Change)

4.   Ultimate Design Wind Speeds, Vult Vasd as determined in accordance with Section 1609.3.1 shall not exceed 115 100 miles per hour (mph) (44 m/s) (3-second gust).

Exception: Vasd as determined in accordance with Section 1609.3.1 shall not exceed 110 mph (48.4 m/s) (3-second gust) for buildings in Exposure Category B that are not located in a hurricane-prone region.

5. - 7. (No Change)

2308.2.1 Ultimate Nominal design wind speed greater than 115 100 mph (3-second gust). Where the Ultimate Design Wind Speed, Vult Vasd as determined in accordance with Section 1609.3.1 exceeds 115 100 mph (3-second gust), the provisions of either AF&PA WFCM or ICC 600 are permitted to be used. Wind speeds in Figures 1609A, 1609B, and 1609C shall be converted in accordance with Section 1609.3.1 for use with AF&PA WFCM or ICC 600.

(Mod S5650  / AS)

Chapter 24 – Glass and Glazing

Section 2401 – General

Change Section 2401.1 to read as shown:

2401.1 Scope.  The provisions of this chapter shall govern the materials, design, construction and quality of glass, light-transmitting ceramic and light-transmitting plastic panels for exterior and interior use in both vertical and sloped applications in buildings and structures.

Exception: Buildings and structures located within the high-velocity hurricane zone shall 	also comply with the provisions of Sections 2410 through 2415, excluding 2405.5.

(Mod S5025 / AS)

Section 2403 – General Requirements for Glass

Change Section 2403.1 to read as shown:

2403.1 Identification. Each pane shall bear the manufacturer’s mark designating the type and thickness of the glass or glazing material. With the exception of tempered glazing materials or laminated materials, Tthe identification shall not be omitted unless approved and an affidavit is furnished by the glazing contractor certifying that each light is glazed in accordance with approved construction documents that comply with the provisions of this chapter. Safety glazing shall be identified in accordance with Section 2406.2. Each pane of tempered glass, except tempered spandrel glass, shall be permanently identified by the manufacturer and each pane of laminated glass shall be permanently identified with the laminator, overall glass thickness and trade name of interlayer. The identification mark shall be acid etched, sand blasted, ceramic fired, laser etched, embossed or of a type that, once applied, cannot be removed without being destroyed. Tempered or laminated spandrel glass shall be provided with a removable paper marking by the manufacturer.

(Mod S5764 / AS)

Section 2404 – Wind, Snow, Seismic and Dead Loads on Glass

Change Section 2404.1 to read as shown:

2404.1 Vertical glass. Glass sloped 15 degrees (0.26 rad) or less from vertical in windows, curtain and window walls, doors and other exterior applications shall be designed to resist the wind loads due to ultimate design wind speed Vult in Section 1609 (HVHZ shall follow Section 1620) for components and cladding. Glass in glazed curtain walls, glazed storefronts and glazed partitions shall meet the seismic requirements of ASCE 7, Section 13.5.9. The load resistance of glass under uniform load shall be determined in accordance with ASTM E 1300.

The design of vertical glazing shall be based on the following equation:

0.6Fgw ≤  Fga 									(Equation 24-1)

where:

Fgw = Wind load on the glass due to ultimate design wind speed Vult, computed in accordance with Section 1609.

Fga = Short duration load on the glass as determined in accordance with ASTM E 1300.

Section 2404 – Wind, Snow, Seismic and Dead Loads on Glass

Change Section 2404.2 to read as shown:

2404.2 Sloped glass. Glass sloped more than 15 degrees (0.26 rad) from vertical in skylights, sunrooms, sloped roofs and other exterior applications shall be designed to resist the most critical of the following combinations of loads.

Fg = 0.6Wo – D								 (Equation 24-2)

Fg = 0.6Wi + D + 0.5 S							 (Equation 24-3)

Fg = 0.5 0.3Wi + D + S 							(Equation 24-4)

where:

D = Glass dead load psf (kN/m2).

For glass sloped 30 degrees (0.52 rad) or less from horizontal,

= 13 tg (For SI: 0.0245 tg).

For glass sloped more than 30 degrees (0.52 rad) from horizontal,

= 13 tg cos  (For SI: 0.0245 tg cos ).

Fg = Total load, psf (kN/m2) on glass.

S = Snow load, psf (kN/m2) as determined in Section 1608.

tg = Total glass thickness, inches (mm) of glass panes and plies.

Wi = Inward wind force, psf (kN/m2) due to ultimate design wind speed Vult as calculated in Section 1609.

Wo = Outward wind force, psf (kN/m2) due to ultimate design wind speed Vult, as calculated in Section 1609.

 = Angle of slope from horizontal.

Exception: The design pressure rating of unit skylights and tubular daylighting devices shall be designed determined in accordance with Section 2405.5.

The design of sloped glazing shall be based on the following equation:

Fg ≤ Fga 									(Equation 24-5)

where:

Fg = Total load on the glass determined from the load combinations above.

Fga = Short duration load resistance of the glass as determined according to ASTM E 1300 for Equations 24-2 and 24-3; or the long duration load resistance of the glass as determined according to ASTM E 1300 for Equation 24-4.

(Mod S5584-R1 / AM)

(Mod S5026 / AS)

(Mod S5636-R1 / AM)

Section 2404 – Wind, Snow, Seismic and Dead Loads on Glass

Change Sections 2404.3.1 – 2404.3.5  to read as shown:

2404.3.1 Vertical wired glass.  Wired glass sloped 15 degrees (0.26 rad) or less from vertical in windows, curtain and window walls, doors and other exterior applications shall be designed to resist the wind loads in Section 1609 (HVHZ shall comply with Section 1620) for components and cladding according to the following equation.   (Mod S5027 / AS)

0.6Fgw < 0.5 Fge 								(Equation 24-6)

where:

Fgw = Is the wind load on the glass due to ultimate design wind speed Vult, computed per Section 1609. (Mod S5584-R1 / AM)

Fge = Nonfactored load from ASTM E 1300 using a thickness designation for monolithic glass that is not greater than the thickness of wired glass.

2404.3.2 Sloped wired glass. Wired glass sloped more than 15 degrees (0.26 rad) from vertical in skylights, sunspaces, sloped roofs and other exterior applications shall be designed to resist the most critical of the combinations of loads from Section 2404.2.

For Equations 24-2 and 24-3:

Fg < 0.5 Fge 								(Equation 24-7)

For Equation 24-4:

Fg < 0.3 Fge								 (Equation 24-8)

where:

Fg = Total load on the glass, as determined by Equations 24-2, 24-3 or 24-4.

Fge = Nonfactored load from ASTM E 1300. (Mod S5584-R1 / AM)

2404.3.3 Vertical patterned glass. 
Patterned glass sloped 15 degrees (0.26 rad) or less from vertical in windows, curtain and window walls, doors and other exterior applications shall be designed to resist the wind loads in Section 1609 (HVHZ shall comply with Section 1620)  for components and cladding according to the following equation:

Fgw < 1.0 Fge 								(Equation 24-9)

where:

Fgw = Wind load on the glass due to ultimate design wind speed Vult computed per Section 1609 (HVHZ shall comply with Section 1620).

Fge = Nonfactored load from ASTM E 1300. The value for patterned glass shall be based on the thinnest part of the glass. Interpolation between nonfactored load charts in ASTM E 1300 shall be permitted.

(Mod S5027 / AS) (Mod S5584-R1 / AM)

2404.3.4 Sloped patterned glass. Patterned glass sloped more than 15 degrees (0.26 rad) from vertical in skylights, sunspaces, sloped roofs and other exterior applications shall be designed to resist the most critical of the combinations of loads from Section 2404.2.

For Equations 24-2 and 24-3:

Fg < 1.0 Fge 								(Equation 24-10)

For Equation 24-4:

Fg < 0.6Fge 								(Equation 24-11)

where

Fg = Total load on the glass, as determined by equations 24-2, 24-3 or 24-4.

Fge = Nonfactored load from ASTM E 1300. The value for patterned glass shall be based on the thinnest part of the glass. Interpolation between the nonfactored load charts in ASTM E 1300 shall be permitted. (Mod S5584-R1 / AM)

2404.3.5 Vertical sandblasted glass. Sandblasted glass sloped 15 degrees (0.26 rad) or less from vertical in windows, curtain and window walls, doors, and other exterior applications shall be designed to resist the wind loads in Section 1609 (HVHZ shall comply with Section 1620)  for components and cladding according to the following equation:

Fg0.6Fgw < 0.5 Fge 							(Equation 24-12)

where:

FgFgw = Total Wind load on the glass due to ultimate design wind speed Vult computed per Section 1609.

Fge = Nonfactored load from ASTM E 1300. The value for sandblasted glass is for moderate levels of sandblasting.

(Mod S5028 / AS)

(Mod S5584-R1 / AM)

Section 2404 – Wind, Snow, Seismic and Dead Loads on Glass

Change Section 2404.5. to read as shown:

2405.5 Unit skylights and tubular daylighting devices. Unit skylights and tubular devices shall be tested and labeled as complying with AAMA/WDMA/CSA 101/I.S./A440. The label shall state the name of the manufacturer, the approved labeling agency, the product designation and the performance grade rating as specified in AAMA/WDMA/CSA 101/I.S.2/A440. If the product manufacturer has chosen to have the performance grade of the skylight rated separately for positive and negative design pressure, then the label shall state both performance grade ratings as specified in AAMA/ WDMA/CSA 101/I.S.2/A440 and the skylight shall comply with Section 2405.5.2. If the skylight is not rated separately for positive and negative pressure, then the performance grade rating shown on the label shall be the performance grade rating determined in accordance with AAMA/WDMA/ CSA 101/I.S.2/A440 for both positive and negative design pressure and the skylight shall conform to Section 2405.5.1.  (Mod S5636-R1 / AM)

2405.5.1 Unit Skylights rated for the same performance grade for both positive and negative design pressure. The design of unit skylights shall be based on the following equation:

Fg ≤ PG 								(Equation 24-13)

where:

Fg= Maximum load on the skylight determined from Equations 24-2 through 24-4 in Section 2404.2.

F = Maximum load on the skylight determined

PG= Performance grade rating of the skylight.	 (Mod S5636-R1 / AM)

2405.5.2 Unit Skylights rated for separate performance grades for positive and negative design pressure. The design of unit skylights rated for performance grade for both positive and negative design pressures shall be based on the following equations:

Fgi  ≤  PGPo 								(Equation 24-14)

Fgo ≤ PGNe								 (Equation 24-15)

where:

PGPos = Performance grade rating of the skylight under positive design pressure;

PGNeg = Performance grade rating of the skylight under negative design pressure; and

Fgi and Fgo are determined in accordance with the following:

For 0.6 Wo ≥ D,

where:

Wo = Outward wind force, psf (kN/m2) due to ultimate design wind speed Vult, as calculated in Section 1609.

D = The dead weight of the glazing, psf (kN/m2) as determined in Section 2404.2 for glass, or by the weight of the plastic, psf (kN/m2) for plastic glazing.

Fgi = Maximum load on the skylight determined from Equations 24-3 and 24-4 in Section 2404.2.

Fgo = Maximum load on the skylight determined from Equation 24-2.

For 0.6Wo < D,

where:

Wo= Is the outward wind force, psf (kN/m2 ) due to ultimate design wind speed Vult  as calculated in Section 1609.

D= The dead weight of the glazing, psf (kN/m2) as determined in Section 2404.2 for glass, or by the weight of the plastic for plastic glazing.

Fgi= Maximum load on the skylight determined from Equations 24-2 through 24-4 in Section 2404.2.

Fgo = 0.

(Mod S5584-R1 / AM)

(Mod S5636-R1 / AM )

Section 2407 – Wind, Snow, Seismic and Dead Loads on Glass

Change Section 2407.1.4.2 to read as shown:

2407.1.4.2 Glass supporting top rail. When the top rail is supported by glass, the assembly shall be tested according to the impact requirements of Section 1609.1.2 (HVHZ shall comply with Section 1618.4.6.4). The top rail shall remain in place after impact.

(Mod S5029 / AS)

Chapter 25 – Gypsum Board and Plaster

Section 2508 – Gypsum Construction

Change Table 2508.5 to read as shown:

TABLE 2508.5

ALLOWABLE SHEAR CAPACITY FOR HORIZONTAL WOOD FRAMED GYPSUM BOARD DIAPHRAGM CEILING ASSEMBLIES

Table 2508.5 Contents (No Change)

(Mod S5648 / AS)

Chapter 26 - Plastic

Section 2601 – General

Change Section 2601.1 to read as shown:

2601.1 Scope. These provisions shall govern the materials, design, application, construction and installation of foam plastic, foam plastic insulation, plastic veneer, interior plastic finish and trim and light-transmitting plastics. See Chapter 14 for requirements for exterior wall finish and trim.

Exception: Buildings and structures located within the high-velocity hurricane zone shall 	also comply with the provisions of Section 2614.

(Mod F4961 / AS)

Florida Specific Amendment / Code Modification

Section 2603 – Foam Plastic Insulation

Change Section 2603.9 to read as shown:

2603.9 Protection against termites. In Florida areas where the probability of termite infestation is very heavy in accordance with Figure 2603.9, extruded and expanded polystyrene, polyisocyanurate and other foam plastics shall not be installed on the exterior face or under interior or exterior foundation walls or slab foundations located below grade. The clearance between foam plastics installed above grade and exposed earth shall be at least 6 inches (152 mm).

Exceptions:

1. Buildings where the structural members of walls, floors, ceilings and roofs are entirely of noncombustible materials or preservative-treated wood.

2. An approved method of protecting the foam plastic and structure from subterranean termite damage is provided.

3. On the interior side of basement walls.

Section 2603 – Foam Plastic Insulation

Change Figure 2603.9 to read as shown:

FIGURE 2603.9

TERMITE INFESTATION PROBABILITY MAP

Reserved.

(Mod S5221 / AS)

Chapter 27 – Electrical Systems

(No Change)

Chapter 28 – Mechanical Systems

(No Change)

Chapter 29 – Plumbing Systems

(No Change)

Chapter 30 -  Elevators and Conveying Systems

Florida Specific Amendment

Section 3001 – Elevators and Conveying Systems

Change Sections 3001 to read as shown:

3001.1 Scope. This chapter governs the design, construction, installation, alteration, and repair and maintenance of elevators and conveying systems and their components.

Note: Other administrative and programmatic provisions may apply. See the Department of Business and Professional Regulation [DBPR] Chapter 399, Florida Statutes, and 61C-5, Florida Administrative Code. The regulation and enforcement of the following sections of the adopted codes, and their addenda, are preempted to the Bureau of Elevator Safety of the Department of Business and Professional regulation: ASME A17.1, Part 8, ASME A17.3, Sections 1.2, 1.5, ASME A18.1, Part 10.

3001.2 Referenced standards. Except as otherwise provided for in this code, the design, construction, installation, alteration, repair and maintenance of elevators and conveying systems and their components shall conform to ASME A17.1/CSA B44, ASME A17.3 and ASME A18.1, ASME A90.1, ASME B20.1, ALI ALCTV, and ASCE 24 for construction in flood hazard areas established in Section 1612.3. The Division of Hotels and Restaurants may grant exceptions, variances and waivers to the Elevator Safety Code as authorized by the Elevator Safety Code Safety Code for Elevators and Escalators (ASME A17.1, Section 1.2) and Florida Statutes (Chapter 120.)

3001.3 Accessibility. Passenger elevators are required to be accessible or to serve as part of an accessible means of egress shall comply with Sections 1107 and 1109.7. by the Florida Building Code, Accessibility Chapter 11.

- 3001.4 Change in use. A change in use of an elevator from freight to passenger, passenger to freight, or from one freight class to another freight class shall comply with Section 8.7 of ASME A17.1/CSA B44.

3001.5 Design, installation and alteration of elevators.

3001.5.1   Each new elevator shall comply with the Florida Elevator Safety Code that was in effect at the time of receipt of application for the construction permit for the elevator.

3001.5.2   Each alteration to, or relocation of, an elevator shall comply with the Florida Elevator Safety Code that was in effect at the time of receipt of the application for the construction permit for the alteration or relocation.

3001.5.3   All existing elevators shall comply with ASME A17.3

- 3001.6  As used in this chapter, the term:

ALTERATION.  Any change to equipment, including its parts, components, and/or subsystems, other than maintenance, repair, or replacement.

- CERTIFICATE OF OPERATION means a document issued by the department which indicates that the conveyance has had the required safety inspection and tests and that fees have been paid as provided in this Chapter 399, FS.

- CONVEYANCE. An elevator, dumbwaiter, escalator, moving sidewalk, platform lift and stairway chairlift.

- DEPARTMENT. For the purpose of this section, means the Department of Business and Professional Regulation.

DIVISION. For the purpose of this section, means the Division of Hotels and Restaurants of the Department of Business and Professional Regulation.

- ELEVATOR. One of the following mechanical devices:

- (a) A hoisting and lowering mechanism, equipped with a car and platform that moves in guide rails and serves two or more landings to transport material or passengers or both.

- (b) An escalator, which is a power-driven, inclined continuous stairway used for raising or lowering passengers.

- (c) A dumbwaiter, which is a hoisting and lowering mechanism equipped with a car of limited size which moves in guide rails and serves two or more landings.

- (d) A moving walk, which is a type of passenger-carrying device on which passengers stand or walk and in which the passenger-carrying surface remains parallel to its direction of motion and is uninterrupted.

- (e) An inclined stairway chairlift, which is a device used to transport physically handicapped persons over architectural barriers.

(f) An inclined or vertical wheelchair lift, which is a device used to transport wheelchair handicapped persons over architectural barriers.

- Exceptions:

- Personnel hoists and material hoists within the scope of ASME A10.

- Man lifts within the scope of ASME A90.1.

- Mobile scaffolds, towers, and platforms within the scope of ANSI A92.

- Powered platforms and equipment for exterior and interior maintenance within the  scope of ASME A120.1.

- Conveyors and related equipment within the scope of ASME B20.1.

- Cranes, derricks, hoists, hooks, jacks and slings within the scope of ASME B30.

- Industrial trucks within the scope of ASME B56.

- Portable equipment, except for portable escalators that are covered by this code.

- Tiered or piling machines used to move materials to and from storage located and operating entirely within one story.

- Equipment for feeding or positioning materials at machine tools and printing presses.

- Skip or furnace hoists.

- Wharf ramps.

- Railroad car lifts or dumpers.

- Line jacks, false cars, shafters, moving platforms and similar equipment used for installing an elevator by a contractor licensed in this state.

- Automated people movers at airports.

- Elevators in television and radio towers.

- Hand-operated dumbwaiters.

- Sewage pump station lifts.

- Automobile parking lifts.

- Equipment covered in Section 1.1.2 of the Elevator Safety Code ASME A17.1 Safety Code for Elevators and Escalators.

- Elevators, inclined stairway chairlifts, and inclined or vertical wheelchair lifts located in private residences.

- ESCALATOR. An installation defined as an escalator in the Florida Building Code.

- EXISTING INSTALLATION. An installation defined as an “installation, existing” in the Florida Building Code.

PRIVATE RESIDENCE. A separate dwelling or a separate apartment in a multiple dwelling which is occupied by members of a single family.

Florida Specific Amendment

Section 3002 – Elevators and Conveying Systems

Change Sections 3002 to read as shown:

3002.4 Elevator car to accommodate an ambulance stretcher.  Where elevators are provided in buildings four or more stories above, or four or more stories below, grade plane, at least one elevator shall be provided for Any building that is more than three stories high or in which the vertical distance between the bottom terminal landing and the top terminal landing exceeds 25 feet, must be constructed to contain at least one passenger elevator that is operational for building occupants and fire department emergency access to all floors.  The elevator car shall be of such a size and arrangement to accommodate an ambulance stretcher 24-inches by 76-inches (610 mm by 1950 mm) with not less than 5-inch radius corners in the horizontal, open position and shall be identified by the international symbol for emergency medical services (star of life). The symbol shall not be less than 3 inches (76 mm) high and shall be placed inside on both sides of the hoistway door frame.

3002.9 Automatic fire alarm initiating devices shall be located and installed in accordance with ASME A 17.1 and NFPA 72.

Section 3003 – Emergency Operations

Change Section 3003.3 to read as shown:

3003.3 Seven fire service elevator keys. All elevators that operate in a building that is six or more stories in height shall be equipped to operate with a one of seven emergency response region elevator keys standardized fire service elevator key in accordance with the International Fire Code. Florida Fire Prevention Code.

(Mod SP5463 / AS)

Florida Specific Amendment

Section 3004 – Hoistway Venting

Change Section 3004.3.1 to read as shown:

3004.3.1 Reduced vent area. Where mechanical ventilation conforming to the International Florida Building Code, Mechanical Code is provided, a reduction in the required vent area is allowed provided that all of the following conditions are met:

1. The occupancy is not in Group R-1, R-2, I-1 or I-2 or of a similar occupancy with overnight sleeping units.

2. The vents required by Section 3004.2 do not have outside exposure.

3. The hoistway does not extend to the top of the building.

4. The hoistway and machine room exhaust fan is automatically reactivated by thermostatic means.

5. Equivalent venting of the hoistway is accomplished.

Florida Specific Amendment

Section 3005 – Conveying Systems

Change Section 3005.4 to read as shown:

3005.4 Personnel and material hoists. Personnel and material hoists shall be designed utilizing an approved method that accounts for the conditions imposed during the intended operation of the hoist device. The design shall include, but is not limited to, anticipated loads, structural stability, impact, vibration, stresses and seismic restraint. The design shall account for the construction, installation, operation and inspection of the hoist tower, car, machinery and control equipment, guide members and hoisting mechanism. Additionally, the design of personnel hoists shall include provisions for field testing and maintenance which will demonstrate that the hoist device functions in accordance with the design. Field tests shall be conducted upon the completion of an installation or following a major alteration of a personnel hoist.

Section 3007 – Fire Service Access Elevator

Change Section 3007.6 to read as shown:

3007.6 Hoistway enclosures. The fire service access elevator hoistway shall be located in a shaft enclosure complying with  Section 708. Section 713.

(Mod SP5245 / AS)

Section 3007 – Fire Service Access Elevator

Change Section 3007.7 to read as shown:

3007.7 Fire service access elevator lobby. The fire service access elevator shall open into a fire service access elevator lobby in accordance with Sections 3007.7.1 through 3007.7.5.

Exception: Where a fire service access elevator has two entrances onto a floor, the second entrance shall be permitted to open into an elevator lobby in accordance with Section 708.14.1. Section 713.14.1.

(Mod SP5242 / AS)

Section 3008 – Occupant Evacuation Elevators

Change Section 3008.1.2 to read as shown:

3008.1.2 Fire safety and evacuation plan. The building shall have an approved fire safety and evacuation plan in accordance with the applicable requirements of Section 404 of the International Florida Fire Prevention Code. The fire safety and evacuation plan shall incorporate specific procedures for the occupants using evacuation elevators.

(Mod SP5251 / AS)

Florida Specific Amendment

Section 3008 – Occupant Evacuation Elevators

3008.2 Fire safety and evacuation plan. The building shall have an approved fire safety and evacuation plan in accordance with the applicable requirements of Section 404 of the International Florida Fire Prevention Code. The fire safety and evacuation plan shall incorporate specific procedures for the occupants using evacuation elevators.

(Mod SP5251 / AS)

Florida Specific Amendment

Section 3009 – Elevator Accessibility Requirements for the Physically Handicapped

Add Section 3009 to read as shown:

SECTION 3009

ELEVATOR ACCESSIBILITY REQUIREMENTS FOR THE PHYSICALLY HANDICAPPED

3009.1 In a building having any elevators that do not provide access to every floor level, elevator hallway call buttons on all main levels of ingress and on any floor that is commonly served by more than one group of elevators must be marked with Arabic and braille symbols that indicate floor levels to which access is provided. The symbols must be placed directly above each call button.

3009.2 Each elevator car interior must have a support rail on at least one wall. All support rails must be smooth and have no sharp edges and must not be more than 1½ inches (38 mm) thick or 2½ inches (63 mm) in diameter. Support rails must be continuous and a minimum length of 42 inches (1067 mm) overall.

The inside surface of support rails must be 1½ inches (38 mm) clear of the car wall. The distance from the top of the support rail to the finished car floor must be at least 31 inches (787 mm) and not more than 33 inches (838 mm). Padded or tufted material or decorative materials such as wallpaper, vinyl, cloth or the like may be not be used on support rails.

3009.3 A bench or seat may be installed on the rear wall of the elevator car enclosure, if the bench or seat does not protrude beyond the vertical plane of the elevator car enclosure wall when folded into a recess provided for the bench or seat and, when not in use, the bench or seat automatically folds into the recess. The bench or seat must be capable of supporting a live load of at least 250 pounds (113.4 kg) on any 12-inch by 12-inch (305 mm by 305 mm) area. A padded, tufted or other decorative material may not be used to cover the bench or seat; or may the bench or seat encroach on the minimum clear inside-car dimensions specified in this section.

This section applies only to elevators available for the transportation of the public. This section does not apply to elevators restricted by key or similar device to a limited number of persons in a building that has an elevator that otherwise meets the requirements of this section or to elevators used only for the transportation of freight. However, elevators that are used as freight and passenger elevators for the public and employees must comply with this section. This section does not apply to dumbwaiters or escalators.

This section supersedes all other state regulations and local ordinances and rules affecting the accessibility of passenger elevators to the physically handicapped, and the standards established by this section may not be modified by municipal or county ordinance.

Florida Specific Amendment

Section 3010 – Serial Numbers

Add Section 3010 to read as shown:

3010.1 Serial numbers. Each elevator shall have a serial number assigned by the division or authority having jurisdiction  painted on or  attached to the elevator car in plain view and also to the driving mechanism. This serial number shall be shown on all required certificates and permits.

3010.1.1. Certificates of operation must be posted in a conspicuous location in the elevator and shall contain the text of Section 823.12, Florida Statutes relating to the prohibition against smoking in elevators. The certificate must be framed with a transparent cover.

3010.1.2. The designation “NO SMOKING” along with the international symbol for no smoking shall be conspicuously displayed within the interior of the elevator in the plain view of the public.

3010.1.3. The following ASME A17.1, rule is hereby amended to read as follows:

a. Rule 2.29.1 amend to add the following to the rule: "Each car in a multicar group shall be sequentially identified from left to right, as viewed from the elevator lobby."

b. Rule 2.7.3.1 of the ASME A17.1, which is amended to read as follows: “Rule 2.7.3.1 General Requirements. A permanent, safe and convenient means of access to elevator machine rooms and overhead machinery spaces shall be provided for authorized persons. The key to the machine rooms and overhead machinery spaces shall be kept on the premises at all times and readily available for use by State of Florida certified Elevator Inspectors.”

c. Rule 3.11.3 of ASME A17.3 is amended to read as follows:

NOTE: Updates to the Safety Code for Existing Elevators and Escalators ASME A17.1 and ASME A17.3 which require Phase II Firefighters’ Service shall apply except where section 399.02(9) Florida Statute states Phase II Firefighters' Service on elevators may not be enforced until July 1, 2015, or until the elevator is replaced or requires major modification, whichever occurs first, on elevators in condominiums or multifamily residential buildings, including those that are part of a continuing care facility licensed under chapter 651, or similar retirement community with apartments, having a certificate of occupancy by the local building authority that was issued before July 1, 2008. This exception does not prevent an elevator owner from requesting a variance from the applicable codes before or after July 1, 2015. This subsection does not prohibit the division from granting variances pursuant to s. 120.542, Florida Statute.

Florida Specific Amendment

Section 3011 – Electrolysis Protection for Underground Hydraulic Elevator Cylinders

Add Section 3011 to read as shown:

SECTION 3011

ELECTROLYSIS PROTECTION FOR UNDERGROUND HYDRAULIC ELEVATOR CYLINDERS

3011.1 Electrolysis protection for underground hydraulic elevator cylinders.  All newly installed underground hydraulic pressure cylinders shall be encased in outer plastic containment to minimize electrolytic corrosion between the metal cylinder and ground cathode.

3011.1.1 The plastic casing shall be capped at the bottom, and all joints must be solvent or heat welded to ensure water tightness.

3011.1.2 The plastic casing shall be constructed of polyethylene or polyvinyl chloride (PVC). The plastic pipe wall thickness must not be less than 0.125 inch (3.175 mm).

3011.1.3  The neck of the plastic casing shall have a means of inspection provided to monitor the annulus between the pressurized hydraulic cylinder and the protective plastic casing.

3011.1.4 Replacements of existing hydraulic cylinders shall be protected by the aforementioned method where existing physical dimensions permit.

Florida Specific Amendment

Section 3013 – Alterations to Electric and Hydraulic Elevators and Escalators

Add Section 3013 to read as shown:

SECTION 3012

ALTERATIONS TO ELECTRIC AND HYDRAULIC ELEVATORS AND ESCALATORS

3012.1 Alterations to electric and hydraulic elevators and escalators. Alterations set forth in Part 8, ASME A17.1 to include any change to equipment, including its parts, components, and/or subsystems, other than maintenance, repair, or replacement; require an elevator construction permit, along with documented performance of inspections and tests to determine conformance with ASME A17.1.  A repair or replacement of equipment, parts, components or subsystems that requires inspection, tests and independent witnessing in other sections of ASME A17.1,  A17.3  and A18.1 shall require an elevator construction permit.

Chapter 31 – Special Construction

Section 3105 – Awnings and Canopies

Change Section 3105 to read as shown:

SECTION 3105

AWNINGS AND CANOPIES

3105.1 General. Awnings or canopies shall comply with the requirements of Sections 3105.2 through 3105. 4  6 and other applicable sections of this code.

3105.2 Definition. The following terms is are defined in Chapter 2:

AWNING

RETRACTABLE AWNING.

3105.3 Design and construction. Awnings and canopies shall be designed and constructed to withstand wind or other lateral loads and live loads as required by Chapter 16 and in accordance with Section 3105.4 of this code with due allowance for shape, open construction and similar features that relieve the pressures or loads. Structural members shall be protected to prevent deterioration. Awnings shall have frames of noncombustible material, fire-retardant treated wood, wood of Type IV size, or 1-hour construction with combustible or noncombustible covers and shall be fixed, retractable, folding or collapsible.

3105.3.1 Location.

3105.3.1.1 Fabric awnings and fabric-covered frames located over public property or in areas accessible to the general public shall be constructed so that no rigid part of such fabric awnings or fabric-covered frames shall be less than 7 feet 6 inches (2286 mm) from the grade directly below, and no part of the cloth drop shall be less than 7 feet (2134 mm).

3105.3.1.2 A fixed fabric awning or fabric-covered frame shall not extend over public property more than two-thirds the distance from the property line to the nearest curb line in front of the building site as measured from the exterior face of the building, nor shall any portion be closer than 18 inches (457 mm) to the curb line.

Exceptions:

1.       If installed over 14 feet (4267 mm) in height, it may occupy the entire width of the sidewalk.

2.       Unless otherwise regulated by local zoning requirements.

3105.3.1.3 Fabric-covered framework in whole or in part of fabric, erected in connection with gasoline service stations may not be erected within 15 feet (4572 mm) of where flammable liquids are transferred.

3105.3.1.4 Movable fabric awnings or fabric covered frames may extend over public property for a distance of not more than 5 feet (1524 mm), provided such awnings or any part thereof maintain a clear height of 8 feet (2438 mm) above the sidewalk. All such movable awnings shall be supported on metal frames attached to the building.

3105.3.1.5 Every fabric awning or fabric-covered frame shall be located as not to interfere with the operation of any exterior standpipe, stairway, fire escape or any means of egress to and from the building.

3105.3.2 Area. No fabric awning or fabric-covered frame shall exceed the area of the building to which it is attached.

3105.3.4 3Material.

3105.3.4 3.1 Fabric used for awnings or fabric-covered frames shall meet the flame propagation performance criteria of NFPA 701 or have a flame spread index not greater than 25 when tested in accordance with ASTM E 84 or UL 723.

Exception: Awnings or fabric-covered frames used in conjunction with Group R-3 occupancies.

3105.3.4 3.2 Supports for fabric awnings and fabric-covered frame shall be of metal or similar durable material.

3105.4 Design.

3105.4.1 Design of the framing members shall not be based on removal or repositioning of parts, or the whole, during periods of 75 mph wind velocity.

3105.4.2 Design of the structural framing members shall be based on rational analysis, using the applicable wind loads of Chapter 16 as shown below:

3105.4.2.1 The wind design loads for any fabric or membrane-covered structure designed with a quick removal or breakaway membrane or fabric at wind velocities of 75 mph, shall be based on the following criteria:

1.       Minimum wind speed 105 mph

2.       Exposure Category B, C or D as defined in Chapter 16.

3105.4.2.2 The wind design loads for any fabric or membrane covered structure designed with a permanent or nonremovable fabric or membrane, shall be based on the following criteria:

1.       Minimum wind speed velocity as required in Chapter 16 using Figure 1609C.

2.       Exposure B, C or D as defined in Chapter 16.

3105.4.3 The fabric portions of awnings fabric covered frames shall be securely laced, tied or otherwise fastened to the frame; no rafter or front bar will be permitted in pockets; and in no case shall a rolling curtain be caused to operate over a canopy frame.

3105.4.4 The horizontal projection of cantilevered portions shall not be greater than two times the height, except where the building construction does not permit a proper installation; in which case, variance may be permitted by the building official, based on special design and construction.

3105.5 Rigid awnings and canopy shutters.

3105.5.1 Loads. Rigid awnings and canopy shutters shall be designed to resist the loads set forth in Chapter 16 of this Code except that structures or parts thereof which are intended to be removed or repositioned during periods of high wind velocity shall be designed in their open or extended position to design pressures based on a basic wind speed of minimum 115 mph, 3-second wind gust with applicable shape factors and to resist not less than 10 psf (478 Pa) roof live load.

3105.5.2 Where such structure is intended to be folded or otherwise repositioned to close an opening when the building is unattended or act as a storm shutter, the design in the closed position shall also comply with Chapter 16 and shall be impact resistant in accordance with Section 1609.1.4.

3105.5.3 Structures designed to be readily removed or repositioned during periods of high wind velocity shall be posted with a legible and readily visible decal or painted instructions to the owner or tenant to remove or reposition the structure or part thereof during such periods of time as are designated by the U.S. Weather Bureau as being a hurricane warning or alert.

3105.4 6 Canopy materials. Canopies shall be constructed of a rigid framework with an approved covering that meets the fire propagation performance criteria of NFPA 701 or has a flame spread index not greater than 25 when tested in accordance with ASTM E 84 or UL 723.

(Mod S5932 / AS)

Florida Specific Amendment / Proposed Modification

Section 3109 – Structures Seaward of a Coastal Construction Control Line

Add Section 3109 to read as shown:

SECTION 3109

STRUCTURES SEAWARD OF A COASTAL CONSTRUCTION CONTROL LINE

3109.1 General.

Swimming pools shall comply with the requirements of this section and other applicable 	sections of this code.

3109.1.1 Scope. The provisions of Section 3109 shall ensure that structures located seaward of the coastal construction control line are designed to resist the predicted forces associated with a 100-year storm event and shall apply to the following:

1.   All habitable structures which extend wholly or partially seaward of a coastal construction control line (CCCL) or 50-foot (15.3 m) setback line.

2.   Substantial improvement of or additions to existing habitable structures.

3.        Swimming pools that are located in close proximity to a habitable structure or armoring. An environmental permit from the Florida Department of Environmental Protection, requiring special siting considerations to protect the beach-dune system, proposed or existing structures and public beach access, is required prior to the start of construction. The environmental permit may condition the nature, timing and sequence of construction of permitted activities to provide protection to nesting sea turtles and hatchlings and their habitat, including review, submittal and approval of lighting plans.

Exception: The standards for buildings seaward of a CCCL area do not apply to any modification, maintenance or repair of any existing structure within the limits of the existing foundation which does not require, involve or include any additions to, or repair or modification of, the existing foundation of that structure.

(Mod S5676 / AS)

3109.1.2 Certification.  As part of the permit process and upon placement of the lowest horizontal structural member, the applicant shall submit to the building official certification of the elevation of the lowest horizontal structural member of the lowest floor as built in relation to National Geodetic Vertical Datum (N.G.V.D.). Said certification shall be prepared by or under the direct supervision of a registered land surveyor or professional engineer or architect and certified by same and be submitted prior to commencing any addition work. Any work undertaken prior to submission of the certification shall be at the applicant’s risk. The building official shall review the submitted elevation data, and any deficiencies found shall be corrected by the permit holder immediately and prior to any further work being permitted to proceed.

3109.2 Definitions.

ARMORING. A manmade structure designed to either prevent erosion of the upland property or protect upland structures from the effects of coastal wave and current action. Armoring includes certain rigid coastal structures such as geotextile bags or tubes, seawalls, revetments, bulkheads, retaining wall or similar structures, but does not include jetties, groins or other construction whose purpose is to add sand to the beach and dune system, alter the natural coastal currents or stabilize the mouths of inlets.

BREAKAWAY WALL. A partition independent of supporting structural members that is intended to withstand design wind forces but to collapse from a water load less than that which would occur during a 100 year storm event without causing collapse, displacement or other structural damage to the elevated portion of the building or supporting foundation system.

COASTAL CONSTRUCTION CONTROL LINE. The line established by the State of Florida pursuant to Section161.053, Florida Statutes, and recorded in the official records of the county which defines that portion of the beach-dune system subject to severe fluctuations based on a 100-year storm surge, storm waves or other predictable weather conditions.

DESIGN GRADE. The predicted eroded grade caused by the 100-year storm.

FIFTY-FOOT SETBACK LINE. A line of jurisdiction, established pursuant to the provisions of Section161.052, Florida Statutes, in which construction is prohibited within 50 feet  (15.13 m) of the line of mean high water at any riparian coastal location fronting the Gulf of Mexico or the Atlantic coast shoreline.

HABITABLE STRUCTURE. Structures designed primarily for human occupancy and are potential locations for shelter from storms. Typically included within this category are residences, hotels and restaurants.

LOWEST HORIZONTAL STRUCTURE MEMBER. Any shore-parallel structural member which supports floor, wall or column loads and transmits them to the pile foundation.

ONE-HUNDRED-YEAR STORM ELEVATION. The height of the breaking wave crest or wave approach as superimposed on the storm surge with dynamic wave set-up of a 100-year storm. This 100-year storm elevation is determined by the Florida Department of Environmental Protection based on studies published as part of the coastal construction control line establishment process and an analysis of topographic and other site specific data.

REBUILDING. See definition of “Substantial improvement.”

SUBSTANTIAL IMPROVEMENT. See Section 1612.

3109.3 Elevation standards.  All habitable structures shall be elevated at or above an elevation which places the lowest horizontal structural member above the 100-year storm elevation as determined by the Florida Department of Environmental Protection in the report titled “One-Hundred-Year Storm Elevation Requirements for Habitable Structures Located Seaward of a Coastal Construction Control Line.”

An applicant may request the Department of Environmental Protection to determine a site-specific 100-year storm elevation for the applicant’s proposed habitable structure as part of the environmental permit application process. The elevation will be provided as part of the applicant’s environmental permit and shall be subject to review under the provisions of Chapter 120, Florida Statutes.

Exceptions:

1.	Additions, repairs or modifications to existing nonconforming habitable structures that do not advance the seaward limits of the existing habitable structure and do not constitute rebuilding of the existing structure.

2.	Habitable structures located landward of existing armoring which is capable of protecting buildings from the effects of erosion from a 100-year storm surge. The applicant shall provide scientific and engineering evidence that the armoring has been designed, constructed and maintained to survive the effects of the design storm and provide protection to existing and proposed structures from the erosion associated with that event. Evidence shall include a report with data and supporting analysis, and shall be certified by a professional engineer registered in this state, that the armoring was designed and constructed and is in adequate condition to meet the following criteria:

a.	The top must be at or above the still water level, including setup, for the design storm plus the breaking wave calculated at its highest achievable level based on the maximum eroded beach profile and highest surge level combination, and must be high enough to preclude runup overtopping.

b.	The armoring must be stable under the design storm including maximum localized scour, with adequate penetration and toe protection to avoid settlement, toe failure, or loss of material from beneath or behind the armoring.

c.	The armoring must have sufficient continuity or return walls to prevent flanking under the design storm from impacting the proposed construction.

d.	The armoring must withstand the static and hydrodynamic forces of the design storm.

3.	A higher elevation standard is required by either the National Flood Insurance Program (NFIP), as found on a community’s Flood Insurance Rate Map (FIRM), or the local flood damage prevention ordinance. In such instances, the higher elevation standard shall apply.

3109.4 Construction standards.

3109.4.1 Pile foundations.  All habitable structures shall be elevated on, and securely anchored to, an adequate pile foundation. Pile foundations for habitable structures shall be designed to withstand all reasonable anticipated erosion, scour and loads resulting from a 100-year storm including wind, wave, hydrostatic and hydrodynamic forces acting simultaneously with typical structural (live and dead) loads. All habitable structures should be anchored to their pile foundation in such a manner as to prevent flotation, collapse or lateral displacement. The elevation of the soil surface to be used in the calculation of pile reactions and bearing capacities for habitable structures shall not be greater than that which would result from erosion caused by a 100-year storm event. Calculation of the design grade shall account for localized scour resulting from the presence of structural components. Design ratio or pile spacing to pile diameter should not be less than 8:1 for individual piles located above the design grade. Pile caps shall be set below the design grade unless designed to resist increased flood loads associated with setting the cap above the design grade, but at or below the natural grade. Pile penetration shall take into consideration the anticipated loss of soil above the design grade.

Exceptions:

1.	Additions, repairs or modifications to existing nonconforming habitable structures that do not advance the seaward limits of the existing habitable structure and do not constitute rebuilding of the existing structure.

2.	Habitable structures located landward of existing armoring which is capable of protecting buildings from the effects of erosion from a 100-year storm surge. The applicant shall provide scientific and engineering evidence that the armoring has been designed, constructed and maintained to survive the effects of the design storm and provide protection to existing and proposed structures from the erosion associated with that event. Evidence shall include a report with data and supporting analysis, and shall be certified by a professional engineer registered in this state, that the armoring was designed and constructed and is in adequate condition to meet the following criteria:

a.	The top must be at or above the still water level, including setup, for the design storm plus the breaking wave calculated at its highest achievable level based on the maximum eroded beach profile and highest surge level combination, and must be high enough to preclude runup overtopping.

b.	The armoring must be stable under the design storm Including maximum localized scour, with adequate penetration and toe protection to avoid settlement, toe failure or loss of material from beneath or behind the armoring.

c.	The armoring must have sufficient continuity or return walls to prevent flanking under the design storm from impacting the proposed construction.

d.	The armoring must withstand the static and hydrodynamic forces of the design storm.

3109.4.2 Walls below the 100-year storm elevation.  No substantial walls or partitions shall be constructed below the level of the first finished floor of habitable structures. All other walls shall be designed to break away.

Exceptions:

1.	Stairways and stairwells;

2.	Shear walls perpendicular to the shoreline;

3.	Shear walls parallel to the shoreline, which are limited to a maximum of 20 percent of the building length in the direction running parallel to the shore;

4.	Shear walls parallel to the shoreline, which exceed 20 percent of the total building length (including any attached major structure) when they meet the following criteria:

a.	A certification is provided by a Florida-registered professional engineer that certifies that the increased length of shear walls, over 20 percent, are located landward of the 100-year erosion limit;

b.	A hydraulic analysis is provided and certified by a Florida-registered professional engineer that evaluates the potential impact of flow increase on the subject parcel and adjacent properties;

c.	The hydraulic analysis demonstrates that although the overall shearwall coverage is more than 20 percent, the increased shearwall length will not result in substantial increase of flow velocities and drag forces on the structural components of the proposed structure and neighboring structures; and

d.	The provisions under Section 3109.4.2 (Exception 4) do not include any low-rise building as defined in Section 1609.2.

5.	Wind or sand screens constructed of fiber or wire mesh;

6.	Light, open lattice partitions with individual, wooden lattice strips not greater than 3/4 inch (19 mm) thick and 3 inches (76 mm) wide;

7.	Elevator shafts;

8.	Small mechanical and electrical rooms; and

9.	Break-away or frangible walls.

3109.5 Flood loads during a 100-year storm.

3109.5.1 Load basis.  The structural design shall be based on the 100-year storm as determined by the Florida Department of Environmental Protection in studies published as part of the coastal construction control line establishment process. Breaking, broken and nonbreaking waves shall be considered as applicable. Design wave loading analysis shall consider vertical uplift pressures and all lateral pressures to include impact, as well as dynamic loading and the harmonic intensification resulting from repetitive waves.

3109.5.2 Hydrostatic load.  Habitable structures shall be designed in consideration of the hydrostatic loads which would be expected under the conditions of maximum inundation associated with a 100-year storm event. Calculations for hydrostatic loads shall consider the maximum water pressure resulting from a fully peaked, breaking wave superimposed on the design storm surge with dynamic wave setup. Both free and confined hydrostatic loads shall be considered. Hydrostatic loads which are confined shall be determined using the maximum elevation to which the confined water would freely rise if unconfined. Vertical hydrostatic loads shall be considered as forces acting both vertically downward and upward on horizontal or inclined surfaces of major structures (e.g., floors, slabs, roofs, walls). Lateral hydrostatic loads shall be considered as forces acting horizontally above and below grade on vertical or inclined surfaces of major structures and coastal or shore protection structures. Hydrostatic loads on irregular or curving geometric surfaces may be determined in consideration of separate vertical and horizontal components acting simultaneously under the distribution of the hydrostatic pressures.

3109.5.3 Hydrodynamic loads.  Habitable structures shall be designed in consideration of the hydrodynamic loads which would be expected under the conditions of a 100-year storm event. Calculations for hydrodynamic loads shall consider the maximum water pressures resulting from the motion of the water mass associated with a 100-year storm event. Full-intensity loading shall be applied on all structural surfaces above the design grade which would affect the flow velocities.

3109.6 Wind loads.  All habitable structures shall be designed in accordance with Chapter 16.

3109.7 Swimming pools.  Swimming pools located in close proximity to an existing habitable structure or armoring shall be designed with an adequate pile foundation for the erosion and scour conditions of a 100-year storm event.

3109.8 Storm debris.  All structures will be designed to minimize the potential for wind and water-borne debris during a storm.

(Mod SP5676 / AS)

(Mod SP5259 / AS)

Section 3109 – Structures Seaward of a Coastal Construction Control Line

Change Section 3109.2 to read as shown:

SUBSTANTIAL IMPROVEMENT. See Section 1612.

(Mod SP5259 / AS)

Florida Specific Amendment

Section 3112 – Deposit of Material In Tidewater Regulated

Add Section 3112 to read as shown:

SECTION 3112

DEPOSIT OF MATERIAL IN TIDEWATER REGULATED

3112.1  It is not lawful for any person to discharge or cause to be discharged or deposit or cause to be deposited, in the tide or salt waters of any bay, port, harbor or river of this state, any ballast or material of any kind other than clear stone or rock, free from gravel or pebbles, which said clear stone or rock shall be deposited or discharged only in the construction of enclosures in connection with wharves, piers, quays, jetties or in the construction of permanent bulkheads connecting the solid and permanent portion of wharves. It is lawful to construct three characters of bulkheads for retention of material in solid wharves.

First, clear stone or rock enclosures, or bulkheads, may be built upon all sides to a height not less than 2½ feet (762 mm) above high watermark; and after the enclosures have been made so solid, tight and permanent as to prevent any sand, mud, gravel or other material that may be discharged or deposited in them from drifting or escaping through such enclosures, any kind of ballast may be discharged or deposited within the enclosures. The enclosures may be constructed of wood, stone and rock combined, the stone and rocks to be placed on the outside of the wood to a height not less at any point than 2½ feet (762 mm) above high watermark; and after the enclosures have been made so solid, tight and permanent as to prevent any sand, mud gravel or other material that may be discharged or deposited in them from drifting or escaping through such enclosures, any kind of ballast may be discharged or deposited within the enclosures.

Second, a bulkhead may be built by a permanent wharf consisting of thoroughly creosoted piles not less than 12 inches (305 mm) in diameter at the butt end, to be driven close together and to be capped with timber not less than 10 or 14 inches drift (254 or 302 mm), bolted to each pile, and one or more longitudinal stringers to be placed on the outside of the bulkhead and securely anchored by means of iron rods to piles driven within the bulkheads, clear rock to be on the inside of the bulkhead, to a height of not less than 2½ feet (762 mm) above high water; and after this is done, ballast or other material may be deposited within the permanent enclosure so constructed.

Third, a bulkhead may be constructed to consist of creosoted piles, as described herein, driven not exceeding 4 feet (1219 mm) apart from center to center, inside of which two or more longitudinal stringers may be placed and securely bolted to the piles. Inside of these longitudinal pieces, two thicknesses of creosoted sheet piling are to be driven, each course of the sheet piling to make a joint with the other to form an impenetrable wharf; and within this permanent bulkhead so constructed, any ballast or other material may be deposited.

No such enclosure, pier, quay or jetty shall be begun until the point whereat it is to be built shall have been connected by a substantial wharf with a shore or with a permanent wharf; except that the owners of wharves may at any time, with the consent of the Board of Pilot Commissioners of the Division of Professions of the Department of Business and Professional Regulation, build wharves of clear stone or rock, or creosoted walls as hereinafter provided, on each side of their wharves from the shore to a point at which the water is not more than 15 feet (4.6 m) deep, and when such walls have attained a height of 2½ feet (762 mm) above high watermark and have been securely closed at the deepwater end by stone or creosoted walls of the same height, any kind of ballast may be deposited in them.

Nothing contained in this section shall interfere with any rights or privileges now enjoyed by riparian owners. While this section empowers those who desire to construct the several characters of wharves, piers, quays, jetties and bulkheads provided for and described herein, nothing in this section shall be so construed as to require any person not desiring to construct a permanent wharf by filling up with ballast, stone or other material to construct under the specifications contained herein; and nothing in this chapter shall be so construed as to prevent any person from constructing any wharf or placing any pilings, logs or lumber in any waters where the person would have heretofore had the right so to do.

3112.2 This section shall not prohibit Escambia County from placing in Pensacola Bay, on the Escambia County side, beside the old Pensacola Bay Bridge, certain materials, as recommended by the Department of Environmental Protection, in coordination with the Fish and Wildlife Conservation Commission, to increase the number of fish available for persons fishing from the old Pensacola Bay Bridge.

3112.3 This section shall not prohibit Manatee County from placing in the Manatee County portions of Sarasota Bay and Tampa Bay and in the Manatee River, certain materials, as recommended by the Department of Environmental Protection, in coordination with the Fish and Wildlife Conservation Commission, to increase the number of fish available for persons fishing in the above areas.

3112.4 This section shall not prohibit Pinellas County from placing in Tampa Bay certain materials as recommended by the Department of Environmental Protection, in coordination with the Fish and Wildlife Conservation Commission, to increase the number of fish available for persons fishing in the bay. Deposit of material on a wharf or quay is regulated. It is not lawful for any person to deposit or cause to be deposited on any wharf or quay, any ballast, stone, earth or like material, except such wharf or quay may be so secured as to prevent such ballast or other material from washing into the waters of the harbor.

Florida Specific Amendment

Section 3113 – Lighting, Mirrors, Landscaping

Add Section 3113 to read as shown:

SECTION 3113

LIGHTING, MIRRORS, LANDSCAPING

3113.1 Each operator of an automated teller machine that controls the access area or defined parking area to be lighted shall comply with Sections (2), (3), and (4) no later than one year after October 1, 1994. If the access area or defined parking area to be lighted is controlled by a person other than the operator, such other person shall comply with Sections (2), (3), and (4) no later than one year after October 1, 1994.

3113.2 Each operator, or other person responsible for an automated teller machine pursuant to Sections 655.960 through 655.965, shall provide lighting during the hours of darkness with respect to an open and operating automated teller machine and any defined parking area, access area and the exterior of an enclosed automated teller machine installation, as follows:

1.There shall be a minimum of 10 footcandle (108 lux) power at the face of the automated teller machine and extending in an unobstructed direction outward 5 feet (1.5 m).

2.There shall be a minimum of 2 footcandle (21.5 lux) power within 50 feet (15.25 m) in all unobstructed directions from the face of the automated teller machine. If the automated teller machine is located within 10 feet (3 m) of the corner of the building and the automated teller machine is generally accessible from the adjacent side, there shall be a minimum of 2 footcandle (21.5 lux) power along the first 40 unobstructed feet (12 m) of the adjacent side of the building.

3.There shall be a minimum of 2 footcandle (12.5 lux) power in that portion of the defined parking area within 60 feet (18 m) of the automated teller machine.

4.The operator shall provide reflective mirrors or surfaces at each automated teller machine which provide the customer with a rear view while the customer is engaged in using the automated teller machine.

5.The operator, or other person responsible pursuant to Sections 655.960 through 655.965 for an automated teller machine, shall ensure that the height of any landscaping, vegetation or other physical obstructions in the area required to be lighted pursuant to Section (2) for any open and operating automated teller machine shall not exceed 3 feet (914 mm), except that trees trimmed to a height of 10 feet (3 m) and whose diameters are less than 2 feet (610 mm) and manmade physical obstructions required by statute, law, code, ordinance or other governmental regulation shall not be affected by this section.

Section 3114– Airport Noise

Add Section 3114 to read as shown:

SECTION 3114

AIRPORT NOISE

3114.1 Airport noise study guidelines

3114.1   The Aviation Safety and Noise Abatement Act of 1979 14 CFR Part 150 (US Department of Transportation) including revisions through January 2005 and hereby adopted as a guideline for establishing airport noise control. When required by a local government by local ordinance to provide noise attenuation in a new structure or addition to an existing structure near an airport in the area of the local government, the applicant must provide either:

1.  a testing certificate from an accredited noise testing lab that a new structure or addition to existing structure built to the submitted engineering plans will achieve an average minimum dBA reduction equal to or greater than the reduction required,

2.  an engineering judgment signed and sealed by an engineer licensed in the State of Florida that the structure or addition built to the submitted engineering plans will achieve an average minimum dBA reduction equal to or greater than the reduction required, or

3.  plans using the standards contained in "Guidelines for Sound Insulation of Residences Exposed to Aircraft Operations" prepared for the Department of the Navy by Wyle Research and Consulting, Arlington, Virginia, April 2005 on file with the Florida Building Commission.

(Mod S5226 / AS)

Chapter 32 – Encroachments into the Public Right-of-Way

(No Change)

Chapter 33 – Safeguards During Construction

(No Change)

Florida Specific Amendment

Chapter 34 – Existing Structures

Change Sections 3401 – 3412 to read as shown:

SECTION 3401

GENERAL

3401.1 Scope. The provisions of this chapter shall control the alteration, repair, addition and change of occupancy of existing buildings and structures. Alteration, repair, addition, relocation and change of occupancy of existing structures and buildings shall comply with the provisions of the Florida Building Code, Existing Building.

Exception: Existing bleachers, grandstands and folding and telescopic seating shall comply with ICC 300.

3401.2 – 3401.5 Reserved.

SECTION 3402

DEFINITIONS

RESERVED

SECTION 3403

ADDITIONS

RESERVED

SECTION 3404

ALTERATIONS

RESERVED

SECTION 3405

REPAIRS

RESERVED

SECTION 3406

FIRE ESCAPES

RESERVED

SECTION 3407

GLASS REPLACEMENT

RESERVED

SECTION 3408

CHANGE OF OCCUPANCY

RESERVED

SECTION 3409

HISTORIC BUILDINGS

RESERVED

SECTION 3410

MOVED STRUCTURES

RESERVED

SECTION 3411

ACCESSIBILITY FOR EXISTING BUILDINGS

RESERVED

SECTION 3412

COMPLIANCE ALTERNATIVES

RESERVED

Chapter 35 – Referenced Standards

Add Referenced Standard to Chapter 35 to read as shown:

AAF		Aluminum Association of Florida Inc.

3165 McCrory Place, Suite 185

Orlando, FL 32803

Standard reference number	Title		Referenced in code section number

AAF—10	Guide to Aluminum Construction in High Wind Areas 2010      1622.1, 2002.4.1

(Mod S5830 / AS)

Florida Specific Amendment

Chapter 35 – Referenced Standards

Add or change AAMA standards to read as shown:

AAMA	American Architectural Manufacturers Association

1827 Waldon Office Square, Suite 550

Schaumburg, IL 60173-4268

Standard reference number	Title				Referenced in code section number

AAMA/NPEA/NSA 2100-11  Voluntary Specifications for Sunrooms			202, 2002.6

(S5893 AS)

101/I.S.2-97	Voluntary Specifications for Aluminum, Vinyl (PVC) and Wood

Windows and Glass Doors			1008.1.7,  1710.5.1, 1710.5.3, 2411.3.2.1

101/I.S.2/NAFS-02  	Voluntary Specifications for Aluminum, Vinyl (PVC) and Wood   1008.1.7, 1710.5.1,

Windows and Glass Doors 			  1710.5.3, Table 1710.5.2, 2411.3.2.1

AAMA 2502-07	Comparative Analysis Procedure for Window and Door Products 	 1710.5.3 , 2411.3.2.6

AAMA 103 – 09	Procedural Guide for Certification of Window and Door Assemblies, Sec. 2 –

or 10 or 11	Engineering Design Rules						2411.3.2.6

AAMA 1402-86 or 09  Standard Specifications for Aluminum Siding, Soffit and Fascia	1404.5.1

AAMA 203- 98 or 03  Procedural Guide for the Window Inspection and Notification System	1710,5,3

AAMA 501-94 or 05  Methods of Test for Exterior Walls	1710.5.6.5, 2411.3.2.1, 2411.3.2.1.1, 2612.2

AAMA/WDMA/CSA101/  North American Fenestration Standard/Specifications for Windows,             1710.5.1,

I.S.2/A440-05 or 08 or 11  Doors and Skylights    	                        1710.6, 1710.5.3, 1710.5.6.1, 1720.5.6.4, 2405.5

AAMA 450-06 or 09 or 10	 Voluntary Performance Rating Method for Mulled Fenestration Assemblies     1710.5.6.1

AAMA 506-06 or 08 or 11	Voluntary Specifications and Test Methods for Sealants		2510.8

| AAMA 800-05 or 08 or 10 | Voluntary Specifications and Test Methods for Sealants | 2510.8 |
| --- | --- | --- |

AAMA/NPEA/NSA 	( Voluntary 02) Specifications for Sunrooms				202, 2002.1

2100- 02 or 11

(Mod S5674-R1 / AM)

Florida Specific Amendment

Chapter 35 – Referenced Standards

ACI

American Concrete Institute

P.O. Box 9094

Farmington Hills, MI 48333-9094

Standard reference number	Title		Referenced in code section number

117		Standard Tolerances for Concrete Construction and Materials	1920.2

224.3R—95	Joints in Concrete Construction (Reapproved 2001)	1911.2

301		Specifications for Structural Concrete for Buildings	1920.2

315		Manual of Standard Practice for Detailing Reinforced Concrete Structures	1920.2

347		Recommended Practice for Concrete Formwork	1920.2, 1925.1.1

506		Recommended Practice for Shotcreting	1920.2

506.2		Specification for Shotcrete		1920.2, 1929.1.2, 1929.8.1

530—11	Building Code Requirements for Masonry Structures	1405.5, 1405.5.3, 1405.9, 1604.3.4, 1605.3.1.1, 1618.9,1805.5.2, 1812.7, 2101.2.3, 2101.2.4, 2101.2.5, 2103.11.6, 2106.1, 2106.1.1.1, 2106.1.1.2, 2106.1.1.3, 2106.3, 2106.4, 2106.5, 2106.6, 2107.1, 2107.2, 2107.2.1, 2107.2.2, 2107.2.4, 2107.2.5, 2107.2.6, 2108.1, 2108.2, 2108.3, 2108.4, 2109.1, 2109.2.3.1, 2109.2.3.2, 2114.2, 2121.2.12, 2122.1

AF&PA

American Forest & Paper Association

1111 19th St, NW Suite 800

Washington, DC 20036

Standard reference number	Title		Referenced in code section number

Add to read as shown.

AF&PA—92   Wood Structural Design Data                        2314.4.7

AF&PA—05 Design Values for Joists and Rafters            2314.4.7

PWF--07 Permanent Wood Foundation (PWF) Design Specification   1805.4.6, 1807.2, 2304.9.5, 2314.4.7

WCD 1—01    Wood Construction Data No. 1, Details for Conventional Wood Frame Construction        2314.4.7

WCD 4— 03 Wood Construction Data No. 4, Plank and Beam Framing for Residential Buildings         2306.1.2, 2314.4.7

WCD 5—89    Wood Construction Data No. 5, Heavy Timber Construction Details                                   2314.4.7

WCD 6—06 Wood Construction Data No. 6, Design of Wood Frame Structures for Permanence       314.4.7, 2326.2.11

FGI AHA

American Hardboard Association

1210 West N.W. Highway

Palatine, IL 60067

Standard reference number	Title		Referenced in code section number

A135.4—2004	Basic Hardboard						1404.3.1, 2303.1.6, 2314.4.1

A135.5—2004	Prefinished Hardboard Paneling				2303.1.6, 2304.6.2, 2314.4.1

A135.6—98	Hardboard Siding						1404.3.2, 2303.1.6, 2314.4.1

A194.1—85	Cellulosic Fiber Board						2303.1.5, 2314.4.1

IB Spec. No. 1	Recommended Product and Application Specification —Structural Insulating Roof Deck					2314.4.1

IB Spec. No. 2	Recommended Product and Application Specification —½ inch Fiberboard Nail-Base Sheathing					2314.4.1

IB Spec. No. 3	Recommended Product and Application Specification —½ inch Intermediate Fiberboard Sheathing				2314.4.1

AISC	Torsional Analysis of Steel Members	2214.3

Change to read as shown:

AISC	Detailing for Steel Construction					2214.3

AISC	Engineering for Steel Construction					2214.3

AISC	Iron and Steel Beams - 1873 to 1952				2214.3

AISC	Serviceability Design Considerations for Low-Rise Buildings		2214.3, 2223.5.2

AISC	, Manual of Steel Construction, 2005, Thirteenth Edition		2214.3

AISC		Metal Building Certification Program, Category MB Certified		2223.11.2

AISI

American Iron and Steel Institute

1140 Connecticut Avenue, Suite 705

Washington, DC 20036

Standard reference number	Title		Referenced in code section number

Add to read as shown.

AISI	Design Manual For Cold-Formed Steel			2214.3

AISI	Design Manual for Structural Tubing			2214.3

Z—2	Designing Fire Protection for Steel Trusses			2214.3

Z—3	Designing Fire Protection for Steel Columns (Beams), No column listed 		2214.3

AISI	Fire-Resistant Steel-Frame Construction			2214.3

AISI	Fire-Safe Structural Steel - A Design Guide			2214.3

AISI	Specifications for Design of Light-Gage Cold-Formed Stainless Structural Members	2214.3

AISI	Specification for the Criteria for Structural Application of Steel Cables for Buildings	2214.3

SG02—1	North American Specification for Design of Cold-Formed Steel Structural Members 	2214.3

AITC

American Institute of Timber Construction

7012 S. Revere Parkway, Suite 140

Englewood, CO 80112

Standard reference number	Title		Referenced in code section number

A 190.1—07	Structural Glued Laminated Timber	   2303.1.3, 2306.1, 2314.4.2, 2315.1.1

Technical Note 7—96	Calculation of Fire Resistance of Glued Laminated Timbers	721.6.3.3, 2314.4.2

104—03	Typical Construction Details			2306.1, 2314.4.2

106	Code of Suggested Practices				2314.4.2

108—93	Standard for Heavy Timber Construction			2314.4.2

109—98	Standard for Preservative Treatment for Structural Glued Laminated Timber		2314.4.2

110—01	Standard Appearance Grades for Structural Glued Laminated Timber		2306.1, 2314.4.2

112—93	Tongue-and-Groove Heavy Timber Roof Decking	2306.1, 2314.4.2

113—01	Dimensions of Structural Glued Laminated Timber	2306.1, 2314.4.2

117—04	Standard Specifications for Structural Glued Laminated Timber of Softwood Species—Design Requirements—Standard Specifications for Structural Glued Laminated Timber of Softwood Species—Manufacturing Requirements					2306.1, 2314.4.2

119—96	Standard Specifications for Structural Glued Laminated Timber of Hardwood Species	2306.1, 2314.4.2

200—04		Inspection Manual					2306.1

ANSI

American National Standards Institute

25 West 43rd Street, Fourth Floor

New York, NY 10036

Standard reference number	Title		Referenced in code section number

Add to read as shown.

A 41.1	Building Code Requirements for Masonry		2119.1.1, 2121.2.8

A 41.2	Building Code Requirements for Reinforced Masonry		2119.1.1

A 42.1	Specification For Gypsum Plastering			2515.1.1

A 42.4	Standard Specification for Interior Lathing and Furring	2514.1

APA

APA - Engineered Wood Association

7011 So. 19th

Tacoma, WA 98466

Standard reference number	Title		Referenced in code section number

Add to read as shown.

APA E30		Engineered Wood Construction Guide		2314.4.3

APA PDS-Y510J—04       Plywood Design Specification (revised 1998)      2306.1, Table 2306.3.1, 2306.3.2, 2306.4.1, 2314.4.3

Change to read as shown.

APA PDS Supplement 1—90  Design and Fabrication of Plywood Curved Panels (revised1995) 2306.1, 2314.4.3

APA PDS Supplement 2—92 	Design and Fabrication of Plywood-lumber Beams (revised 1998)       2306.1, 2314.4.3

APA PDS Supplement 3—90	Design and Fabrication of Plywood Stressed-skin Panels (revised 1996)	2306.1, 2314.4.3

APA PDS Supplement 4—90	Design and Fabrication of Plywood Sandwich Panels (revised 1993)	2306.1, 2314.4.3

APA PDS Supplement 5—95	Design and Fabrication of All-plywood Beams (revised 1995)	2306.1, 2314.4.3

Add to read as shown.

APA B840		Siding Manufacturing Specifications		2314.4.3

APA L350		Design/Construction Guide Diaphragms and Shearwalls			2314.4.3

APA PRP108		Performance Standards and Policies for Structural-Use Panels	2314.4.3, 2315.1.2

APA V910		Plywood Folded Plate Laboratory Report 21		2314.4.3

APSP

Association of Pool and Spa Professionals

2111 Eisenhower Avenue

Alexandria, VA 22314

Standard                                                                                                            		  Referenced in code

reference number    	Title                                                                                                 section number

ANSI/NSPI 3—99 	American National Standard for Permanently Installed Residential

Spas								454.2.6.1

ANSI/APSP 4—12 	American National Standard for Aboveground/On ground

Residential Swimming Pools . . . .  . . . . . . . . . . . . . .. . . . . . .		454.2.6.1

.

ANSI/ APSP 5-11 	American National Standard for Residential In ground Swimming

Pools…………………………………………………………….	454.2.6.1

ANSI/APSP 6—12 	American National Standard for Portable Spas. 	. . . . . .. . . . . 	454.2.6.1

ANSI/APSP 7—06     	American National Standard for Suction Entrapment Avoidance in

Swimming Pools, Wading Pools, Spas, Hot Tubs, and Catch 		3109.5

Basins…………….……………………		.454.2.6.1, 454.2.6.3, 4354.26.6

ANSI/APSP 16—11     	American National Standard for Suction Fittings for Use in

Swimming Pools, Wading Pools, Spas, and Hot Tubs  		454.1.6.5.10.2…

(Mod SW5872-R1 / AM)

ASCE/SEI

American Society of Civil Engineers

Structural Engineering Institute

1801 Alexander Bell Drive

Reston, VA 20191-4400

Standard reference number	Title		Referenced in code section number

Change to read as shown.

3—91	Structural Design of Composite Slabs	1604.3.3, 1920.3, 2209.2, 2214.3

5—11	Building Code Requirements for Masonry Structures	1405.5, 1405.5.3, 1405.9, 1604.3.4, 1618.9, 1805.5.2, 1812.7, 2101.2.3, 2101.2.4, 2101.2.5, 2103.11.6, 2106.1, 2106.1.1.1, 2106.1.1.2, 2106.1.1.3, 2106.3, 2106.4, 2106.5, 2106.6, 2107.1, 2107.2, 2107.2.1, 2107.2.2, 2107.2.4, 2107.2.5, 2107.2.6, 2108.1, 2108.2, 2108.3, 2108.4, 2109.1, 2109.2.3.1, 2109.2.3.2, 2121.2.12,

7-10                              Minimum Design Loads for Buildings and Other Structures (with Errata dated January 11, 2011)

8—02	Specification for the Design of Cold-formed Stainless Steel Structural Members	1604.3.3, 2209.1, 2214.3

Add to read as shown.

11	Guidelines for Structural Condition Assessment of Existing Buildings	1920.3, 2003.2, 2214.3

FCI

Facility Guidelines Institute

1919 McKinney Avenue

Dallas, Texas 75201

www.fgiguidelines.org

Standard reference number	Title		Referenced in code section number

HHCF   10 	Guideline for the Design and Construction of  Health Care Facilities    419.2.1.2, 419.2.2, 419.3.2, 419.3.3, 419.3.4, 419.3.4.1, 419.3.4.2, 419.3.5, 419.3.5.1, 419.3.5.2, 419.3.6, 419.3.6.1, 419.3.7, 419.3.8.8, 419.3.8.9, 419.3.9, 419.3.10, 419.3.11, 419.3.13, 419.3.15, 419.3.17, 420.2.2, 420.2.5, 421.2.1.2, 421.2.2, 421.3.2, 421.3.2.1,  421.3.2.2, 421.3.3, 421.3.3.2.2, 421.3.3.3, 421.3.4, 421.3.5, 421.3.10

Illuminating Engineering Society of North America,

120 Wall Street, 17th Floor,

New York, NY 10005-4001.

ANSI/IESNA RP-28-07 	Lighting and the Visual Environment for Senior Living             …420.3.22.3

Add to read as shown.

ASHRAE

American Society of Heating, Refrigerating and Air-Conditioning Engineers, Inc.

1791 Tullie Circle NE

Atlanta, GA 30329-2305

Standard reference number	Title		Referenced in code section number

52.1—92	Gravimetric and Dust-Spot Procedures for Testing Air-Cleaning Devices Used in General Ventilation for Removing Particulate Matter ASHRAE Handbook—HVAC Applications 			Table 420.3.13.7

62—01	Ventilation for Acceptable Indoor Air Quality	Table 420.3.13.7

Change to read as shown.

A 17.1/CSA B44—07	Safety Code for Elevators and Escalators includes A17.1a in 2008 and A17.1b-2009 Addenda 1607.8.1, 3001.1, 3001.2, 3001.4, 3002.5, 3003.2, 3007.1, 3008.3,  3008.11.5, 308.14.1, 3008.1, 3010.1, 3011.1

ASME

Add to read as shown.

A 17.3—96	Safety Code for Existing Elevators and Escalators	3001.1, 3001.2, 3001.5

Change to read as shown.

A18.1—08                      	Safety Standard for Platform Lifts and Stairway Chairlifts              3001.1, 3001.2

Delete text to read as follows:

Add to read as shown.

A 120.1—01	Safety Requirements

A90.1 - 09                                           Safety Standard for Belt Manlifts                 3001.2

A120.1—01                                          Safety Requirements for Powered Platforms for Building Maintenance                 3001.6

B20.1 - 2009                                           Safety Standard for Conveyors and related equipment                                         3001.2,  3005.3

E 108—07a	Test Methods for Fire Tests of Roof Coverings	423.12.1, 1505.1, 1513.1, 1516.1, 1523.1.2, 2329.1, 2603.6, 2610.2, 2610.3

F1346—91 (2003)	Performance Specification for Safety Covers and Labeling Requirements for All Covers for Swimming Pools, Spas and Hot Tubs		424.1.3.9, 424.2.2, 424.2.17,

G53—96	Practice for Operating Light-and Water-Exposure Apparatus (Fluorescent UV-Condensation Type) for Exposure of Nonmetallic Materials

Add to read as shown.

Pub. No. 362		Safety Barrier Guidelines for Home Pools		424.1.3.1.9

ASTM

ASTM International

100 Barr Harbor Drive

West Conshohocken, PA 19428-2959

Standard reference number	Title		Referenced in code section number

A1760—76	Standard Specification for Pressure Treatment of Timber Products		Table 1823

A 6/A 6M— 04a	Specification for General Requirements for Rolled Steel, Structural Steel Bars, Plates, Shapes, and Sheet Piling			2214.3

A 29	Standards for General Requirements for Hot-Rolled and Cold-Finished Carbon and Alloy Steel Bars		1827.1

A 252—98(2007)	Specification for Welded and Seamless Steel Pipe Piles	1809.3.1, 1810.6.1, 1826.1.5.3

A 306	Carbon Steel Bars Subject to Mechanical Property Requirements		1827.1

A 325—94	Specification for Structural Bolts, Steel, Heat-Treated, 120/105 Ksi Minimum Tensile Strength			2214.3

A 361	Specification for Steel Sheet Zinc-Coated (Withdrawn)	2319.17.1.1

A 421/A 421M—02     Specification for Uncoated Stress-Relieved Steel Wire for

Prestressed Concrete    1922.4.2, 2103.11.6

A 446	Specification for Steel Sheet, Zinc-coated (Galvanized) by the Hot-Dip Process, Structural (Physical) Quality			1917.4.4

A 490—93          Specification for Heat-Treated, Steel Structural Bolts, 150 ksi

Minimum Tensile Strength                                                 2214.3

A 525—87	Specification for General Requirements for Steel Sheet, Zinc-Coated (Galvanized) by the Hot-Dip Process	1917.4.4, 2214.3, 2517.2, 2517.5.1, 2517.5.4

A570/A570M-98	Specification for Steel, Sheet and Strip, Carbon, Hot-Rolled (withdrawn)	1826.1.5.3

A 611	Standard Specification for Structural Steel (SS), Sheet, Carbon, Coil-Rolled	1826.1.5.3, 1917.4.4

A 615/A 615M—09	Specification for Deformed and Plain Billet-Steel Bars for Concrete Reinforcement	1908.1.8, 1920.2, 1920.4, 1922.4.6, 2103.11.1, 2103.11.6

A616/A616M-96a	Specification for Rail-Steel Deformed and Plain Bars for Concrete Reinforcement (withdrawn)			1922.4.6

A 617	Standard Specification for Axle-Steel Reformed and Plain Bars for Concrete Reinforcement					1922.4.6

A 653/A 653M—08	Specification for Steel Sheet, Zinc-Coated Galvanized or Zinc-Iron Alloy-Coated Galvannealed by the Hot-Dip Process	Table 1507.4.3, 2211.2, 2211.2.2.1, 2319.17.2.2.7

A 706/A 706M—09	Specification for Low-Alloy Steel Deformed and Plain Bars for Concrete Reinforcement	1903.5.2, 1908.1.3, 1922.4.6

A 722/A 722M—07     Specification for Uncoated High-Strength Steel Bar for Prestressing Concrete	1922.4.2, 2103.11.6, 2106.1.1.3.1

A 767/A 767M—00b	Specification for Zinc-Coated (Galvanized) Steel Bars for Concrete Reinforcement	1922.4.6, 1926.5.5, 2103.11.1

A 775/A 775M—03(2008)Specification for Epoxy-Coated Steel Reinforcing Bars		1922.4.6, 2103.11.1

Revise text to read as follows:

A 924 /A924M—08a  Standard Specification for General Requirements for Steel Sheet, Metallic-

coated by the Hot-dip Process . . . . . . . . . . .			 Table 1507.4.3(1). 2319.17.2.2.7.

B 370-09              Specification for Copper Sheet and Strip for Building Construction        Table 1507.4.3

C 5—03	Specification for Quicklime for Structural Purposes	Table 2507.2, 2525.2.3

C 28/C 28M—00 (2005) Specification for Gypsum Plasters		Table 2507.2, 2515.2.2

C 31/C 31M—08b	Practice for Making and Curing Concrete Test Specimens in the Field.	1905.6.3.2, 1905.6.4.2, 1923.2.2.3, 1923.2.3.2

C 33—08	Specification for Concrete Aggregates 	721.3.1.4, 721.4.1.1.3, Table 1904.2.1, 1922.1, 1922.2, 1922.2.2

C 34—03	Specification for Structural Clay Load-Bearing Wall Tile	2103.2, 2119.8.3

C 35—01(2005)	Specification for Inorganic Aggregates for Use in Gypsum Plaster 	Table 2507.2, 2515.2.1.1

C 36/C 36M—03	Specification for Gypsum Wallboard 		Figure 721.5.1(2), Figure 721.5.1(3), Table 721.5.1(2), Table 2506.2, 2517.2

C 37/C 37M—-01	Specification for Gypsum Lath		Table 2507.2, 2514.2

C 39—99ae1	Test Method for Compressive Strength of Cylindrical Concrete Specimens 	1905.6.3.2, 1923.2.2.3

C 42/C 42M—99	Test Method for Obtaining and Testing Drilled Cores and Sawed Beams of Concrete	1923.2.4.1, 1923.2.4.3

C 52-01A	Specification for Gypsum Partition Tile or Block					2119.9.3

C 55—06e01	Specification for Concrete Brick	Table 721.3.2, 2103.1, 2105.2.2.1.2, 2119.4.3.2, 2119.4.3.3

C 56—05	Specification for Structural Clay Non-Load-Bearing Tile		2103.2, 2119.8.3.3

C 57	Specification for Structural Clay Floor Tile			2119.8.3.2

C 61/C 61M—00 (2006)	Specification for Gypsum Keene’s Cement			Table 2507.2, 2515.2.4

C 62—08	Specification for Building Brick (Solid Masonry Units Made from Clay or Shale)		2103.2, 2105.2.2.1.1, 2119.4.3.1

C 67—08	Test Methods of Sampling and Testing Brick and Structural Clay Tile 	721.4.1.1.1, 1507.3.5, 2104.5, 2105.2.2.1.1, 2109.8.1.1, 2119.4.2

C 90—08 11b	Specification for Loadbearing Concrete Masonry Units	Table 721.3.2, 1805.5.2, 2103.1,

(Mod S6021 / AS)							2105.2.2.1.2, 2119.7.2

C 91—05	Specification for Masonry Cement			Table 2103.7(1), Table 2507.2, 2515.2.6

C 94/C 94M—07	Specification for Ready-Mixed Concrete		109.3.1, 1905.8.2, 1924.2.2, 1924.2.3

C 144—03	Standard Specification for Aggregate for Masonry Mortar		1928.7.2, 2119.12.1.1

C 150—07	Specification for Portland Cement 	1904, Table 1904.2.3, 1922.1, Table 2103.7(1), Table 2507.2, 2515.2.4

C 172—08	Practice for Sampling Freshly Mixed Concrete			1905.6.3.1, 1923.2.2.2

C 206—03	Specification for Finishing Hydrated Lime			Table 2507.2, 2525.2.3

C 212—00(2006)	Specification for Structural Clay Facing Tile					2103.2, 2119.8.2

C 216—07a	Specification for Facing Brick (Solid Masonry Units Made from Clay or Shale)	2103.2, 2105.2.2.1.1, 2119.4.3.1

C 270—08a	Specification for Mortar for Unit Masonry			2103.7, Table 2103.7(2), 2119.12.1

C 330—05	Specification for Lightweight Aggregates for Structural Concrete	721.1.1, 1905.1.4,

1922.2.2

C 471M—01	Standard Test Methods for Chemical Analysis of Gypsum and Gypsum Products		2119.9.2

C 472—99 (2004)	Specification for Standard Test Methods for Physical Testing of Gypsum, Gypsum Plasters and Gypsum Concrete						Table 2506.2, 2119.9.2

C 473—07	Test Method for Physical Testing of Gypsum Panel Products		Table 2506.2, 2119.9.2

C 475—02(2007	Specification for Joint Compound and Joint Tape for Finishing Gypsum Wallboard		Table 2506.2, 2517.2

C 494/C494M-99	Standard Specification for Chemical Admixtures for Concrete				1917.4.5

C 495–99a	Standard Test Method for Compressive Strength of Lightweight Insulating Concrete	1917.1.1, 1917.1.2, 1917.1.3

C 509-00               Elastomeric Cellular Preformed Gaskets and Sealing Material      2411.3.4

C 578—08b	Standard Specification for Rigid, Cellular Polystyrene Thermal Insulation	1917.4.12

C 595—08a	Specification for Blended Hydraulic Cements	1922.1.2, Table 2103.7(1), Table 2507.2

C 645—08a	Specification for Nonstructural Steel Framing Members	2319.17.1.3, Table 2506.2, Table 2507.2, 2517.2, 2517.5.1, 2517.5.4

C 652—09	Specification for Hollow Brick (Hollow Masonry Units Made from Clay or Shale)	2103.2, 2105.2.2.1.1, 2119.4.3.1, 2119.4.3.1

C 685/ C 685M—98a	Specification for Concrete Made by Volumetric Batching and Continuous Mixing	1905.8.2, 1924.2.2

C 794—01	Standard Test Method for Adhesion-in-Peel of Elastomeric Joint Sealants	2415.4

C 796—97	Standard Test Method for Foaming Agents For Use in Producing Cellular Concrete Using Performed Foam	1917.1.1, 1917.1.2, 1917.1.3, 1917.4.6

C 864-05               Dense Elastomeric Compression Seal Gaskets, Setting Blocks, and Spacers    2411.3.4

- C 920—08 Specification for Elastomeric Joint Sealants .……………. 2415.4, 2510.8.8

C 926—06 11a	Specification for Application of Portland Cement-Based Plaster	2510.3, Table 2511.1, 2511.3, 2511.4, 2512.1, 2512.1.2, 2512.2, 2512.6, 2512.8.2, 2513.7, 2512.9, 2513.7, 2516.1.1, 2516.1.4

(Mod S6021 / AS)

C 1036—01	Specification for Flat Glass							2411.1.1

C 1048—97b	Standard Specification for Heat-Treated Flat Glass—Kind HS, Kind FT Coated and Uncoated Glass									2411.1.5

C 1063-08 12a	Specification for Installation of Lathing and Furring to Receive Interior

and Exterior Portland Cement-based Plaster

(Mod S6021 / AS)

C 1077	Standard Practice for Laboratories Testing Concrete and Concrete Apparatus for Use in Construction and Criteria for Laboratory Evaluation				1920.4, 1922.6.2

C 1115-00             Dense Elastomeric Silicone Rubber Gaskets and Accessories        2411.3.4

C 1167—03	Specification for Clay Roof Tiles		1507.3.4, 1507.3.5, 1523.6.5.2

C 1225	Specification For Nonasbestos Fiber-Cement Roofing Shingles, Shakes and Slates	1518.5.1

C 1281- 03 Standard Specification for Preformed Tape Sealants for Glazing Applications …………………………………………………………. 2510.8

D 25—99- ((2005)	Specification for Round Timber Piles		1809.1.1, 1823.1

D 41—05	Specification for Asphalt Primer Used in Roofing, Dampproofing, and Waterproofing	Table 1507.10.2, 1514.2.3.2, 1517.6.2.4, 1519.6, 1521.6, 1521.14.1

D 43-00 (2006)	Specification for Coal Tar Primer Used in Roofing, Dampproofing, and Waterproofing 	Table

1507.10.2, 1521.14.2, 1517.6.2.4, 1519.6, 1521.6

D 92	Standard Test Method for Flash and Fire Points by Cleveland Open Cup		1519.2.2

D 256—03	Standard Test Methods for Determining the Izod Pendulum Impact Resistance of Plastics	2612.2

D 312—00(2006)	 Specification for Asphalt Used in Roofing	Table 1507.10.2, 1519.3, Table 1519.3A, 1519.4,

1521.14.1

D412—98a (2002)e1	Standard Test Methods for Vulcanized Rubber and Thermoplastic Elastomers—Tension

D 450—07	Specification for Coal-Tar Pitch Used in Roofing, Dampproofing, and Waterproofing	Table 1507.10.2, Table 1519.3B

D624—00e1	Standard Test Method for Tear Strength of Conventional Vulcanized Rubber and Thermoplastic Elastomers			2415.4

D 635—06	Test Method for Rate of Burning and/or Extent and Time of Burning of Self-Supporting Plastics in a Horizontal Position	2606.4, 2612.2

D 638-03              Test Method for Tensile Properties of Plastics          2612.2

D1079—02	Standard Terminology Relating to Roofing, Waterproofing, and Bituminous Materials	1513.1

D1143/D 1143M- 07el	Test Method for Piles Under Static Axial Compressive Load	1808.2.8.3, 1829.1.7

D1167	Methods of Testing Asphalt-Base Emulsions for Use as Protective Coatings for Built-Up Roofs	1523.6.5.2

D1556	Standard Test Method for Density of Soil In-Place by the Sandcone Method	1820.3.2, 1834.3.3

D1557—07	Test Method for Laboratory Compaction Characteristics of Soil Using Modified Effort (56,000 ft-lb/ft3 (2,700 kN m/m3))	1803.5, 1820.3.2

D1621	Standard Test Method for Compressive Properties of Rigid Cellular Plastics	1523.6.5.2.17.1

D1622	Standard Test Method for Apparent Density of Rigid Cellular Plastics	1523.6.5.2.17.2

D1623	Standard Test Method for Tensile and Tensile Adhesion Properties of Rigid Cellular Plastics	523.6.5.2.17.3

D1761—06     Test Method for Mechanical Fasteners in Wood	                        1716.1.2, 1716.1.2.1, 1716.1.2.2

1834.3.3, 2314.4.4 ,

D 1761-88 (2000) Standard Test Methods for Mechanical Fasteners in Wood  1716.1.2, 1716.1.2.1, 1716.1.2.2

(Mod S6023-R1 / AM)

D1836 	Specification for Commercial Hexanes			1519.12.1

D1863—05	Specification for Mineral Aggregate Used on Built-Up Roofs	Table 1507.10.2, 1519.2.1

D1929—96 (2000)e01	Test Method for Determining Ignition Properties of Plastics	402.14.4, 406.5.2,

1407.11.2.1, 2606.4, 2612.2

D2126	Standard Test Method for Response of Rigid Cellular Plastics to Thermal and Humid Aging	523.6.5.2.17.4

D2240—03	Standard Test Method for Rubber Property—Durometer Hardness			2415.4

Add text to read as follows:

D 2824  - 06 Standard Specification for Aluminum-Pigmented Asphalt Roof Coatings, Nonfibered Asbestos Fibered, and Fibered without Asbestos…….    Table 1507.10.2

D2565—00	Standard Practice for Xenon Arc Exposure of Plastics Intended for Outdoor Applications	2612.2

D2626—04	Specification for Asphalt-Saturated and Coated Organic Felt Base Sheet Used in Roofing	1507.3.3, Table 1507.10.2, 1518.4

D2842	Standard Test Method for Water Absorption of Rigid Cellular Plastics	1523.6.5.2.17.6

D2843—99(2004)e01	Test for Density of Smoke from the Burning or Decomposition of Plastics	2606.4,

2612.2

D2856	Standard Test Method for Open-cell Content of Rigid Cellular Plastics by the Air- Pycnometer.	523.6.5.2.17.5

D2898—04	Test Methods for Accelerated Weathering of Fire-Retardant-Treated Wood for Fire Testing	1505.1, 1516.1, 2303.2.1, 2303.2.3, 2314.4.4, 2327.4, 2329.1

D2922	Standard Test Method for Density of Soil and Soil Aggregate In-Place by Nuclear Methods (Shallow Depth)				1820.3.2

D3018	Standard Specification for Class A Asphalt Shingles Surfaced with Mineral Granules	1523.6.5.1

D3201—08a	Test Method for Hygroscopic Properties of Fire-Retardant Wood and Wood-Base Products						2303.2.4, 2314.4.4, 2327.5

D3441	Static Cone Soundings					1834.3.3

D3462—09	Specification for Asphalt Shingles Made from Glass Felt and Surfaced with Mineral Granules

1507.2.5, 1523.6.5.1

D 3498—03	Standard Specifications for Adhesives for Field-Gluing Plywood to Lumber Framing for Floor Systems			2314.4.4, 2322.1.5

D3679—09	Specification for Rigid Poly (Vinyl Chloride) (PVC) Siding		1404.9, 1405.13

D3737—08	Practice for Establishing Allowable Properties for Structural Glued Laminated Timber (Glulam)	2303.1.3

D3746—85 (2008) 	Test Method for Impact Resistance of Bituminous Roofing Systems	1504.7, 1515.2.4

D3787—89	Test Method for Bursting Strength of Textiles-Constant-Rate-of-Traverse (CRT) Ball Burst Test	424.2.17.1.15

D4272—08a	Test Method for Total Energy Impact of Plastic Films by Dart Drop		1504.7, 1515.2.4

D4402	Viscosity Determinations of Unfilled Asphalt Using the Brookfield Thermoset Apparatus	1519.2.3

D4477-04a           Standard Specification for Rigid (Unplasticized) Poly (Vinyl Chloride) (PVC) Siding

1404.9, 1404.9.1, 1405.13

D5034—95	Standard Test Method for Breaking Strength and Elongation of Textile Fabrics (Grab Test)	24.2.17.1.15

D5055—09	Specification for Establishing and Monitoring Structural Capacities of Prefabricated Wood I-joists	424.2.14.1.15, 2303.1.2

D5456—09	Specification for Evaluation of Structural Composite Lumber Products		2303.1.9

D5957-98             Standard Guide for Flood Testing Horizontal Waterproofing Installation 1519.16.6

D6083—05e01	Specification for Liquid Applied Acrylic Coating Used in Roofing Table 1507.10.2, 1507.15.2,

1523.6.2.1.1, 1523.6.3.1, 1523.6.5.12.2

D6380-03(2009)	Specifications for Asphalt Roll Roofing (Organic Felt)	1507.3.3

Add text to read as follows:

D6841-08 b         Standard Practice for Calculating Design Value Treatment Adjustment Factors

for Fire-Retardant-Treated Lumber                     				     2303.2.2.2

D7147 – 11 	Standard Specification for Testing and Establishing Allowable Loads of Joist Hangers    1711.1.1

(Mod S6023-R1 / AM)

D7158-08d              Standard Test Method for Wind Resistance of Sealed Asphalt Shingles (Uplift Force/Uplift

Resistance Method)                                        Table 1507.2.10

E 84—09	Test Method for Surface Burning Characteristics of Building Materials	402.10, 402.14.4, 406.5.2, 410.3.5.3, 422.2.16.3, 423.11.5, 703.4.2, 719.1, 719.4, 802.1, 803.1, 803.5, 803.6.1, 803.6.2, 1407.10, 1407.10.1, 2303.2, 2314.4.4, 2327.1, 2603.3, 2603.4.1.13, 2603.5.4, 2604.2.4, 2606.4, 2612.2, 2612.3

E 96/E 96M—05	Test Method for Water Vapor Transmission of Materials		1203.2, 1523.6.5.2.17.7

E 108—07a	Test Methods for Fire Tests of Roof Coverings	423.12.1, 1505.1, 1513.1, 1516.1, 1523.1.2, 2329.1, 2603.6, 2610.2, 2610.3

E 119—08a	Test Methods for Fire Tests of Building Construction and Materials	410.3.5.2, 703.2, 703.2.1, 703.2.3, 703.3, 704.7, 704.9, 706.7, 711.3.2, 712.3.1, 712.4.1, 712.4.6, 713.1, 713.4, 714.7, 715.2, 716.5.2, 715.5.3.1, 715.6.2, 716.5.2, 716.5.3.1, 716.6.2, Table 721.1(1), 1407.10.2, 2103.2, 2603.3, 2603.4, 2603.4.1.13, 2603.5.4, 2604.2.4, 2606.4, 2612.2, 2612.3.1.1, 2612.3.1.4

E163-84E01	Methods of Fire Tests For Window Assemblies (withdrawn)			2121.2.1.2.8

E 330—02	Test Method for Structural Performance of Exterior Windows, Curtain Walls, and Doors by Uniform Static Air Pressure Difference				1714.5.3, 2415.4, 2415.7.1

E 331—00(2009)	Test Method for Water Penetration of Exterior Windows, Skylights, Doors, and Curtain Walls by Uniform Static Air Pressure Difference					1403.2, 2415.4

E1300—04e01,07e01, 09a or 98 (HVHZ)	Practice for Determining Load Resistance of Glass in Buildings			1714.5.2.1, 2404.1, 2404.2, 2404.3, 2411.2.1.1, 2411.2.1.2, 2411.3.1.2

(Mod S5671-R1 / AM)

E1592—01	Test Method for Structural Performance of Sheet Metal Roof and Siding Systems by Uniform Static Air Pressure Difference					1504.3.2, 2411.2.1.2

E 2203-02             Dense Thermoplastic Elastomers Used for Compression Seals, Gaskets, Setting Blocks, Spacers and Accessories                                                                                             2411.3.4

E 1886·02 or 05 Standard Test Method for Performance of Exterior Windows. Curtain Walls.

Doors. and Storm Shutters Impacted by Missile(s) and Exposed to Cyclic Pressure Differentials

1609.1.2, 1710.5

E 1996- 02, 05, 06, 09, or 12  Specification for Performance of Exterior Windows. Glazed Curtain Walls.

Doors. and Storm Shutters Impact by Windborne Debris in Hurricanes 		1609.1.2, 1609.1.2.2,-1710.5

(Mod S5674-R1 / AM)

F851—87 (2000)	Standard Test Method for Self-Rising Seat Mechanisms	1024.10

F1346—91 (2003)	Performance Specification for Safety Covers and Labeling Requirements for All Covers for Swimming Pools, Spas and Hot Tubs		424.1.3.9, 424.2.2, 424.2.17,

G53—96	Practice for Operating Light-and Water-Exposure Apparatus (Fluorescent UV-Condensation Type) for Exposure of Nonmetallic Materials					424.17.1.15.2

G85	Standard Practice for Modified Salt Spray (Fog) Testing	1517.5.1, 1517.5.2, 1523.6.5.2.10, 1523.6.5.2.11

G60—01	Standard Practice for Conducting Cyclic Humidity Tests			2319.17.2.2.8

G 155 – 05a 	Standard Practice for Operating Xenon Arc Light Apparatus for Exposure of

Non-Metallic Materials………						….2612.2

AWPA

American Wood-Preservers’ Association

P.O. Box 5690

Grandbury, TX 76049

Standard reference number	Title			Referenced in section number

Change to read as shown.

C1—03	All Timber Products—Preservative Treatment by Pressure Processes	1505.6, 2303.1.8, 2314.4.5

C2—01	Lumber, Timber, Bridge Ties and Mine Ties—Preservative Treatment by Pressure Processes

Table 1507.9.5, 1805.4.5, 1805.7.1, 2303.1.8, 2304.11.2, 2304.11.4, 2304.11.7, 2314.4.5

C3—99	Piles—Preservative Treatment by Pressure Processes	1805.4.5, 1809.1.2, 1823.1.3, 2303.1.8, 2314.4.5

C4—99	Poles—Preservative Treatment by Pressure Processes		1805.7.1, 1808.1.2, 2303.1.8, 2314.4.5

Add to read as shown.

C5	Posts - Pressure Treatment					2314.4.5

C6	Cross Ties and Switch Ties Pressure Treatment		2314.4.5

C7	Incised (Red, White & Alaska Yellow Cedar) Poles Butts Thermal Treatment		2314.4.5

C8	Poles (Western Red & Alaska Yellow Cedar) Full Length Thermal Treatment		2314.4.5

Change to read as shown.

C9—00	Plywood—Preservative Treatment by Pressure Processes	2304.11.2, 2304.11.4, 2304.11.7, 2314.4.5

Add to read as shown.

C10	Poles (Lodgepole Pine) Full Length Thermal Treatment	2314.4.5

C11	Wood Blocks for Floors & Platforms Pressure Treatment	2314.4.5

Change to read as shown.

C14—99	Wood for Highway Construction, Pressure Treatment by Pressure Process          2314.4.5

C16—00	Wood Used on Farms, Pressure Treatment by Pressure Process 	2314.4.5

C18—99	Standard for Pressure Treated Material in Marine Construction	    2314.4.5

Add to read as shown.

C20	Structural Lumber, Fire Retardant Pressure Treatment	    2314.4.5

Change to read as shown.

C22—96	Lumber and Plywood for Permanent Wood Foundations— Preservative Treatment by Pressure Processes		1805.4.6, 2314.4.5

C23—00	Round Poles and Posts Used in Building Construction— Preservative Treatment by Pressure Processes			2314.4.5

Add to read as shown.

C25	Crossarms Pressure Treatment				2314.4.5

C26		Crossarms, Non-Pressure Treatment			2314.4.5

Change to read as shown.

C28—99	Standard for Preservative Treatment by Pressure Process of Structural Glued Laminated Members and Laminations before Gluing					2314.4.5

Add to read as shown.

C29	Lumber to be Used for the Harvesting, Storage and Transportation of Food Stuffs— Preservative Treatment by Pressure Processes	2314.4.5

Change to read as shown.

M4—08	Standard for the Care of Preservative-Treated Wood Products	1809.1.2, 1823.1.4, 2303.1.8, 2314.4.5

Add to read as shown.

M6—96	Brands Used on Forest Products							2315.1.9

AWS

American Welding Society

550 N.W. LeJeune Road

Miami, FL 33126

Standard reference number	Title			Referenced in section numb

Add to read as shown.

B2.1	Standard Welding Procedure and Performance Qualification	2214.3

C5.4	Recommended Practice for Stud Welding			2214.3

Change to read as shown.

D1.1—04	Structural Welding Code—Steel				2214.3

Add to read as shown.

D1.2	Structural Welding Code—Aluminum			2003.3

Change to read as shown.

D1.3—98	Structural Welding Code—Sheet Steel			2214.3

D1.4—98	Structural Welding Code—Reinforcing Steel	1903.5.2, 1922.4.4, 1922.4.5, 1926.4.6, 1926.4.8, 2119.1.1, 2214.3

Add to read as shown.

D9.1	Specification for Welding of Sheet Metal			2214.3

D10.9	Standard for Qualification of Welding Procedures and Welders for Piping and Tubing	2214.3

CPSC

Consumer Product Safety Commission

4330 East West Highway

Bethesada, MD 20814-4408

Standard reference number	Title			Referenced in section number

Change to read as shown.

16 CFR Part 1201(2002)	Safety Standard for Architectural Glazing Material		2406.1.1, 2406.2.1, 2407.1, 2408.2.1, 2408.3, 2411.1.3, 2411.3.1.3, 2411.4.2, 2612.4.8,

Add to read as shown.

Pub. No. 362		Safety Barrier Guidelines for Home Pools		424.1.3.1.9

DOC/NIST

Department of Commerce

National Institute of Standards and Technology

100 Bureau Drive Stop 3460

Gaithersburg, MD 20899

Standard reference number	Title		Referenced in section number

Add to read as shown.

CS236	Mat-Formed Particleboard					2314.4.6, 2315.1.6

Change to read as shown.

PS-1-09	Construction and Industrial Plywood	2211.2.2.2, 2303.1.4, 2304.6.2, Table 2304.7(4), 2306.3.2, 2314.4.6, 2315.1.2

PS-2-10	Performance Standard for Wood Based Structural Use Panels	1809.1.1, 2211.3.1, 2303.1.4, 2304.6.2, Table 2304.7(4), Table 2304.7(5), Table 2306.3.1, 2306.3.2, 2314.4.6, 2315.1.2

PS20-05	American Softwood Lumber Standard        1809.1.1, 2302.1, 2303.1.1, 2314.4.6, 2315.1.8

Add to read as shown.

PS56	Structural Glued Laminated Timber					2314.4.6

DOL/OSHA

Department of Labor

Occupational Safety and Health Administration

Frances Perkins Building

200 Constitution Avenue, NW

Washington, DC 20210

Standard reference number	Title			Referenced in section number

Add to read as shown.

29CFR Part 1910		Occupational Safety and Health Standards		1618.4

29CFR 1926-950 (p)	Occupational Safety and Health Administration

Excavation Safety Act	1817.1

DOT

Department of Transportation

c/o Superintendent of Documents

U.S. Government Printing Office

Washington, DC 20402-9325

Standard reference number	Title			Referenced in section number

Add to read as shown.

FBC-TPHVHZ—2013	Florida Building Code, Test Protocols for High Velocity Hurricane Zones

RAS 109	1521.18, 1523.6.2.1

RAS 111	1503.3, 1504.5, 1514.2, 1514.2.1, 1514.2.2, 1514.2.3, 1514.2.4, 1514.2.5.2, 1514.3, 1514.4.1.1, 1515.2.3.2, 1517.6.1, 1517.6.2.1, 1517.6.2.3, 1517.6.2.5, 1518.5.3, 1518.6.2, 1518.7.3.4, 1518.9.5, 1519.8, 1519.10, 1519.13, 1523.6.5.2.14, 1519.16.5, 1523.6.5.2.14

RAS 115	1518.7

RAS 117              1519.7, 1519.11, 1520.4, 1520.5, 1521.7.1, 1521.14.3, 1523.6.5.29

RAS 118	1518.8.1

RAS 119	1518.8.1

RAS 120	1518.8.1

RAS 127	1518.8.5, 1518.8.6, 1523.6.5.2, 1523.6.5.2.2.2, 1523.6.5.2.2.3, 1523.6.5.2.3.2, 1523.6.5.2.3.3, 1523.6.5.2.6.2, 1525

RAS 128	1525

RAS 130	1518.10

RAS 133	1519.9.2

RAS 150	1519.1

TAS 100	1523.6.5, 1523.6.5.1, 1523.6.5.2, 1523.6.5.2.4, 1523.6.5.2.4.1, 1523.6.5.2.5, 1523.6.5.2.6, 1523.6.5.2.7

TAS 100A	1523.6.5.2.13

TAS 101	1523.6.5.22.2 1523.6.2.22, 1523.6.5.2.2.3

TAS 102	1523.6.5.2.3, 1523.6.5.2.3.2, 1523.6.5.2.3.3, 1523.6.5.2.6.2, 1523.6.5.2.6.3

TAS 102A	1523.6.5.2.3, 1523.6.5.2.3.2, 1523.6.5.2.3.3, 1523.6.5.2.6.2, 1523.6.5.2.6.3

TAS 103	1523.6.5.2.1

TAS 104	1523.6.5.2.1

TAS 105	1513.1, 1519.7.1, 1521.7, 1521.11

TAS 106	1512.4.2.4, 1523.6.5.2.2.4, 1523.6.5.2.3.4, 1523.6.5.2.6.4

TAS 107	1507.2.10, Table 1507.2.10, 1523.6.5.1

TAS 108	1523.6.5.2.2.1, 1523.6.5.2.2.2, 1523.6.5.2.2.3, 1523.6.5.2.3.1, 1523.6.5.2.3.2, 1523.6.5.2.3.3, 1523.6.5.2.6.1, 1523.6.5.2.6.2, 1523.6.5.2.6.3, 1715.2, 1715.2.2

TAS 110	1515.1.4, 1515.2.5, 1520.1, 1520.4, 1523.1.1, 1523.6.2, 1523.6.2.1, 1523.6.3, 1523.6.5.2.4.1, 1523.6.5.2.6, 1523.6.5.2.7, 1523.6.5.2.8, 1523.6.5.2.9, 1523.6.5.2.12, 1523.6.5.2.13.1, 1523.6.5.2.14, 1523.6.5.2.15, 1523.6.5.2.16, 1523.6.5.2.17

TAS 110A	1523.6.5.2.13

TAS 111A	1523.6.5.2.14

TAS 111B	1523.6.5.2.14

TAS 111C	1523.6.5.2.14

TAS 112	1523.6.5.2

TAS 113	1518.8.1.1

TAS 114	1513.1, 1515.1.1, 1515.2.4, 1517.5.1, 1519.5.1, 1520.4, 1523.6.2, 1523.6.2.1, 1523.6.3, 1523.6.5.2.9, 1523.6.5.2.10, 1523.6.5.2.11

TAS 115	1523.6.5.2.6.3

TAS 116	1513.1, 1523.6.5.2.2.1, 1523.6.5.2.3.1, 1523.6.5.2.6.1

TAS 121	1523.6.5.2.12

TAS 123	1518.8.1.1, 1523.6.5.2.15, 1523.6.5.2.17

TAS 123A	1523.6.5.2.16

TAS 124	1521.10, 1523.6.4

TAS 125	1518.9.1, 1523.6.5.2.4.1

TAS 126	1521.12

TAS 135	1523.6.5.2.6

TAS 201	202, 1609.1.4

TAS 202    1609.1.4, 1008.1.6, 1714.5.2.1, 1714.5.2.1.1, 1714.5.3, 1714.6

TAS 203	202, 1609.1.4

TAS 301	1515.1.3

Change to read as shown.

Florida Codes

Florida Building Commission

Building Codes and Standards

Department of Community Affairs Business and Professional Regulation

2555 Shumard Oak Blvd. 1940 N. Monroe St.

Tallahassee, Fl. 32399-2100 0772

Change to read as shown.

FM

Factory Mutual

Standards Laboratories Department

1151 Boston-Providence Turnpike

Norwood, MA 02062

Standard reference number	Title			Referenced in section number

4450 (1992) 	Approval Standard for Class 1 Insulated Steel Deck Roofs—with Supplements through July 1992	1504.3.1, 1508.1, 2603.3, 2603.4.1.5, 2612.3.2.5.2

Add to read as shown.

FM

4470 (1992) Approval Standard for Class 1 Roof Covers  .. . .1504.3.1, 1504.7, 1515.1.1

4471		Approval Standard for Class I Panel Roofs			1515.1.1

Add to read as shown:

FRSA

Florida Roofing, Sheet Metal and Air Conditioning Contractors Association

4111 Metric Drive

Winter Park, Florida 32792

Standard reference	Title							Referenced in code

number 									section number

FRSA/TRI 07320/8—05 	Florida High Wind Concrete and Clay Roof                       1507.3.2, 1507.3.3, 1507.3.3.1,

April 2012 (04-12)	Tile Installation Manual, Fourth Fifth Edition                       1507.3.6, 1507.3.7, 1507.3.8, 1507.3.9

(Mod R5586 / AS)

GSA

General Services Administration

1800 F Street, NW

Washington, DC 20405

Standard reference number	Title		Referenced in section number

DD-G-451D (1977)	Glass, Flat and Corrugated for Glazing Mirrors and Other Uses		2411.1.2

DECO

Document Engineering Co., Inc.,

5210 Stagg Street

Van Nuys, California 9140

ANSI Z 358.1 04  Emergency Eyewash and shower Equipment    Table 420.3.17.2

FINA

Federation Internationale de Natation Amateur

Av. de l' Avant-Poste 4

1005 Lausanne

SWITZERLAND

Standard reference number	Title		Referenced in section number

CHG-22	FINA Handbook 1998-2000					424.1.2.7

NFPA

Add to read as shown.

10—10		Standard for Portable Fire Extinguisher		419.4.2.10.2, 420.4.2.10.1.2, 423.28.2.14

Change to read as shown.

13—10                Installation of Sprinkler Systems	402.4.6, 431, 704.12, 707.2, 903.1.4, 903.3.1.1, 903.3.2, 903.3.5.1.1, 904.11, 907.8, 1621.3.10.1, 2121.2.12.8, 3104.5, 3104.9

30—12 	Flammable and Combustible Liquids Code			415.3, 423.20.4.1

Revise text to read as follows:

NFPA

61—08	Prevention of Fires and Dust Explosions in Agricultural and Food Product Facilities	415.7.1,

423.7.7

72—10	National Fire Alarm Code	423.7.7, 436.7.1.1, 436.7.1.3, 416.7.2, 436.10.5.1, 436.10.5.2, 505.4, 901.6, 903.4.1, 904.3.5, 907.2, 907.2.1, 907.2.1.1, 907.2.10, 907.2.10.4, 907.2.11.2, 907.2.11.3, 907.2.12.2.3, 907.2.12.3, 907.4, 907.5, 907.9.2, 907.10, 907.14, 907.16, 907.17, 911.1, 1008.1.3.7.4, 3002.8, 3006.5

96-04 Standard for Ventilation Control and Fire Protection of Commercial Cooking Operations . . . . . . . . . . . . . . . . . . . . . . . . 436.6.2

99—10  Standard for Health Care Facilities. . . . . . . . . . . . . . . . . . . . . . . . . . . . . 4203.18.1, 420.3.20.2, 420.3.25.1, 419.3.18, 419.3.18.8

101—12 Life Safety Code . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 420.3.3.6, 423.6.1, 423.14.2.1, 423.27.9.1, 423.27.10.1, 427.2.2.1.1.1, 427.1.4.13.2, 427.1.4.2.13, 427.1.4.1.1.2, 427.1.3.1.1.2, 903.6.2, 1024.6.2

110—10	Emergency and Standby Power Systems	419.3.18, 419.3.18.8, 420.3.25, 1006.2.33, 421.3.13.1, 4006.2.3.3, 1006.2.3.3, 2702.1

Add to read as shown.

780—04  Installation of Lighting Systems . . .419.3.19, 420.3.26.1, 423.17.7

PCA

Portland Cement Association

5420 Old Orchard Road

Skokie, IL 60077

Standard reference number	Title			Referenced in section number

EB008-9	Concrete Masonry Handbook				2119.1.1

SMACNA

Sheet Metal and Air Conditioning Contractors' National Association

8224 Old Courthouse Rd.

Vienna, VA 22180

Standard reference number	Title		Referenced in section number

SMACNA—2003	Fire, Smoke and Radiation Damper Installation Guide for HVAC Systems							419.2.1.3, 420.2.3, 421.2.1.3,

- Metal Roof and Wall Systems . . .RAS 133-9.2

UL

Underwriters Laboratories

333 Pfingsten Road

Northbrook, IL 60062-2096

Standard reference number	Title			Referenced in section number

Add to read as shown.

181—96		Standard for Factory-Made Air Ducts and Air Connectors	419.3.11.6

Add to read as shown.

RCSC

Research Council on Structural Connections

c/o Stanley D. Lindsey & Assoc. Ltd.

2244 Metro Center Blvd., Suite 208

Nashville, TN 37228-1320

Standard reference number	Title		Referenced in section number

RCSC—88	Specification for Structural Joints Using ASTM A 325 or A 490 Bolts		2214.3

RMI

Rack Manufacturers Institute

8720 Red Oak Boulevard, Suite 201

Charlotte, NC 28217

Standard reference number	Title			Referenced in section number

Change to read as shown.

10100	Manual of Safety Practices - A Code of Practices for the Use of Industrial and Commercial Steel Storage Racks			2214.3

10150	Industrial Steel Storage Racks Manual				2214.3

10083	Specification for the Design, Testing and Utilization of Industrial Steel Storage Racks		2208.1

SDI

Steel Deck Institute

PO Box 25

Fox River Grove, IL 60021

Standard reference number	Title		Referenced in section number

DDP		Deck Damage and Penetrations				2214.3

DDM—023	Diaphragm Design Manual			2214.3, 2222.4

Number 30 31	Design Manual For Composite Decks, Form Decks and Roof Decks			2214.3

MOC1 2		Manual of Construction with Steel Deck			2214.3

SPD2		Standard Practice Details					2214.3

SDI-C-2011 Standard for Composite Steel Floor Deck Slabs

(Mod R4944 / AS)

SJI

Steel Joist Institute

3127 10th Avenue, North

Myrtle Beach, SC 29577-6760

Standard reference number	Title		Referenced in section number

Add to read as shown.

SJI—71	Structural Design of Steel Joist Roofs to Resist Ponding Loads, Technical Digest No. 3		2214.3

SJI—88	Vibration of Steel Joist-Concrete Slab Floors, Technical Digest No. 5				2214.3

SJI—03	Structural Design of Steel Joist Roofs to Resist Uplift Loads, Technical Digest No. 6		2214.3

SJI—83	Welding of Open Web Steel, Technical Digest No. 8			2214.3

SJI—87	Handling and Erection of Steel Joists and Joist Girders, Technical Digest No. 9			2214.3

SJI—02	Standard Specifications, Load Tables and Weight Tables for Steel Joists and Joist Girders							1604.3.3, 2206, 2214.3

SJI—03	75-Year Steel Joist Manual					2214.3

Add to read as shown.

SMA

Storage Equipment Manufacturers Association

8720 Red Oak Blvd, Suite 201

Charlotte, NC 28217

Standard reference number	Title		Referenced in section number

ANSI/SMA MH281—97	Specification of Industrial Grade Steel Shelving	2214.3

Add to read as shown.

SSPC

The Society for Protective Coatings

40 24th Street, 6th Floor

Pittsburgh PA 15222-4656

Standard reference number	Title		Referenced in section number

SSPC - Paint 15	Steel Joist Shop Paint					2214.3

SSPC/AISC	Guide to the Shop Painting of Structural Steel		2214.3

STI

Steel Tube Institute

522 Westgate Tower

Cleveland, OH 44116

Standard reference number	Title		Referenced in section number

STI	Manual of Cold-Formed Welded Structural Steel Tube		2214.3

TECO

Timber Company, Inc.

2402 Daniels Street

Madison, WI 53704

Standard reference number	Title			Referenced in section number

TECO PRP-133	Performance Standards and Policies for Structural Use Panels	2314.4.8, 2315.1.2

1256—02            Fire Test of Roof Deck Construction—with Revisions through March 2000

1508.1, 2603.3, 2603.4.1.5, 2612.3.2.5.2

Add to read as shown.

2017-08 Standard for General-Purpose Signaling Devices and Systems – with Revisions through October 13, 2009        424.2.17.1.9

Change to read as shown.

Underwriters Laboratories Inc. (UL),

333 Pfingsten Road, Northbrook,

IL 60062-2096.

UL 1069, 7th edition…..420.3.25

Chapter 36 Florida Fire Prevention Code.  Add to read as shown.

Chapter 36 Florida Fire Prevention Code

3601.1 Scope.  Add to read as shown.

3601.1 Scope.  Provisions of this chapter shall govern the design, construction and arrangement of elements to provide a safe means of egress from buildings and structures and to minimize hazard to life and property due to fire and panic.

3601.2 Add to read as shown.

3601.2  In addition to the provisions of this code, buildings shall comply with the 2013 Florida Fire Prevention Code as adopted by the Florida State Fire Marshal.

Appendix B Board of Appeals.  Change to read as shown.

APPENDIX B

CHAPTER 9B-52 F.A.C.

FLORIDA STANDARD FOR PASSIVE RADON-RESISTANT CONSTRUCTION

See Appendix B of the 2010 FBC, Building

Appendix C Group U – Agricultural Buildings.  Change to read as shown.

APPENDIX C

CHAPTER 9B-53 F.A.C STANDARD FOR MITIGATION OF RADON IN EXISTING BUILDINGS

See Appendix C of the 2010 FBC, Building

APPENDIX E

Chapter 9 B-67 FLORIDA STANDARD FOR RADON-RESISTANT NEW COMMERCIAL CONSTRUCTION

See Appendix E of the 2010 FBC, Building