Florida Supplement to the 2012 IMC

PRE-GLITCH CORRECTION VERSION

Note 1:  Throughout the document, change International Building Code to Florida Building Code, Building; change the ICC Electrical Code to Chapter 27 of the Florida Building Code, Building; change the International Energy Conservation Code to the Florida Building Code, Energy Conservation; change the International Existing Building Code to Florida Building Code, Existing Building; change the International Fire code to Florida Fire Prevention Code; change International Fuel Gas Code to Florida Building Code, Fuel Gas; change the International Mechanical Code to Florida Building Code, Mechanical; change the International Plumbing Code to Florida Building Code, Plumbing; change the International Residential Code to Florida Building Code, Residential.

Note 2:  Criteria blocked in yellow indicate Florida specific language from the 2010 FBC.

Chapter 1, Administration

Section 101 General

101.1 Scope. Change to read as shown.

[A] 101.1 Title. These regulations shall be known as the Mechanical Code of [NAME OF JURISDICTION], hereinafter referred to as "this code.”  Scope. The provisions of Chapter 1, Florida Building Code, Building shall govern the administration and enforcement of the Florida Building Code, Mechanical.

101.2 Scope. Change to read as shown.

101.2 Scope. Reserved.

101.3 Intent. Change to read as shown.

101.3 Intent. Reserved.

101.4    Severability. Change to read as shown.

101.4 Severability. Reserved.

Section 102 Applicability. Change to read as shown.

Section 102 Applicability. Reserved.

Section 103, Department of Mechanical Inspection. Change to read as shown.

Section 103, Department of Mechanical Inspection. Reserved.

Section 104, Duties and Powers of the Code Official. Change to read as shown.

Section 104, Duties and Powers of the Code Official. Reserved.

Section 105, Approval. Change to read as shown.

Section 105, Approval. Reserved.

Section 106, Permits. Change to read as shown.

Section 106, Permits. Reserved.

Section 107, Inspections and Testing. Change to read as shown.

Section 107, Inspections and Testing.  Reserved.

Section 108, Violations. Change to read as shown.

Section 108, Violations. Reserved.

Section 109, Means of Appeal. Change to read as shown.

Section 109, Means of Appeal. Reserved.

Section 110, Temporary Equipment, Systems and Uses. Change to read as shown:

Section 110. Temporary Equipment, Systems and Uses. Reserved.

(M5201 AS)

Chapter 2, Definitions

SECTION 202

GENERAL DEFINITIONS

Section 202 General definitions. Change definitions specified to read as follows:

BOILER, HOT WATER SUPPLY. Any vessel used for generating hot water to be used external to the vessel, which exceeds any of the following limitations:

1. A heat input capacity of 400,000 Btuh (117.2 kW).

2. A water temperature of 210ºF (99ºC).

3. A nominal water capacity of 120 gal (454 L).

(M5645 AM- A1)

DESIGN FLOOD ELEVATION. The elevation of the “design flood,” including wave height, relative to the datum specified on the community’s legally designated flood hazard map. In areas designated as Zone AO, the design flood elevation shall be the elevation of the highest existing grade of the building’s perimeter plus the depth number (in feet) specified on the flood hazard map. In areas designated as Zone AO where a depth number is not specified on the map, the depth number shall be taken as being equal to 2 feet (610 mm).

(SP5283 AS)

Chapter 3, General Regulations

SECTION 301

GENERAL

Section 301.16.1 High-velocity wave action. Change to read as follows:

301.16.1 High-velocity wave action Coastal high hazard areas and coastal A zones. In flood hazard areas subject to high-velocity wave action coastal high hazard areas and coastal A zones mechanical systems and equipment shall not be mounted on or penetrate walls intended to break away under flood loads.   (SP5682 AM)(SP5679 AS)

SECTION 307

CONDENSATE DISPOSAL

Section 307.2.5. Add to read as follows:

307.2.5 Pipe insulation. All horizontal primary condensate drains within unconditioned areas shall be insulated to prevent condensation from forming on the exterior of the drain pipe.

(M5756 AS)

Chapter 5, Exhaust Systems

Section 515. Add section to read as follows:

SECTION 515

MAUSOLEUM RELIEF VENT

515.1 General. A pressure relief vent shall be provided for each crypt. Niches shall not require pressure relief systems.

515.2 Materials. The pressure relief vent pipe and fittings shall conform to one of the standards listed in Table M515.2A and Table M515.2B.

TABLE 515.2A

CRYPT PRESSURE RELIEF PIPE

MATERIAL                                     					STANDARD

Acrylonitrile butadiene styrene (ABS) plastic pipe		ASTM D 2661

ASTM F 628 CSA B181.1

Polylefin pipe	                   		                             	CSA CAN/CSA - B181.3

Polyvinyl chloride (PVC) plastic pipe  (Type DWV)	            ASTM D 2665

ASTM D 2949, ASTM F 891

Table 515.2B

CRYPT PRESSURE RELIEF FITTINGS

MATERIAL			                              	              	STANDARD

Acrylonitrile butadiene styrene (ABS) plastic pipe   		              ASTM D 3311,  CSA B181.1

Polyvinyl chloride (PVC) plastic pipe (Type DWV)     ASTM D 3311, ASTM D 2949, ASTM F 891

Plastic, general			                                                   ASTM F 409

515.3 Pressure Relief Vent.  For family mausoleum units where all crypts are bordering an exterior wall, pressure relief ventilation shall be provided from the crypt to the outside of the mausoleum through the exterior wall or roof. For all other mausoleum units, each crypt shall have a pressure relief vent from the crypt to the roof of the mausoleum. The minimum nominal pipe size shall be 1 inch (25 mm). The system shall have a minimum of one-eighth unit vertical to 12 units horizontal (1-percent slope). The piping shall not be trapped or installed to trap water or condensate.

515.4 Termination.  Except for family mausoleum units where all crypts are bordering an exterior wall, crypt pressure relief system shall extend through the roof and terminate at least 6 inches (152 mm) above the roof and at least 10 feet (3048 mm) from any openable opening, air intake, or property line. The termination of the relief system pipe shall be done by a roof and vent cap compatible with the relief pressure pipe. The roof and vent cap shall be waterproof.  For family mausoleum units where all crypts are bordering an exterior wall, pressure relief ventilation shall be provided from the crypt to the outside of the mausoleum through the exterior wall or roof.

(SP5223 AS)

Section 516. Add a section to read as follows:

SECTION 516

CARBON MONOXIDE CONTROL SYSTEMS

516.1 Carbon monoxide control systems. See Section 908.7 916 of the Florida Building Code, Building.

(M5228 AM)

Chapter 6, Duct Systems

Section 601 General. Add Section 601.5 to read as follows:

601.5 Balanced Return Air. Restricted return air occurs in buildings when returns are located in central zones and closed interior doors impede air flow to the return grill or when ceiling spaces are used as return plenums and fire walls restrict air movement from one portion of the return plenum to another. Provisions shall be made in both residential and commercial buildings to avoid unbalanced air flows and pressure differentials caused by restricted return air. Pressure differentials across closed doors where returns are centrally located shall be limited to 0.01 inch WC (2.5 pascals) or less. Pressure differentials across fire walls in ceiling space plenums shall be limited to 0.01 inch WC (2.5 pascals) by providing air duct pathways or air transfer pathways from the high pressure zone to the low zone.

Exceptions:

1.      Transfer ducts may achieve this by increasing the return transfer 1½ times the cross sectional area (square inches) of the supply duct entering the room or space it's serving and the door having at least an unrestricted 1 inch undercut to achieve proper return air balance.

2.      Transfer grilles shall use 50 square inches (of grille area) to 100 cfm (of supply air) for sizing through-the-wall transfer grilles and using an unrestricted 1 inch undercutting of doors to achieve proper return air balance.

3.      Habitable rooms only shall be required to meet these requirements for proper balanced return air excluding bathrooms, closets, storage rooms and laundry rooms, except that all supply air into the master suite shall be included.

(M5772 AM)

SECTION 603

DUCT CONSTRUCTION AND INSTALLATION

Section 603.1.1. Add section to read as follows:

603.1.1 Space provided. Sufficient space shall be provided adjacent to all mechanical components located in or forming a part of the air distribution system to assure adequate access for (1) construction and sealing in accordance with the requirements of Section 603.1 of this code; (2) inspection; and (3) cleaning and maintenance. A minimum of 4 inches (102 mm) is considered sufficient space around air handling units.

Exception: Retrofit or replacement units not part of a renovation are exempt from the minimum clearance requirement

(M5776 AS)

Chapter 15, Referenced Standards

Change to make Florida-specific references as follows:

ASTM

Standard										Referenced in

Reference 										code section

Number		Title									number

D 2661—01 Acrylonitrile-Butadiene-Styrene (ABS) Schedule 40 Plastic Drain, Waste, and Vent

Pipe and Fittings…………………………………………………………………………Table 515.2A

D2665—01  Poly (Vinyl Chloride) (PVC) Plastic Drain, Waste, and Vent Pipe and Fittings…………Table 515.2A

D 2949—97  3.25-in. Outside Diameter Poly (Vinyl Chloride) (PVC) Plastic Drain, Waste,

and Vent Pipe and Fittings………………………………………………………Table 515.2A, 515.2B

D 3311—94  Drain, Waste, and Vent (DWV) Plastic Pipe Fittings Patterns………………………….. Table 515.2B

F 409—02     Thermoplastic Accessible and Replaceable Plastic Tube and Tubular Fittings	    Table 515.2B

F 628—01     Acrylonitrile-Butadiene-Styrene (ABS) Schedule 40 Plastic Drain, Waste, and Vent

Pipe with Cellular Core…………………………………………………………………………………..Table 515.2A

F 891—00 Coextruded Poly (Vinyl Chloride) (PVC) Plastic Pipe with Cellular Core…..Table 515.2A, Table 515.2B

CSA

Standard										 Referenced in

Reference 										 code section

Number		        Title								  number

CAN/CSA B 181.1—99 ABS Drain, Waste, and Vent Pipe and Pipe Fittings………………..Tables 515.2A, 515.2B

CAN/CSA B 181.3—99 Polyolefin Laboratory Drainage Systems with revisions through

October 1990………………………………………………………………………Table 515.2A

Florida Codes Florida Building Commission

c/o Florida Department of Business and Professional Regulation

Building Codes and Standards

1940 North Monroe Street

Tallahassee, Florida 32399-0722.

Standard                                                                                                                                          Referenced in code

reference number    Title                                                                                                                 section number

2013 Florida Building Code, Building                      	101.1, 201.3, 202, 301.12, 301.12, 301.14, 301.15, 302.1, 302.2,               304.7, 304.10, 308.8, 308.10, 401.4, 401.6, 406.1, 502.10, 502.10.1,

504.2, 506.3.3, 506.3.10, 506.3.12.2, 506.4.1, 509.1,

510.6, 510.6.3, 510.6.2, 510.7, 511.1.5, 513.1,

513.2, 513.3, 513.4.3, 513.5, 513.5.2, 513.5.2.1,

513.6.2, 513.10.5, 513.12, 513.12.2, 513.20,

602.2.1.5.1, 602.2.1.5.2, 602.3, 603.1, 603.10,

604.5.4, 607.1.1, 607.3.2.1, 607.5.1, 607.5.2,

607.5.3, 607.5.4, 607.5.4.1, 607.5.5, 607.5.5.1,

607.6, 607.6.2, 701.4.1, 701.4.2, 801.3, 801.16.1,

801.18.4, 902.1, 908.3, 908.4, 910.3, 925.1,

1004.6, 1105.1, 1206.4, 1402.4, 1402.4.1

2013 Florida Building Code, Energy Conservation                  202, 301.2, 303.3, 312.1, 603.9, 604.1, 1204.1, 1204.2

2013 Florida Building Code, Fuel Gas                                     101.2, 201.3, 301.3, 701.1, 801.1, 901.1, 906.1, 1101.5

2013 Florida Building Code, Plumbing		              201.3, 301.8, 512.2, 908.5, 1002.1, 1002.2, 1002.3,                                   1005.2, 1006.6, 1008.2, 1009.3, 1101.4, 1201.1, 1206.2, 1206.3, 1401.2

2013 Florida Fire Prevention Code                    	201.3, 310.1, 311.1, 502.4, 502.5, 502.7.2, 502.8.1, 502.9.5, 502.9.5.2,

502.9.5.3, 502.9.8.2, 502.9.8.3, 502.9.8.5, 502.9.8.6, 502.10,

502.10.3, 502.16.2, 509.1, 510.2.1, 510.2.2, 510.4,

511.1.1 513.12.3, 513.15, 513.16, 513.17, 513.18, 513.19,

513.20.2, 513.20.3, 606.2.1, 908.7, 1101.9,

1105.3, 1105.9, 1106.5, 1106.6, 1301.1, 1301.2

Delete all references to ICC codes in their entirety.

ICC