| PLUMBING Local Technical Amendments to the 2014 5th Edition Florida Building Code |  |  |  |
| --- | --- | --- | --- |
| JURISDICTION | DOCUMENT with TECHNICAL AMENDMENT | TEXT OF TECHNICAL AMENDMENT | TAC REVEW |
| Broward County | Florida Building Code, Plumbing Ch. 3 – General Regulations | Florida Building Code – Plumbing , 5th Edition (2014) Amendment to Section [M] 314.2.1 [M] 314.2.1 Condensate drainage collection, use or disposal. Condensate from all cooling coils and evaporators of equipment served by an onsite cooling tower in a building or structure wherein the aggregate cooling capacity of the equipment exceeds 65,000 Btu/hr shall be collected and conveyed from the drain pan outlet and discharged to the cooling tower. Where an on-site cooling tower is not installed the condensate from all cooling coils and evaporators shall be conveyed from the drain pan outlet to an approved place of disposal. Such piping shall maintain a minimum horizontal slope in the direction of discharge of not less than one-eighth unit vertical in 12 units horizontal (1-percent slope). Condensate shall not discharge into a street, alley or other areas so as to cause nuisance Exceptions: 1. Condensate from cooling coils and evaporators is not required to be collected and conveyed to an on-site cooling tower; provided 1.1 through 1.3 are met: 1.1 The equipment comprises 10% or less of the total capacity of the cooling tower system 1.2 The equipment is located in an isolated or remote area - The size of the equipment is 65,000 Btu/hr or less - In existing buildings condensate may be collected and conveyed to a cooling tower or discharged to an approved place of disposal. | Plumbing TAC Vote: (0Yes-7No NAR) |
| Broward County | Florida Building Code, Plumbing – Ch. 6 – Water Supply and Distribution | Amendment to Section 604.3 and Table 604.4 Florida Building Code – Plumbing, 5th Edition (2014) Amendment to Section 604.3 and Table 604.4 Table 604.4 MAXIMUM FLOW RATES AND CONSUMPTION FOR PLUMBING FIXUTRES, AND FIXTURE FITTINGS AND APPLIANCES PLUMBING FIXTURE OR FIXTURE FITTING; MAXIMUM FLOW RATE OR QUANTITY b. Lavatory, private; 2.2 1.5 gpm at 60 psi. Lavatory, public, (metering); 0.25 gallon per metering cycle. Lavatory, public (other than metering); 0.5 gpm at 60 psi. Shower head a; 2.0 2.5 gpm at 80 psi. Sink faucet; 2.2 gpm at 60 psi. Urinal; 1.0 0.5 gallon per flushing. Water closet; 1.6 1.28 gallons per flushing cycle. Dishwasher (Residential )*; 6.5 gallons per cycle or less (Energy Star/WaterSense Certified). Dishwasher (Commercial); Less than1.2 gallons per rack for fill and dump machines and less than 0.9 gallons per rack for low temperature machines. Dishwasher(Under the counter machines commercial); 1.0 gallons per rack for high temperature machines and 1.7 gallons per rack for low temperature machines. Washing Machine *; Water factor of 8 or lower (Energy Star/WaterSense Certified) (c). For SI: 1 gallon = 3.785 L, 1 gallon per minute = 3.785 L/m, 1 pound per square inch = 6.895 kPa. a. A hand‐held shower spray is a shower head. *If installed b. Consumption tolerance shall be determined from referenced standards. c. Water factor in gallons per cycle per cubic foot Section #: 604 - Design of Building Water Distribution System, Table 604.4 ______________________ Please see attachment. THIS PROPOSED MODIFICATION SHALL BE EFFECTIVE JUNE 30, 2015. BROWARD BORA PUBLIC HEARING AND VOTE, 2015. AMENDMENT EFFECTIVE DATE JUNE 30, 2015. SECTION 603 WATER SERVICE 603.1 Size of water service pipe. The water service pipe shall be sized to supply water to the structure in the quantities and at the pressures required in this code. The water service pipe shall be not less than ¾ inch (19.1mm) in diameter. 603.2 Separation of water service and building sewer. Water service pipe and the building sewer shall be separated by not less than 5 feet (1524 mm) of undisturbed or compacted earth. Exceptions: - The required separation distance shall not apply where the bottom of the water service pipe within 5 feet (1524 mm) of the sewer is not less than 12 inches (305mm) above the top of the highest point of the sewer and the pipe materials conform to Table 702.3 - Water service pipe is permitted to be located in the same trench with a building sewer, provided such sewer is constructed of materials listed in Table 702.2 - The required separation distance shall not apply where a water service pipe crosses a sewer pipe centerline on both sides of such crossing with pipe materials listed in Table 605.3, 702.2 or 702.3. 603.2.1 Water service near sources of pollution. Potable water service pipes shall not be located in, under or above cesspools, septic tank, drainage fields or seepage pits (see Section 605.1 for soil and groundwater conditions). SECTION 604 DESIGN OF BUILDING WATER DISTRIBUTION SYSTEM 604.1 General. The design of the water distribution system shall conform to accepted engineering practice. Methods utilized to determine pipe sizes shall be approved. 604.2 System Interconnection. At the points of interconnection between the hot and cold water supply piping systems and the individual fixtures, appliances or devices, provisions shall be made to prevent flow between such piping systems. 604.3 Water distribution system design criteria. The water distribution system shall be designed, and pipe sizes shall be selected such that under conditions of peak demand, the capacities at the fixture supply pipe outlets shall not be less than shown in Table 604.3. The minimum flow rate and flow pressure provided to fixtures and appliances not listed in Table 604.3 shall be in accordance with the manufacturer’s instructions. Table 604.3 WATER DISTRIBUTION SYSTEM DESIGN CRITERIA REQUIRED CAPACITY AT FIXTURE SYPPLY PIPE OUTLETS FIXTURE SUPPLY OUTLET SERVING; FLOW RATE* (gpm); FLOW PRESSURE (psi). Bathtub, balanced-pressure, thermo-static or combination balanced pressure/thermo-static mixing valve; 4; 20. Bidet, thermostatic mixing valve; 2; 20. Combination fixture; 4; 8. Dishwasher, residential; 2.75; 8. Drinking fountain; 0.75; 8. Laundry tray; 4; 8. Lavatory; 2; 8. Shower; 3; 8. Shower, balanced-pressure, thermo-static or combination balanced-pressure/thermo-static mixing valve; 3; 20. Sillcock, hose bibb; 5; 8. Sink, residential; 2.5; 8. Sink, service; 3; 8. Urinal, valve; 12; 25. Water closet, blowout, flushometer valve; 25; 45. Water closet, flushometer tank; 1.6; 20. Water closet, siphonic, flushometer valve; 25; 35. Water closet, tank, close coupled; 3; 20. Water closet, tank, one piece; 6; 20. For SI: 1 pound per square inch = 6.895 kPs 1 gallon per minute = 3.785 L/m - For additional requirements for flow rates and quantities, see Section 604.4 604.4 Maximum flow and water consumption. The maximum water consumption flow rates and quantities for all plumbing fixtures and fixture fittings shall be in accordance with Table 604.4 Exceptions: - Blowout design water closets having a water consumption not greater than 3 ½ gallons (13L) per flushing cycle. - Vegetable sprays. - Clinical sinks having a water consumption not greater than 4 ½ gallons (17.1 L) per flushing cycle. - Service sinks. - Emergency showers - All fixtures, fittings and appliances with U.S. Environmental Agency WaterSense ® (EPA) label. TABLE 604.4 MAXIMUM RATES AND CONSUJPTION FOR PLUMBING FIXTURES, AND FIXTURE FITTINGS AND APPLIANCES PLUMBING FIXTURE OR FIXTURE FITTING; MAXIMUM FLOW RATE OR QUANTITY b. Lavatory, private; 2.2 1.5 gpm at 60 psi. Lavatory, public, (metering); 0.25 gallon per metering cycle. Lavatory, public, (other than metering); .5 gpm at 60 psi. Shower head *; 2.0 2.5 gpm at 80psi. Sink faucet; 2.2 gpm at 60 psi. Urinal; 1.0 0.5 gallons per flushing. Water closet; 1.6 1.28 gallons per flushing cycle. Dishwasher (Residential) *; 6.5 gallons per cycle or less (Energy Star/WaterSense Certified). Dishwasher (Commercial); Less than 1.2 gallons per rack for fill and dump machines and less than 0.9 gallons per rack for low temperature machines.. Dishwasher (Under the counter machines commercial); 1.0 gallons per rack for high temperature machines and 1.7 gallons per rack for low temperature machines.. Washing Machine *; Water factor of 8 or lower- (Energy Star/WaterSense Certified). For Si: 1 gallon = 3.785L, 1 gallon per minute = 3.785 L/m, 1 pound per square inch = 6.895 kPa. - A hand-held shower spray is a shower head *if installed - Consumption tolerance shall be determined from referenced standards - Water factor in gallons per cycle per cubic foot 604.5 Size of Fixture supply. The minimum size of a fixture supply pipe shall be as shown in Table 604.5. The fixture supply pipe shall terminate not more than 30 inches (762 mm) from the point of connection to the fixture. A reduced-size flexible water connector installed between the supply pipe and the fixture shall be of an approved type. The supply pipe shall extend to the floor or wall adjacent to the fixture. The minimum size of individual distribution lines utilized in gridded or parallel water distribution systems shall be as shown in Table 604.5. 604.6 Variable street pressures. Where street water main pressures fluctuate, the building water distribution system shall be designed for the minimum pressure available. 604.7 Inadequate water pressure. Where water pressure from the street main or other source of supply is insufficient to provide flow pressures at fixture outlets as required under Table 604.3, a water pressure booster system conforming to Section 606.5 shall be installed on the building water supply system. 604.8 Water pressure reducing valve or regulator. Where water pressure within a building exceeds 80 psi (552 kPa) static, an approved water-pressure reducing valve conforming to ASSE 1003 or CSA B356 with strainer shall be installed to reduce the pressure in the building water distribution piping to not greater than 80 psi (552 kPa) static. Exception: Service lines to sill cocks and outside hydrants, and main supply risers where pressure from the mains is reduced to 80 psi (552 kPa) or less at individual fixtures. 604.8.1 Valve design. The pressure-reducing valve shall be designed to remain open to permit uninterrupted water flow in case of valve failure. 604.8.2 Repair and removal. Water-pressure reducing valves, regulators and strainers shall be so constructed and installed as to permit repair or removal of parts without breaking a pipeline or removing the valve and strainer from the pipeline. TABLE 604.5 MINIMUM SIZES OF FIXTURE WATER SUPPLY PIPES FIXTURE; MINIMUM PIPE SIZE (INCH). Bathtubs (60” x 32” and smaller); 1/2. Bathtubs (larger than 60” x 32”); 1/2. Bidet; 3/8. Combination sink and tray; 1/2. Dishwasher, domestic; 1/8. Drinking fountain; 3/8. Hose bibbs; 1/2. Kitchen sink; 1/2. Laundry, 1,2 or 3 compartments; 1/2. Lavatory; 3/8. Shower, single head; 1/2. Sinks, flushing rim; 3/4. Sinks, service; 1/2. Urinal, flush tank; 1/2. Urinal, flushometer valve; 3/4. Wall hydrant; 1/2. Water closet, flush tank; 3/8. Water closet, flushometer valve; 1. Water closet, flushometer tank; 3/8. Water closet, one piece; 1/2. For SI: 1 inch = 25.4 mm, 1 foot = 304.8 mm. - pound per square inch = 6.895 kPa. - Where the developed length of the distribution line is 60 feet or less and The available pressure at the meter is 35 psi or greater, the minimum size of Individual distribution line supplied from a manifold and installed as part of Parallel water distribution system shall be one nominal tube size smaller than the sizes indicated. 604.9 Water hammer. The flow velocity of the water distribution system shall be controlled to reduce the possibility of water hammer. A water-hammer arrestor shall be installed where quick-closing valves are utilized. Water-hammer arrestors shall be installed in accordance with the manufacturer’s instructions. Water-hammer arrestors shall conform to ASSE 1010. 604.10 Gridded and parallel water distribution system manifolds. Hot water and cold water manifolds installed with gridded or parallel connected individual distribution lines to each fixture or fixture fitting shall be designed in accordance with Sections 604.10.1 through 604.10.3. 604.10.1 Manifold sizing. Hot water and cold water manifolds shall be sized in accordance with Table 604.10.1. The total gallons per minute is the demand of all outlets supplied. | Plumbing TAC Vote: (0Yes-7No NAR) |
| Broward County | Florida Building Code, Plumbing | (Due to formatting, please review amendment by clicking on this link) Plumbing 604.3 and Table 604.4 https://floridabuilding.org/Upload/FBC/CodeID_7187_92a2_Broward%20County-Local-Amend-FBC%205th%20ED-2014-Plumbing-%20Sec604%203-604%204-2015-06-04.pdf | Plumbing TAC (0Yes-7No NAR) |
| Broward County | Florida Building Code, Plumbing – Appendix F | Appendix F - Florida Building Code – Plumbing – APPENDIX F , 5th Edition (2014) Amendment to APPENDIX F c. Sprinkler layout. Sprinkler layout may be modified to adjust for field conditions provided it complies with part VI, Section B, subsection 1 Sprinkler layout and spacing. Prior to final inspection, the contractor shall submit a letter or as-built drawing that reflects the modification to the authority with jurisdiction. PART IV: MATERIALS - PVC Pipe and fittings 3. Threaded PVC pipe firings fittings shall meet the requirements of Schedule 40 as set forth in ASTM D 2464 PART V: INSTALLATION A. Pipe Installation 4. Thrust blocks, or other approved method must be used on all gasketed PVC systems. They must be formed against a solid, hand-excavated trench wall undamaged by mechanical equipment. They shall be constructed of concrete, and the space between the pipe and trench shall be filled to the height of the outside diameter of the pipe. Size thrustblocks in accordance with ASAE S-376.1 5. The trench bottom must be uniform, free os of debris, and sufficient width to properly place pipe and support it over its entire length. Native excavated material may be used to backfill the pipe trench. However, the initial backfill material to 6”above the top of the pipe shall be free from rocks or stones larger than 1-inch in diameter. The final backfill material shall be free of rock or debris that is greater than 3” in diameter. At the time of placement , the moisture content of the material shall be such that the required degree of compaction can be obtained with the backfill method to be used. Blocking or mounding shall not be used to bring the pipe to final grade. 6. Pipe Sleeves must be used to protect pipes or wires installed under pavement or roadways or when position of irrigation pipes or wires conflict with pipes or appurtenances of other trades. Use pipe sleeves two pipe sizes larger than the carrier pipe or twice the diameter of the wire bundle to be placed under the paving or roadway and extending a minimum of 3 feet beyond the paved area or as required by the Florida Department of Transportation (FDOT).Use sleeve pipe with wall thickness at least equal to the thickness of schedule 40 or PR 160 pipe, whichever is thicker. Proper backfill and compaction procedures should be followed. PART VI: TESTING & INSPECTIONS C. Final Inspection. 3. Open Trench Inspection: The trench at all joints and every transition in pipe size, will be open where open trench inspection is required | Plumbing TAC (0Yes-7No NAR) |
| City of Miami-Dade | Florida Building Code, Plumbing | Sec. 8-31. - Local technical amendments to Florida Building Code. (A) The County hereby adopts the following local technical amendments to Chapter 6 (Plumbing) of the Florida Building Code. 604.4 Maximum flow and water consumption. The maximum water consumption flow rates and quantities for all plumbing fixtures, fixture fittings and appliances shall be in accordance with Table 604.4. Effective January 1, 2009, permit applications for new residential and commercial structures shall include high efficiency plumbing fixtures, fixture fittings and appliances as provided in Table 604.4. Such high efficiency plumbing fixtures, fixture fittings and appliances shall comply with the specifications in Table 604.4 or have received the U.S. Environmental Protection Agency (EPA) WaterSense Label. Exceptions: 1. Blowout design water closets [3.5 gallons (13L) per flushing cycle]. 2. Vegetable sprays. 3. Clinical sinks [4.5 gallons (17 L) per flushing cycle]. 4. Service sinks. 5. Emergency showers. _____ TABLE 604.4 MAXIMUM FLOW RATES AND CONSUMPTION FOR PLUMBING FIXTURES, FIXTURE FITTINGS AND APPLIANCES PLUMBING FIXTURE OR FIXTURE FITTING; MAXIMUM FLOW RATE (b). Lavatory, private; 1.5 gpm at 60 psi. Lavatory, public, (metering); 0.25 gallon per metering cycle. Shower head (a); 1.5 gpm at 60 psi. Sink faucet; 1.5 gpm at 60 psi. Urinal; >>Waterless or 0.5 gallon flushing cycle. Water Closet; 1.28 gallons per flushing cycle. Dishwasher (residential); 6.5 gallons per cycle or less (Energy Star/Water Sense Certified) ©. Dishwasher (commercial); Less than 1.2 gallons per rack for fill and dump machines and less Than 0.9 gallons per rack for all other types of machines.. Dishwasher (under the counter machines); 1.0 gallon or less per rack for high-temperature machines and 1.7 gallons per rack for low-temperature machines. Washing machine; Water factor of 8 or lower (Energy Star / Water Sense Certified) ©. For SI: 1 gallon = 3.785 L 1 gallon per minute = 3.785 L/m 1 pound per square inch = 6.895 kPa. (a) A hand-held shower spray is a shower head. (b) Consumption tolerances shall be determined from referenced standards. (c) Water factor in gallons per cycle per cubic foot. _____ (B) The County hereby adopts the following local technical amendments to Chapter 29 (Residential) of the Florida Building Code. P2903.2 Maximum flow and water consumption. The maximum water consumption flow rates and quantities for all plumbing fixtures, fixture, fittings and appliances shall be in accordance with Table P2903.2a. Effective January 1, 2009, permit applications for new residential structures shall include high efficiency plumbing fixtures, fixture fittings and appliances as provided in Table P2903.2a. Such high efficiency plumbing fixtures, fixture fittings and appliances shall comply with the specifications in Table P2903.2a or have received the U.S. Environmental Protection Agency (EPA) WaterSense Label. _____ TABLE P2903.2a MAXIMUM FLOW RATES AND CONSUMPTION FOR PLUMBING FIXTURES, FIXTURE FITTINGS AND APPLIANCES PLUMBING FIXTURE OR FIXTURE FITTING; PLUMBING FIXTURE OR FIXTURE FITTING MAXIMUM FLOW RATE (B). Lavatory faucet; 1.5 gpm at 60 psi. Shower head (a); 1.5 gpm at 80 psi. Sink faucet; 1.5 gpm at 60 psi. Water closet; 1.28 gallons per flushing cycle. Dishwasher (residential); 6.5 gallons per cycle or less (Energy Star/Water Sense Certified) ©. Washing Machine; Water factor of 8 or lower (Energy Star / Water Sense Certified) ©. For SI: 1 gallon = 3.785 L 1 gallon per minute = 3.785 L/m 1 pound per square inch = 6.895kPa (a) A handheld shower spray is a showerhead. (b) Consumption tolerances shall be determined from referenced standards. (c) Water factor in gallons per cycle per cubic foot | Plumbing TAC (0Yes-7No NAR) |
| Pinellas County Construction Licensing Board (PCCLB) | Florida Building Code, Residential | P2903.2b Minimum Water Service Size AMEND FOOTNOTES: TABLE P2903.2b MINIMUM WATER SERVICE SIZEa NO. OF FIXTURE UNITS FLUSH TANK WCb; DIAMETER OF WATER PIPEC; RECOMMENDED METER SIZE (inches)d; APPROX. PRESSURE LOSS METER + 100’ PIPE (psi)e; NO. OF FIXTURE UNITS FLUSH VALVE WCb. 18; ¾; 5/8; 30; =. 19-55 =; 1 1; 1 1; 30 30; = 9. 56-85 =; 1 ¼ 1 ¼; 1 1; 30 30; = 10-20. 8-225 =; 1 ½ 1 ½; 1 ½ 1 ½; 30 30; = 21-77. 226-350 =; 2 2; 1 ½ 1 ½; 30 30; = 78-175. 351-550 =; 2 2; 2 2; 30 30; = 176-315. 551-640 =; 2 ½ 2 ½; 2 2; 30 30; = 316-392. 641-1340 =; 3 3; 3 3; 22 22; = 393-940. AMEND FOOTNOTES: - Table is applicable for both copper and plastic water piping. - See Table P2903.6 for fixture unit values. c. Minimum water service shall be 3/4" to control valve. d. All secondary submeters and backflow assemblies shall be at least the same size as the line in which they are installed. e. Table based on minimum water main pressure of 50 psi. f. Minimum sizes for fixtu re supply pipe from the main or from the riser shall be from the Florida Building Code 5h Edition (2014) - Plumbinq Section 604.5. g. Four (4) fixtures maximum (hot or cold) mav connect to a one-half inch fixture water supply or as required bv manufacturers' installation instructions. h. Where the water main pressure falls below 50 p.s.i. the next larger pipe size shall be used. i. Buildings above three (3) stories in height shall use the next larger pipe size. | Plumbing TAC (0Yes-7No NAR) |
| Pinellas County Construction Licensing Board (PCCLB) | Florida Building Code, Plumbing | AMEND EXISTING SECTION 605.22.2 Solvent cementing. Joint surfaces shall be clean and free from moisture. A purple primer that conforms to ASTM F 656 shall be applied. Solvent cement not purple in color and conforming to ASTM D 2564 or CSA-8137.3 shall be applied to all joint surfaces. The joint shall be made while the cement is wet and shall be in accordance with ASTM D 2855. Solventcement joints shall be permitted above or below ground. Exception: Clear Primer conforming to ASTM F 656 mav be used on anv exposed PVC pipe or fittings on trim/finish work. | Plumbing TAC (0Yes-7No NAR) |
| Pinellas County Construction Licensing Board (PCCLB) | Florida Building Code, Plumbing | AMEND EXISTING SECTION SECTION 610 DISINFECTION OF POTABLE WATER SYSTEM 610.2 Applicable Sizes. The requirements of 610.1 in the following sizes shall apply when connected to an existing approved potable system. 1. All Building Department permitted and approved onsite potable drinking water piping two-inch (2") diameter and greater than one hundred fifty (150) lineal feet in length. 2. All Building Department permitted and approved onsite potable drinking water piping of greater than two-inch (2") diameter and greater than fifty (50) lineal feet in length. 3. All Building Department permitted and approved onsite potable drinking water piping in size(s) and length(s) adequate to contain twentv (20) gallons or more. (Volume = .0408 x diameter2 x length in feet). 4. Anv size or length water pipe that has been subiected to contamination will require disinfection. | Plumbing TAC (0Yes-7No NAR) |
| Pinellas County Construction Licensing Board (PCCLB) | Florida Building Code, Plumbing | AMEND EXISTING SECTION 705.14.2 Solvent cementing. Joint surfaces shall be clean and free from moisture. A purple primer that conforms to ASTM F 656 shall be applied. Solvent cement not purple in color and conforming to ASTMD2564, CSA 8137.3, CSA 8181.2 or CSA 8182.1 shall be applied to all joint surfaces. The joint shall be made while the cement is wet and shall be in accordance with ASTM D 2855. Solvent-cement joints shall be permitted above or below ground. Exception: Clear Primer conforming to ASTM F 656 mav be used on anv exposed PVC pipe or fittings on trim/finish work. | Plumbing TAC (0Yes-7No NAR) |
| Broward County | Florida Building Code, Plumbing | Amendment to 2014 5th Edition FBC – PLUMBING - APPENDIX F (Due to size of file must view link) https://floridabuilding.org/Upload/FBC/CodeID_7185_d37e_Broward%20County-Local_Amend-FBC%205th%20ED-2014-Plumbing-%20Appendix-F-2015-06-04.pdf | Plumbing TAC (0Yes-7No NAR) |
| Pinellas County Construction Licensing Board | Florida Building Code, Residential | SECTION P2705 INSTALLATION P2705.1 General. The installation of fixtures shall conform to the following: 1. Floor-outlet or floor-mounted fixtures shall be secured to the drainage connection and to the floor, where so designed, by screws, bolts, washers, nuts and similar fasteners of copper, brass or other corrosion-resistant material. 2. Wall-hung fixtures shall be rigidly supported so that strain is not transmitted to the plumbing system. 3. Where fixtures come in contact with walls and floors, the contact area shall be water tight. 4. Plumbing fixtures shall be usable and functionally accessible. 5. Water closets, lavatories and bidets. A water closet, lavatory or bidet shall not be set closer than 15 inches (381 mm) from its center to any side wall, partition or vanity or closer than 30 inches (762 mm) center-to-center between adjacent fixtures. There shall be at least a 21-inch (533 mm) in front of the water closet, lavatory or bidet to any wall, fixture or door. Plus the fixture spacing requirements of Section R307.1. 6. The location of piping, fixtures or equipment shall not interfere with the operation of windows or doors. 7. In flood hazard areas as established by Table R301.2 (1), plumbing fixtures shall be located or installed in accordance with Section R322.1.7. 8. Integral fixture-fitting mounting surfaces on manufactured plumbing fixtu res or plumbing fixtures constructed on site, shall meet the design requirements of ASME A112.19.2/CSA 845.4 or ASME A112.19.3/CSA 845.1. | Plumbing TAC (0Yes-7No NAR) |
| Pinellas County Construction Licensing Board | Florida Building Code, Residential | AMEND EXISTING SECTION P2903.1 Water supply system design criteria. The water service and water distribution systems shall be designed and pipe sizes shall be selected such that under conditions of peak demand, the capacities at the point of outlet discharge shall not be less than shown in Table P2903.1. EXCEPTION: For anv one, two or three residential family dwellings. When the building owner approves in writing, one bathroom group mav be added to the existing hot and cold water system, not to exceed a maximum of eight drainaqe fixture units for anv fixtures added. In no case shall the additional fixtures be connected to existing piping less than %" diameter (Hot and/or Cold). P2903.1.1 Applicable Sizes. The requirements of P2903.1 in the following sizes shall apply when connected to an existing approved potable system. 1. All Building Department permitted and approved onsite potable drinking water piping two-inch (2") diameter and greater than one hundred fifty (150) lineal feet in length. 2. All Building Department permitted and approved onsite potable drinking water piping of greater than two-inch (2") diameter and greater than fifty (50) lineal feet in length. 3. All Building Department permitted and approved onsite potable drinking water pipinq in size(s) and length(s) adequate to contain twenty (20) gallons or more. (Volume = .0408 x diameter2 x length in feet). 4. Anv size or length water pipe that has been subiected to contamination will require disinfection. | Plumbing TAC (0Yes-7No NAR) |
| Pinellas County Construction Licensing Board | Florida Building Code, Residential | AMEND EXISTING SECTION TABLE P2903.2b MINIMUM WATER SERVICE SIZEa AMEND FOOTNOTES: TABLE P2903.2b MINIMUM WATER SERVICE SIZEa NO. OF FIXTURE UNITS FLUSH TANK WCb; DIAMETER OF WATER PIPE; RECOMMENDED METER SIZE (INCHES)d; APPROX. PRESSURE LOSS METER + 100’ PIPE (psi)e; NO. OF FIXUTRE UNITS FLUSH VALVE WCb. 18; 3/4; 5/8; 30; =. 19-55 =; 1 1; 1 1; 30 30; = 9. 56-85 =; 1 ¼ 1 ¼; 1 1; 30 30; = 10-20. 8-225 =; 1 ½ 1 ½; 1 ½ 1 ½; 30 30; = 21-77. 226-350 =; 2 2; 1 ½ 1 ½; 30 30; = 78-175. 351-550 =; 2 2; 2 2; 30 30; = 176-315. 551-640 =; 2 ½ 2 ½; 2 2; 30 30; = 316-392. 641-1340 =; 3 3; 3 3; 22 22; = 393-940. AMEND FOOTNOTES: - Table is applicable for both copper and plastic water piping. - See Table P2903.6 for fixture unit values. - Minimum water serviceshall be ¾ “ to control valve. - All secondary sumeters and backflow assemblies shall be at least the same size as the line in which they are installed. - Table based on minimum water main pressure of 50 psi. - Minimu sizes for fixture supply pipe from the main or from the riser shall be from the Florida Building Code 5th Edition (2014) – Plumbing Section 604.5 - Four (4) fixtures maximum (hot or cold) may connect to a one-half inch fixture water supply or as required by manufacturers’ installation instructions. - Where the wter main pressure falls below 50 p.s.i. the next larger pipe size shall be used. - Buildings above three (3) stories in height shall use the next larger pipe size. | Plumbing TAC (0Yes-7No NAR) |
| Pinellas County Construction Licensing Board | Florida Building Code, Residential | AMEND EXISTING SECTION P2905.9.1.3 PVC plastic pipe. A purple primer that conforms to ASTM F 656 shall be applied to PVC solvent cemented joints. Solvent cement for PVC plastic pipe conforming to ASTM D 2564 shall be applied to all joint surfaces. Exception: Clear Primer conforming to ASTM F 656 mav be used on anv exposed PVC pipe or fittings on trim/finish work. | Plumbing TAC (0Yes-7No NAR) |
| Pinellas County Construction Licensing | Florida Building Code, Residential | AMEND EXISTING SECTION P3003.3.2 Solvent cementing. Joint surfaces shall be clean and free from moisture. Solvent cement that conforms to ASTM D 2235 or CSA 8181.1 shall be applied to all joint surfaces. The joint shall be made while the cement is wet. Joints shall be made in accordance with ASTM D 2235, ASTM D 2661, ASTM F 628 or CSA 8181.1. Solvent-cement joints shall be permitted above or below ground. Exception: Clear Primer conforming to ASTM F 656 mav be used on anv exposed PVC pipe or fittings on trim/finish work. | Plumbing TAC (0Yes – 7No NAR) |