{"text_format":"1","workbook":"xlsx","n_sheets":6,"sheets":["Prototype A1","Prototype A3","Prototype A20","Prototype B1","Prototype C1","Prototype D7"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":0,"defined_names":229,"comments":3,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Prototype A1","index":0,"n_rows":95,"n_cols":13,"rows_kept":95,"cut":false,"hidden":false,"merged":[[3,10,3,14],[3,5,3,9]]}
[]
["Output Results for Performance Based Code Compliance Reference Design Tests (Envelope Requirements shall use U-Factor for walls and Roofs, and F-Factor for slab-on-grade floors)"]
[]
[null,null,null,null,null,"Test Run 1 (Climate Zone 1)",null,null,null,null,"Test Run 2 (Climate Zone 2)"]
[null,"TYPE","Description of Components","UNITS","MIN / MAX","Sizing Results","Reference Results for Baseline model (ASHRAE)","Compliance Software Baseline Model Results (ASHRAE)",null,null,"Sizing Results","Reference Results for Baseline model (ASHRAE)","Compliance Software Baseline Model Results (ASHRAE)"]
["Envelope Components"]
[null,"Wall","Exterior Wall: U-Value","Btu/(h-ft2-°F)","MAX",null,0.124,0.124,null,null,null,0.124,0.124]
[null,"Wall","Exterior Wall: Thermal Capacity","(Btu/ft2-°F)",null,null,0.6,0.6,null,null,null,0.6,0.6]
[null,"Wall","Exterior Wall: Solar Reflectance","-","MIN",null,"NA","NA",null,null,null,"NA","NA"]
[null,"Wall","Exterior Wall: Solar Absorptance","-","MAX",null,"NA","NA",null,null,null,"NA","NA"]
[null,"Wall","Exterior Wall: Thermal Emittance","-","MIN",null,"NA","NA",null,null,null,"NA","NA"]
[null,"Floor","Floor Slab-on-grade: Unheated F-factor","Btu/(h-ft-°F)","MAX",null,0.73,0.73,null,null,null,0.73,0.73]
[null,"Floor","Floor Slab-on-grade: Thermal Capacity","(Btu/ft2-°F)",null,null,4.84,4.84,null,null,null,4.84,4.84]
[null,"Roof","Exterior Roof: U-Value","Btu/(h-ft2-°F)","MAX",null,6.3E-2,6.3E-2,null,null,null,6.3E-2,6.3E-2]
[null,"Roof","Exterior Roof: Thermal Capacity","(Btu/ft2-°F)",null,null,1.35,1.35,null,null,null,1.35,1.35]
[null,"Roof","Exterior Roof: Solar Reflectance","-","MIN",null,0.6,0.6,null,null,null,0.6,0.6]
[null,"Roof","Exterior Roof: Solar Absorptance","-","MAX",null,"NR","NR",null,null,null,"NR","NR"]
[null,"Roof","Exterior Roof: Thermal Emittance","-","MIN",null,0.9,0.9,null,null,null,0.9,0.9]
[null,"Fenestration","Exterior Window: U-Value","Btu/(h-ft2-°F)","MAX",null,0.5,0.5,null,null,null,0.37,0.37]
[null,"Fenestration","Exterior SEW Window: SHGC","-","MAX",null,0.25,0.25,null,null,null,0.25,0.25]
[null,"Fenestration","Exterior N Window: SHGC","-","MAX",null,0.27500000000000002,0.27500000000000002,null,null,null,0.27500000000000002,0.27500000000000002]
[null,"Fenestration","Exterior Window: WWR","(%)","Max",null,31,31,null,null,null,31,31]
[null,"Skylight","Skylight: U-Value","Btu/(h-ft2-°F)","MAX",null,0.75,0.75,null,null,null,0.65,0.65]
[null,"Skylight","Skylight: SHGC","-","MAX",null,0.35,0.35,null,null,null,0.35,0.35]
[null,"Skylight","Skylight: Skylight-Roof Ratio","(%)","MAX",null,3,3,null,null,null,3,3]
[null,null," "]
["Interior Lighting"]
[null,"Lighting","LPD: Space Method","W/ft2","MAX",null,1.1000000000000001,1.1000000000000001,null,null,null,1.1000000000000001,1.1000000000000001]
[null,null,null,null,""]
["Exterior Lighting",null,null,null,""]
[null,"Lighting","Total Lighting Allowance","W","MAX",null,870,846,null,null,null,870,846]
[null,null,null,null,""]
["Internal Loads"]
[null,"Equipment","Internal Electric Power Density","W/ft2","-",null,1.5,1.5,null,null,null,1.5,1.5]
[]
["HVAC System"]
[null,null,"HVAC System Type",null,null,null,"Packaged Roof Top Heat Pump","Packaged Roof Top Heat Pump",null,null,null,"Packaged Roof Top Heat Pump","Packaged Roof Top Heat Pump"]
[]
[null,null,"Heating Minimum Efficiency:"]
[null,null,"Efficiency (HSPF, COP at 47°F/COP at 17°F):"]
[null,"Heating HP","North Zone System Efficiency: ASHRAE","COP / COP","MIN",null,3.1,3.1,null,null,null,3.1,3.1]
[null,"Heating HP","North Zone System Efficiency: FEC","COP / COP","MIN"]
[]
[null,"Heating HP","South Zone System Efficiency: ASHRAE","COP / COP","MIN",null,3.1,3.1,null,null,null,3.1,3.1]
[null,"Heating HP","South Zone System Efficiency: FEC","COP / COP","MIN"]
[]
[null,"Heating HP","East Zone System Efficiency: ASHRAE","COP / COP","MIN",null,3.1,3.1,null,null,null,3.1,3.1]
[null,"Heating HP","East Zone System Efficiency: FEC","COP / COP","MIN"]
[]
[null,"Heating HP","West Zone System Efficiency: ASHRAE","COP / COP","MIN",null,3.1,3.1,null,null,null,3.1,3.1]
[null,"Heating HP","West Zone System Efficiency: FEC","COP / COP","MIN"]
[]
[null,"Heating HP","Core Zone System Efficiency: ASHRAE","COP / COP","MIN",null,3.1,3.1,null,null,null,3.1,3.1]
[null,"Heating HP","Core Zone System Efficiency: FEC","COP / COP","MIN"]
[]
[null,null,"Cooling Minimum Efficiency:",null,null,null,null,"with fan…",null,null,null,null,"with fan…"]
[null,"Cooling HP","North Zone System Efficiency: ASHRAE","EER / IEER","MIN",null,9.1,9.1,null,null,null,9.1,9.1]
[null,"Cooling HP","North Zone System Efficiency: FEC","EER / IEER","MIN"]
[]
[null,"Cooling HP","South Zone System Efficiency: ASHRAE","EER / IEER","MIN",null,9.1,9.1,null,null,null,9.1,9.1]
[null,"Cooling HP","South Zone System Efficiency: FEC","EER / IEER","MIN"]
[]
[null,"Cooling HP","East Zone System Efficiency: ASHRAE","EER / IEER","MIN",null,9.1,9.1,null,null,null,9.1,9.1]
[null,"Cooling HP","East Zone System Efficiency: FEC","EER / IEER","MIN"]
[]
[null,"Cooling HP","West Zone System Efficiency: ASHRAE","EER / IEER","MIN",null,9.1,9.1,null,null,null,9.1,9.1]
[null,"Cooling HP","West Zone System Efficiency: FEC","EER / IEER","MIN"]
[]
[null,"Cooling HP","Core Zone System Efficiency: ASHRAE","EER / IEER","MIN",null,9.1,9.1,null,null,null,9.1,9.1]
[null,"Cooling HP","Core Zone System Efficiency: FEC","EER / IEER","MIN"]
[]
[]
[null,null,"Air Economizer (Yes, or No):"]
[null,"Air Economizer","North Zone System Economizer: ASHRAE ","-","-",null,"No","No",null,null,null,"Yes","Yes"]
[null,"Air Economizer","North Zone System Economizer: FEC","-","-"]
[]
[null,"Air Economizer","South Zone System Economizer: ASHRAE ","-","-",null,"No","No",null,null,null,"Yes","Yes"]
[null,"Air Economizer","South Zone System Economizer: FEC","-","-"]
[]
[null,"Air Economizer","East Zone System Economizer: ASHRAE ","-","-",null,"No","No",null,null,null,"Yes","Yes"]
[null,"Air Economizer","East Zone System Economizer: FEC","-","-"]
[]
[null,"Air Economizer","West Zone System Economizer: ASHRAE ","-","-",null,"No","No",null,null,null,"Yes","Yes"]
[null,"Air Economizer","West Zone System Economizer: FEC","-","-"]
[]
[null,"Air Economizer","Core Zone System Economizer: ASHRAE ","-","-",null,"No","No",null,null,null,"Yes","Yes"]
[null,"Air Economizer","Core Zone System Economizer: FEC","-","-"]
[]
[]
["Service Water Heating"]
[null,"SWH","SWH Type",null,null,null,"Storage Water Heater",null,null,null,null,"Storage Water Heater"]
[null,"SWH","Fuel Type",null,null,null,"Electric",null,null,null,null,"Electric"]
[null,"SWH","Thermal Efficiency:"]
[null,"SWH","Size <= 12 kW, Energy Factor (EF) "," EF ","MIN",null,0.94199999999999995,0.94,null,null,null,null,0.94]
[null,"SWH","Size > 12 kW, Size > 20 gal, Standby Loss ","%/h","MAX"]

{"sheet":"Prototype A3","index":1,"n_rows":97,"n_cols":15,"rows_kept":97,"cut":false,"hidden":false,"merged":[[3,10,3,14],[3,5,3,9]]}
[]
["Output Results for Performance Based Code Compliance Reference Design Tests (Envelope Requirements shall use U-Factor for walls and Roofs, and F-Factor for slab-on-grade floors)"]
[]
[null,null,null,null,null,"Test Run 1 (Climate Zone 1)",null,null,null,null,"Test Run 2 (Climate Zone 2)"]
[null,"TYPE","Description of Components","UNITS","MIN / MAX","Sizing Results","Reference Results for Baseline model (ASHRAE)","Compliance Software Baseline Model Results (ASHRAE)",null,null,"Sizing Results","Reference Results for Baseline model (ASHRAE)","Compliance Software Baseline Model Results (ASHRAE)","Reference Results for Baseline model (FEC)","Compliance Software Baseline Model Results (FEC)"]
["Envelope Components"]
[null,"Wall","Exterior Wall: U-Value","Btu/(h-ft2-°F)","MAX",null,0.124,0.124,null,null,null,0.124,0.124]
[null,"Wall","Exterior Wall: Thermal Capacity","(Btu/ft2-°F)",null,null,0.6,0.6,null,null,null,0.6,0.6]
[null,"Wall","Exterior Wall: Solar Reflectance","-","MIN",null,"NA","NA",null,null,null,"NA","NA"]
[null,"Wall","Exterior Wall: Solar Absorptance","-","MAX",null,"NA","NA",null,null,null,"NA","NA"]
[null,"Wall","Exterior Wall: Thermal Emittance","-","MIN",null,"NA","NA",null,null,null,"NA","NA"]
[null,"Floor","Floor Slab-on-grade: Unheated F-factor","Btu/(h-ft-°F)","MAX",null,0.73,0.73,null,null,null,0.73,0.73]
[null,"Floor","Floor Slab-on-grade: Thermal Capacity","(Btu/ft2-°F)",null,null,4.84,4.84,null,null,null,4.84,4.84]
[null,"Roof","Exterior Roof: U-Value","Btu/(h-ft2-°F)","MAX",null,6.3E-2,6.3E-2,null,null,null,6.3E-2,6.3E-2]
[null,"Roof","Exterior Roof: Thermal Capacity","(Btu/ft2-°F)",null,null,1.35,1.35,null,null,null,1.35,1.35]
[null,"Roof","Exterior Roof: Solar Reflectance","-","MIN",null,0.6,0.6,null,null,null,0.6,0.6]
[null,"Roof","Exterior Roof: Solar Absorptance","-","MAX",null,"NR","NR",null,null,null,"NR","NR"]
[null,"Roof","Exterior Roof: Thermal Emittance","-","MIN",null,0.9,0.9,null,null,null,0.9,0.9]
[null,"Floor","Internal Floor: Thermal Capacity","(Btu/ft2-°F)",null,null,0.5,0.5,null,null,null,0.37,0.37]
[null,"Floor","Internal Floor: U-Value","Btu/(h-ft2-°F)","MAX",null,0.25,0.25,null,null,null,0.25,0.25]
[null,"Fenestration","Exterior Window: U-Value","Btu/(h-ft2-°F)","MAX",null,0.27500000000000002,0.27500000000000002,null,null,null,0.27500000000000002,0.27500000000000002]
[null,"Fenestration","Exterior SEW Window: SHGC","-","MAX",null,31,31,null,null,null,31,31]
[null,"Fenestration","Exterior N Window: SHGC","-","MAX",null,0.75,0.75,null,null,null,0.65,0.65]
[null,"Fenestration","Exterior Window: WWR","(%)","Max",null,0.35,0.35,null,null,null,0.35,0.35]
[null,null,null,null,null,null,3,3,null,null,null,3,3]
["Interior Lighting"]
[null,"Lighting","LPD: Space Method","W/ft2","MAX",null,1.1000000000000001,1.1000000000000001,null,null,null,1.1000000000000001,1.1000000000000001]
[null,null,null,null,""]
["Exterior Lighting",null,null,null,""]
[null,"Lighting","Total Lighting Allowance (W)","W","MAX",null,870,846,null,null,null,870,846]
[null,null,null,null,""]
["Internal Loads"]
[null,"Equipment","Internal Electric Power Density","W/ft2","-",null,1.5,1.5,null,null,null,1.5,1.5]
[]
["HVAC System"]
[null,null,"HVAC System Type",null,null,null,"Packaged Roof Top Heat Pump","Packaged Roof Top Heat Pump",null,null,null,"Packaged Roof Top Heat Pump","Packaged Roof Top Heat Pump"]
[]
[null,null,"Heating Minimum Efficiency:"]
[null,null,"Efficiency (HSPF, COP at 47°F/COP at 17°F):"]
[null,"Heating HP","North Zone System Efficiency: ASHRAE","COP / COP","MIN",null,3.1,3.1,null,null,null,3.1,3.1]
[null,"Heating HP","North Zone System Efficiency: FEC","COP / COP","MIN"]
[]
[null,"Heating HP","South Zone System Efficiency: ASHRAE","COP / COP","MIN",null,3.1,3.1,null,null,null,3.1,3.1]
[null,"Heating HP","South Zone System Efficiency: FEC","COP / COP","MIN"]
[]
[null,"Heating HP","East Zone System Efficiency: ASHRAE","COP / COP","MIN",null,3.1,3.1,null,null,null,3.1,3.1]
[null,"Heating HP","East Zone System Efficiency: FEC","COP / COP","MIN"]
[]
[null,"Heating HP","West Zone System Efficiency: ASHRAE","COP / COP","MIN",null,3.1,3.1,null,null,null,3.1,3.1]
[null,"Heating HP","West Zone System Efficiency: FEC","COP / COP","MIN"]
[]
[null,"Heating HP","Core Zone System Efficiency: ASHRAE","COP / COP","MIN",null,3.1,3.1,null,null,null,3.1,3.1]
[null,"Heating HP","Core Zone System Efficiency: FEC","COP / COP","MIN"]
[]
[null,null,"Cooling Minimum Efficiency:",null,null,null,"No","with fan…",null,null,null,null,"with fan…"]
[null,"Cooling HP","North Zone System Efficiency: ASHRAE","EER / IEER","MIN",null,9.1,9.1,null,null,null,9.1,9.1]
[null,"Cooling HP","North Zone System Efficiency: FEC","EER / IEER","MIN"]
[null,null,null,null,null,null,"No"]
[null,"Cooling HP","South Zone System Efficiency: ASHRAE","EER / IEER","MIN",null,9.1,9.1,null,null,null,9.1,9.1]
[null,"Cooling HP","South Zone System Efficiency: FEC","EER / IEER","MIN"]
[null,null,null,null,null,null,"No"]
[null,"Cooling HP","East Zone System Efficiency: ASHRAE","EER / IEER","MIN",null,9.1,9.1,null,null,null,9.1,9.1]
[null,"Cooling HP","East Zone System Efficiency: FEC","EER / IEER","MIN"]
[]
[null,"Cooling HP","West Zone System Efficiency: ASHRAE","EER / IEER","MIN",null,9.1,9.1,null,null,null,9.1,9.1]
[null,"Cooling HP","West Zone System Efficiency: FEC","EER / IEER","MIN"]
[]
[null,"Cooling HP","Core Zone System Efficiency: ASHRAE","EER / IEER","MIN",null,9.1,9.1,null,null,null,9.1,9.1]
[null,"Cooling HP","Core Zone System Efficiency: FEC","EER / IEER","MIN"]
[]
[null,null,"Air Economizer (Yes, or No):"]
[null,"Air Economizer","North Zone System Economizer: ASHRAE ","-","-",null,"No","No",null,null,null,"Yes","Yes"]
[null,"Air Economizer","North Zone System Economizer: FEC","-","-"]
[]
[null,"Air Economizer","South Zone System Economizer: ASHRAE ","-","-",null,"No","No",null,null,null,"Yes","Yes"]
[null,"Air Economizer","South Zone System Economizer: FEC","-","-"]
[]
[null,"Air Economizer","East Zone System Economizer: ASHRAE ","-","-",null,"No","No",null,null,null,"Yes","Yes"]
[null,"Air Economizer","East Zone System Economizer: FEC","-","-"]
[]
[null,"Air Economizer","West Zone System Economizer: ASHRAE ","-","-",null,"No","No",null,null,null,"Yes","Yes"]
[null,"Air Economizer","West Zone System Economizer: FEC","-","-"]
[]
[null,"Air Economizer","Core Zone System Economizer: ASHRAE ","-","-",null,"No","No",null,null,null,"Yes","Yes"]
[null,"Air Economizer","Core Zone System Economizer: FEC","-","-"]
[]
["Service Water Heating"]
[null,"SWH","SWH Type",null,null,null,"Storage Water Heater","Storage Water Heater",null,null,null,"Storage Water Heater","Storage Water Heater"]
[null,"SWH","Fuel Type",null,null,null,"Gas","Gas",null,null,null,"Gas","Gas"]
[null,"SWH","Thermal Efficiency:"]
[null,"SWH","Size <= 75 kBtu/h, Energy Factor (EF)"," EF ","MIN",null,0.63,0.63,null,null,null,0.63,0.63]
[null,"SWH","Size > 75 kBtu/h, Thermal Efficiency (Et)","%","MIN"]
[null,"SWH","Size > 75 kBtu/h, Standby Loss (SL)","Btu/h","MAX"]
[]
["Elevator Motor"]
[null,null,"Electric Motor Power (HP)","HP","MAX",null,7.5,7.5,null,null,null,7.5,7.5]
[null,null,"Electric Motor Efficiency (%)","%","MIN",null,88,88,null,null,null,88,88]

{"sheet":"Prototype A20","index":2,"n_rows":60,"n_cols":15,"rows_kept":60,"cut":false,"hidden":false,"merged":[[3,5,3,9],[3,10,3,14]]}
[]
["Output Results for Performance Based Code Compliance Reference Design Tests (Envelope Requirements shall use U-Factor for walls and Roofs, and F-Factor for slab-on-grade floors)"]
[]
[null,null,null,null,null,"Test Run 1 (Climate Zone 1)",null,null,null,null,"Test Run 2 (Climate Zone 2)"]
[null,"TYPE","Description of Components","UNITS","MIN / MAX","Sizing Results","Reference Results for Baseline model (ASHRAE)","Compliance Software Baseline Model Results (ASHRAE)","Reference Results for Baseline model (FEC)","Compliance Software Baseline Model Results (FEC)","Sizing Results","Reference Results for Baseline model (ASHRAE)","Compliance Software Baseline Model Results (ASHRAE)","Reference Results for Baseline model (FEC)","Compliance Software Baseline Model Results (FEC)"]
["Envelope Components"]
[null,"Wall","Exterior Wall: U-Value","Btu/(h-ft2-°F)","MAX",null,0.124,0.124,null,null,null,0.124,0.124]
[null,"Wall","Exterior Wall: Thermal Capacity","(Btu/ft2-°F)",null,null,0.6,0.6,null,null,null,0.6,0.6]
[null,"Wall","Exterior Wall: Solar Reflectance","-","MIN",null,"NA","NA",null,null,null,"NA","NA"]
[null,"Wall","Exterior Wall: Solar Absorptance","-","MAX",null,"NA","NA",null,null,null,"NA","NA"]
[null,"Wall","Exterior Wall: Thermal Emittance","-","MIN",null,"NA","NA",null,null,null,"NA","NA"]
[null,"Floor","Floor Slab-on-grade: Unheated F-factor","Btu/(h-ft-°F)","MAX",null,0.73,0.73,null,null,null,0.73,0.73]
[null,"Floor","Floor Slab-on-grade: Thermal Capacity","(Btu/ft2-°F)",null,null,4.84,4.84,null,null,null,4.84,4.84]
[null,"Roof","Exterior Roof: U-Value","Btu/(h-ft2-°F)","MAX",null,6.3E-2,6.3E-2,null,null,null,6.3E-2,6.3E-2]
[null,"Roof","Exterior Roof: Thermal Capacity","(Btu/ft2-°F)",null,null,1.35,1.35,null,null,null,1.35,1.35]
[null,"Roof","Exterior Roof: Solar Reflectance","-","MIN",null,0.6,0.6,null,null,null,0.6,0.6]
[null,"Roof","Exterior Roof: Solar Absorptance","-","MAX",null,"NR","NR",null,null,null,"NR","NR"]
[null,"Roof","Exterior Roof: Thermal Emittance","-","MIN",null,0.9,0.9,null,null,null,0.9,0.9]
[null,"Floor","Internal Floor: Thermal Capacity","(Btu/ft2-°F)",null,null,0.5,0.5,null,null,null,0.37,0.37]
[null,"Floor","Internal Floor: U-Value","Btu/(h-ft2-°F)","MAX",null,0.25,0.25,null,null,null,0.25,0.25]
[null,"Fenestration","Exterior Window: U-Value","Btu/(h-ft2-°F)","MAX",null,0.27500000000000002,0.27500000000000002,null,null,null,0.27500000000000002,0.27500000000000002]
[null,"Fenestration","Exterior SEW Window: SHGC","-","MAX",null,31,31,null,null,null,31,31]
[null,"Fenestration","Exterior N Window: SHGC","-","MAX",null,0.75,0.75,null,null,null,0.65,0.65]
[null,"Fenestration","Exterior Window: WWR","(%)","Max",null,0.35,0.35,null,null,null,0.35,0.35]
[null,null,null,null,null,null,3,3,null,null,null,3,3]
["Interior Lighting"]
[null,"Lighting","LPD: Space Method","W/ft2","MAX",null,1.1000000000000001,1.1000000000000001,null,null,null,1.1000000000000001,1.1000000000000001]
[null,null,null,null,""]
["Exterior Lighting",null,null,null,""]
[null,"Lighting","Total Lighting Allowance (W)","W","MAX",null,870,846,null,null,null,870,846]
[null,null,null,null,""]
["Internal Loads"]
[null,"Equipment","Internal Electric Power Density","W/ft2","-",null,1.5,1.5,null,null,null,1.5,1.5]
[]
["HVAC System"]
[null,null,"HVAC system type",null,null,null,"VAV with Reheat, Chilled Water, Electric Resistence","VAV with Reheat, Chilled Water, Electric Resistence",null,null,null,"VAV with Reheat, Chilled Water, Electric Resistence","VAV with Reheat, Chilled Water, Electric Resistence"]
[]
[null,null,"Electric Resistence"]
[]
[null,null,"Water Chilling Package Minimum Efficiency:"]
[null,null,"Electrically Operated: "]
[null,null,"Path A: Centrifugal"]
[null,"Chiller","Central Centrifugal Chiller Efficiency: ASHRAE","kW/ton","MAX",null,"0.576 FL, 0.549 IPLV","6.01 COP",null,null,null,"0.576 FL, 0.549 IPLV","6.01 COP"]
[null,"Chiller","Central Centrifugal Chiller Efficiency: FEC"]
[]
[]
[null,null,"Air Economizer Requirement (Yes, or No):"]
[null,"Air Economizer","First Floor System Economizer: ASHRAE ","-","-","-","No","No",null,null,null,"Yes","Yes"]
[null,"Air Economizer","First Floor System Economizer: FEC","-","-","-"]
[]
[null,"Air Economizer","Mid Floors (2-19) System Economizer: ASHRAE ","-","-","-","No","No",null,null,null,"Yes","Yes"]
[null,"Air Economizer","Mid Floors (2-19) System Economizer: FEC","-","-","-"]
[]
[null,"Air Economizer","Top Floor System Economizer: ASHRAE ","-","-","-","No","No",null,null,null,"Yes","Yes"]
[null,"Air Economizer","Top Floor System Economizer: FEC","-","-","-"]
[]
[]
["Elevator Motor"]
[null,null,"Electric Motor Power (HP)","HP","MAX",null,20,20,null,null,null,20,20]
[null,null,"Electric Motor Efficiency (%)","%","MAX",null,92,92,null,null,null,92,92]

{"sheet":"Prototype B1","index":3,"n_rows":99,"n_cols":25,"rows_kept":99,"cut":false,"hidden":false,"merged":[[3,20,3,24],[3,6,3,9],[3,16,3,19],[3,10,3,14]]}
[]
["Output Results for Performance Based Code Compliance Reference Design Tests (Envelope Requirements shall use U-Factor for walls and Roofs, and F-Factor for slab-on-grade floors)"]
[]
[null,null,null,null,null,null,"Test Run 1 (Climate Zone 1), Retail",null,null,null,"Test Run 2 (Climate Zone 2), Retail",null,null,null,null,null,"Test Run 3 (Climate Zone 1), Supermarket",null,null,null,"Test Run 4 (Climate Zone 2), Supermarket"]
[null,"TYPE","Description of Components","UNITS","MIN / MAX","Sizing Results","Reference Results for Baseline model (ASHRAE)","Compliance Software Baseline Model Results (ASHRAE)","Reference Results for Baseline model (FEC)","Compliance Software Baseline Model Results (FEC)","Sizing Results","Reference Results for Baseline model (ASHRAE)","Compliance Software Baseline Model Results (ASHRAE)","Reference Results for Baseline model (FEC)","Compliance Software Baseline Model Results (FEC)","Sizing Results","Reference Results for Baseline model (ASHRAE)","Compliance Software Baseline Model Results (ASHRAE)","Reference Results for Baseline model (FEC)","Compliance Software Baseline Model Results (FEC)","Sizing Results","Reference Results for Baseline model (ASHRAE)","Compliance Software Baseline Model Results (ASHRAE)","Reference Results for Baseline model (FEC)","Compliance Software Baseline Model Results (FEC)"]
["Envelope Components"]
[null,"Wall","Exterior Wall: U-Value","Btu/(h-ft2-°F)","MAX",null,0.124,0.124,null,null,null,0.124,0.124,null,null,null,0.124,0.124,null,null,null,0.124,0.124]
[null,"Wall","Exterior Wall: Thermal Capacity","(Btu/ft2-°F)",null,null,0.6,0.6,null,null,null,0.6,0.6,null,null,null,0.6,0.6,null,null,null,0.6,0.6]
[null,"Wall","Exterior Wall: Solar Reflectance","-","MIN",null,"NA","NA",null,null,null,"NA","NA",null,null,null,"NA","NA",null,null,null,"NA","NA"]
[null,"Wall","Exterior Wall: Solar Absorptance","-","MAX",null,"NA","NA",null,null,null,"NA","NA",null,null,null,"NA","NA",null,null,null,"NA","NA"]
[null,"Wall","Exterior Wall: Thermal Emittance","-","MIN",null,"NA","NA",null,null,null,"NA","NA",null,null,null,"NA","NA",null,null,null,"NA","NA"]
[null,"Floor","Floor Slab-on-grade: Unheated F-factor","Btu/(h-ft-°F)","MAX",null,0.73,0.73,null,null,null,0.73,0.73,null,null,null,0.73,0.73,null,null,null,0.73,0.73]
[null,"Floor","Floor Slab-on-grade: Thermal Capacity","(Btu/ft2-°F)",null,null,4.84,4.84,null,null,null,4.84,4.84,null,null,null,4.84,4.84,null,null,null,4.84,4.84]
[null,"Roof","Exterior Roof: U-Value","Btu/(h-ft2-°F)","MAX",null,6.3E-2,6.3E-2,null,null,null,6.3E-2,6.3E-2,null,null,null,6.3E-2,6.3E-2,null,null,null,6.3E-2,6.3E-2]
[null,"Roof","Exterior Roof: Thermal Capacity","(Btu/ft2-°F)",null,null,1.35,1.35,null,null,null,1.35,1.35,null,null,null,1.35,1.35,null,null,null,1.35,1.35]
[null,"Roof","Exterior Roof: Solar Reflectance","-","MIN",null,0.6,0.6,null,null,null,0.6,0.6,null,null,null,0.6,0.6,null,null,null,0.6,0.6]
[null,"Roof","Exterior Roof: Solar Absorptance","-","MAX",null,"NR","NR",null,null,null,"NR","NR",null,null,null,"NR","NR",null,null,null,"NR","NR"]
[null,"Roof","Exterior Roof: Thermal Emittance","-","MIN",null,0.9,0.9,null,null,null,0.9,0.9,null,null,null,0.9,0.9,null,null,null,0.9,0.9]
[null,"Fenestration","Exterior Window: U-Value","Btu/(h-ft2-°F)","MAX",null,0.5,0.5,null,null,null,0.37,0.37,null,null,null,0.5,0.5,null,null,null,0.37,0.37]
[null,"Fenestration","Exterior SEW Window: SHGC","-","MAX",null,0.25,0.25,null,null,null,0.25,0.25,null,null,null,0.25,0.25,null,null,null,0.25,0.25]
[null,"Fenestration","Exterior N Window: SHGC","-","MAX",null,0.27500000000000002,0.27500000000000002,null,null,null,0.27500000000000002,0.27500000000000002,null,null,null,0.27500000000000002,0.27500000000000002,null,null,null,0.27500000000000002,0.27500000000000002]
[null,"Fenestration","Exterior Window: WWR","(%)","Max",null,31,31,null,null,null,31,31,null,null,null,31,31,null,null,null,31,31]
[null,"Skylight","Skylight: U-Value","Btu/(h-ft2-°F)","MAX",null,0.75,0.75,null,null,null,0.65,0.65,null,null,null,0.75,0.75,null,null,null,0.65,0.65]
[null,"Skylight","Skylight: SHGC","-","MAX",null,0.35,0.35,null,null,null,0.35,0.35,null,null,null,0.35,0.35,null,null,null,0.35,0.35]
[null,"Skylight","Skylight: Skylight-Roof Ratio","(%)","MAX",null,3,3,null,null,null,3,3,null,null,null,3,3,null,null,null,3,3]
[null,null," "]
["Horizontal Overhang Shade"]
[null,null,"Projection Factor  (-)",null,null,null,0,0,null,null,null,0,0,null,null,null,0,0,null,null,null,0,0]
[]
["Interior Lighting"]
[null,"Lighting","LPD: Space Method","W/ft2","MAX",null,1.7,1.7,null,null,null,1.7,1.7,null,null,null,1.7,1.7,null,null,null,1.7,1.7]
[null,null,null,null,""]
["Exterior Lighting",null,null,null,""]
[null,"Lighting","Total Lighting Allowance","W","MAX",null,740,712,null,null,null,740,712,null,null,null,740,712,null,null,null,740,712]
[null,null,null,null,""]
["Internal Loads"]
[null,"Equipment","Internal Electric Power Density","W/ft2","-",null,1,1,null,null,null,1,1,null,null,null,1,1,null,null,null,1,1]
[]
["HVAC System"]
[null,null,"HVAC System Type",null,null,null,"Packaged Roof Top Heat Pump","Packaged Roof Top Heat Pump",null,null,null,"Packaged Roof Top Heat Pump","Packaged Roof Top Heat Pump",null,null,null,"Packaged Roof Top Heat Pump","Packaged Roof Top Heat Pump",null,null,null,"Packaged Roof Top Heat Pump","Packaged Roof Top Heat Pump"]
[]
[null,null,"Heating Minimum Efficiency:"]
[null,null,"Efficiency (HSPF, COP at 47°F/COP at 17°F):"]
[null,"Heating HP","North Zone System Efficiency: ASHRAE","COP / COP","MIN",null,3.1,3.1,null,null,null,3.1,3.1,null,null,null,3.1,3.1,null,null,null,3.1,3.1]
[null,"Heating HP","North Zone System Efficiency: FEC","COP / COP","MIN"]
[]
[null,"Heating HP","South Zone System Efficiency: ASHRAE","COP / COP","MIN",null,3.1,3.1,null,null,null,3.1,3.1,null,null,null,3.1,3.1,null,null,null,3.1,3.1]
[null,"Heating HP","South Zone System Efficiency: FEC","COP / COP","MIN"]
[]
[null,"Heating HP","East Zone System Efficiency: ASHRAE","COP / COP","MIN",null,3.1,3.1,null,null,null,3.1,3.1,null,null,null,3.1,3.1,null,null,null,3.1,3.1]
[null,"Heating HP","East Zone System Efficiency: FEC","COP / COP","MIN"]
[]
[null,"Heating HP","West Zone System Efficiency: ASHRAE","COP / COP","MIN",null,3.1,3.1,null,null,null,3.1,3.1,null,null,null,3.1,3.1,null,null,null,3.1,3.1]
[null,"Heating HP","West Zone System Efficiency: FEC","COP / COP","MIN"]
[]
[null,"Heating HP","Core Zone System Efficiency: ASHRAE","COP / COP","MIN",null,3.1,3.1,null,null,null,3.1,3.1,null,null,null,3.1,3.1,null,null,null,3.1,3.1]
[null,"Heating HP","Core Zone System Efficiency: FEC","COP / COP","MIN"]
[]
[]
[null,"Cooling HP","Cooling Minimum Efficiency:",null,null,null,null,"with fan…",null,null,null,null,"with fan…",null,null,null,null,"with fan…",null,null,null,null,"with fan…"]
[null,"Cooling HP","North Zone System Efficiency: ASHRAE","EER / IEER","MIN",null,9.1,9.1,null,null,null,9.1,9.1,null,null,null,9.1,9.1,null,null,null,9.1,9.1]
[null,null,"North Zone System Efficiency: FEC","EER / IEER","MIN"]
[null,"Cooling HP"]
[null,"Cooling HP","South Zone System Efficiency: ASHRAE","EER / IEER","MIN",null,9.1,9.1,null,null,null,9.1,9.1,null,null,null,9.1,9.1,null,null,null,9.1,9.1]
[null,null,"South Zone System Efficiency: FEC","EER / IEER","MIN"]
[null,"Cooling HP"]
[null,"Cooling HP","East Zone System Efficiency: ASHRAE","EER / IEER","MIN",null,9.1,9.1,null,null,null,9.1,9.1,null,null,null,9.1,9.1,null,null,null,9.1,9.1]
[null,null,"East Zone System Efficiency: FEC","EER / IEER","MIN"]
[null,"Cooling HP"]
[null,"Cooling HP","West Zone System Efficiency: ASHRAE","EER / IEER","MIN",null,9.1,9.1,null,null,null,9.1,9.1,null,null,null,9.1,9.1,null,null,null,9.1,9.1]
[null,null,"West Zone System Efficiency: FEC","EER / IEER","MIN"]
[null,"Cooling HP"]
[null,"Cooling HP","Core Zone System Efficiency: ASHRAE","EER / IEER","MIN",null,9.1,9.1,null,null,null,9.1,9.1,null,null,null,9.1,9.1,null,null,null,9.1,9.1]
[null,"Cooling DX","Core Zone System Efficiency: FEC","EER / IEER","MIN"]
[]
[]
[null,null,"Air Economizer (Yes, or No):"]
[null,"Air Economizer","North Zone System Economizer: ASHRAE ","-","-",null,"No","No",null,null,null,"Yes","Yes",null,null,null,"No","No",null,null,null,"Yes","Yes"]
[null,"Air Economizer","North Zone System Economizer: FEC","-","-"]
[]
[null,"Air Economizer","South Zone System Economizer: ASHRAE ","-","-",null,"No","No",null,null,null,"Yes","Yes",null,null,null,"No","No",null,null,null,"Yes","Yes"]
[null,"Air Economizer","South Zone System Economizer: FEC","-","-"]
[]
[null,"Air Economizer","East Zone System Economizer: ASHRAE ","-","-",null,"No","No",null,null,null,"Yes","Yes",null,null,null,"No","No",null,null,null,"Yes","Yes"]
[null,"Air Economizer","East Zone System Economizer: FEC","-","-"]
[]
[null,"Air Economizer","West Zone System Economizer: ASHRAE ","-","-",null,"No","No",null,null,null,"Yes","Yes",null,null,null,"No","No",null,null,null,"Yes","Yes"]
[null,"Air Economizer","West Zone System Economizer: FEC","-","-"]
[]
[null,"Air Economizer","Core Zone System Economizer: ASHRAE ","-","-",null,"No","No",null,null,null,"Yes","Yes",null,null,null,"No","No",null,null,null,"Yes","Yes"]
[null,"Air Economizer","Core Zone System Economizer: FEC","-","-"]
[]
[]
["Service Water Heating"]
[null,"SWH","SWH Type",null,null,null,null,"Storage Water Heater",null,null,null,"Storage Water Heater","Storage Water Heater",null,null,null,"Storage Water Heater","Storage Water Heater",null,null,null,"Storage Water Heater","Storage Water Heater"]
[null,"SWH","Fuel Type",null,null,null,null,"Electric",null,null,null,"Electric","Electric",null,null,null,"Electric","Electric",null,null,null,"Electric","Electric"]
[null,"SWH","Thermal Efficiency:"]
[null,"SWH","Size <= 12 kW, Energy Factor (EF)"," EF ","MIN",null,null,12,null,null,null,0.94199999999999995,null,null,null,null,0.94199999999999995,0.94,null,null,null,0.94199999999999995]
[null,"SWH","Size > 12 kW, Size > 20 gal, Standby Loss","%/h","MAX",null,null,null,null,null,null,null,0.94,null,null,null,null,null,null,null,null,null,0.94]

{"sheet":"Prototype C1","index":4,"n_rows":73,"n_cols":25,"rows_kept":73,"cut":false,"hidden":false,"merged":[[3,10,3,14],[3,20,3,24],[3,5,3,9],[3,15,3,19]]}
[]
["Output Results for Performance Based Code Compliance Reference Design Tests (Envelope Requirements shall use U-Factor for walls and Roofs, and F-Factor for slab-on-grade floors)"]
[]
[null,null,null,null,null,"Test Run 1 (Climate Zone 1), Manufacturing",null,null,null,null,"Test Run 2 (Climate Zone 2), Manufacturing",null,null,null,null,"Test Run 3 (Climate Zone 1), Warehouse",null,null,null,null,"Test Run 4 (Climate Zone 2), Warehouse"]
[null,"TYPE","Description of Components","UNITS","MIN / MAX","Sizing Results","Reference Results for Baseline model (ASHRAE)","Compliance Software Baseline Model Results (ASHRAE)","Reference Results for Baseline model (FEC)","Compliance Software Baseline Model Results (FEC)","Sizing Results","Reference Results for Baseline model (ASHRAE)","Compliance Software Baseline Model Results (ASHRAE)","Reference Results for Baseline model (FEC)","Compliance Software Baseline Model Results (FEC)","Sizing Results","Reference Results for Baseline model (ASHRAE)","Compliance Software Baseline Model Results (ASHRAE)","Reference Results for Baseline model (FEC)","Compliance Software Baseline Model Results (FEC)","Sizing Results","Reference Results for Baseline model (ASHRAE)","Compliance Software Baseline Model Results (ASHRAE)","Reference Results for Baseline model (FEC)","Compliance Software Baseline Model Results (FEC)"]
["Envelope Components"]
[null,"Wall","Exterior Wall: U-Value","Btu/(h-ft2-°F)","MAX",null,0.124,0.124,null,null,null,0.124,0.124,null,null,null,0.124,0.124,null,null,null,0.124,0.124]
[null,"Wall","Exterior Wall: Thermal Capacity","(Btu/ft2-°F)",null,null,0.6,0.6,null,null,null,0.6,0.6,null,null,null,0.6,0.6,null,null,null,0.6,0.6]
[null,"Wall","Exterior Wall: Solar Reflectance","-","MIN",null,"NA","NA",null,null,null,"NA","NA",null,null,null,"NA","NA",null,null,null,"NA","NA"]
[null,"Wall","Exterior Wall: Solar Absorptance","-","MAX",null,"NA","NA",null,null,null,"NA","NA",null,null,null,"NA","NA",null,null,null,"NA","NA"]
[null,"Wall","Exterior Wall: Thermal Emittance","-","MIN",null,"NA","NA",null,null,null,"NA","NA",null,null,null,"NA","NA",null,null,null,"NA","NA"]
[null,"Floor","Floor Slab-on-grade: Unheated F-factor","Btu/(h-ft-°F)","MAX",null,0.73,0.73,null,null,null,0.73,0.73,null,null,null,0.73,0.73,null,null,null,0.73,0.73]
[null,"Floor","Floor Slab-on-grade: Thermal Capacity","(Btu/ft2-°F)",null,null,4.84,4.84,null,null,null,4.84,4.84,null,null,null,4.84,4.84,null,null,null,4.84,4.84]
[null,"Roof","Exterior Roof: U-Value","Btu/(h-ft2-°F)","MAX",null,6.3E-2,6.3E-2,null,null,null,6.3E-2,6.3E-2,null,null,null,6.3E-2,6.3E-2,null,null,null,6.3E-2,6.3E-2]
[null,"Roof","Exterior Roof: Thermal Capacity","(Btu/ft2-°F)",null,null,1.35,1.35,null,null,null,1.35,1.35,null,null,null,1.35,1.35,null,null,null,1.35,1.35]
[null,"Roof","Exterior Roof: Solar Reflectance","-","MIN",null,0.6,0.6,null,null,null,0.6,0.6,null,null,null,0.6,0.6,null,null,null,0.6,0.6]
[null,"Roof","Exterior Roof: Solar Absorptance","-","MAX",null,"NR","NR",null,null,null,"NR","NR",null,null,null,"NR","NR",null,null,null,"NR","NR"]
[null,"Roof","Exterior Roof: Thermal Emittance","-","MIN",null,0.9,0.9,null,null,null,0.9,0.9,null,null,null,0.9,0.9,null,null,null,0.9,0.9]
[null,"Fenestration","Exterior Window: U-Value","Btu/(h-ft2-°F)","MAX",null,0.5,0.5,null,null,null,0.37,0.37,null,null,null,0.5,0.5,null,null,null,0.37,0.37]
[null,"Fenestration","Exterior SEW Window: SHGC","-","MAX",null,0.25,0.25,null,null,null,0.25,0.25,null,null,null,0.25,0.25,null,null,null,0.25,0.25]
[null,"Fenestration","Exterior N Window: SHGC","-","MAX",null,0.27500000000000002,0.27500000000000002,null,null,null,0.27500000000000002,0.27500000000000002,null,null,null,0.27500000000000002,0.27500000000000002,null,null,null,0.27500000000000002,0.27500000000000002]
[null,"Fenestration","Exterior Window: WWR","(%)","Max",null,31,31,null,null,null,31,31,null,null,null,31,31,null,null,null,31,31]
[null,"Skylight","Skylight: U-Value","Btu/(h-ft2-°F)","MAX",null,0.75,0.75,null,null,null,0.65,0.65,null,null,null,0.75,0.75,null,null,null,0.65,0.65]
[null,"Skylight","Skylight: SHGC","-","MAX",null,0.35,0.35,null,null,null,0.35,0.35,null,null,null,0.35,0.35,null,null,null,0.35,0.35]
[null,"Skylight","Skylight: Skylight-Roof Ratio","(%)","MAX",null,3,3,null,null,null,3,3,null,null,null,3,3,null,null,null,3,3]
[null,null," "]
["Horizontal Overhang Shade"]
[null,null,"Projection Factor  (-)",null,null,null,0,0,null,null,null,0,0,null,null,null,0,0,null,null,null,0,0]
[]
["Interior Lighting"]
[null,"Lighting","LPD: Space Method","W/ft2","MAX",null,1.2,1.2,null,null,null,1.2,1.2,null,null,null,1.4,1.4,null,null,null,1.4,1.4]
[null,null,null,null,""]
["Exterior Lighting",null,null,null,""]
[null,"Lighting","Total Lighting Allowance (W)","W","MAX",null,880,824,null,null,null,880,824,null,null,null,880,824,null,null,null,880,824]
[null,null,null,null,""]
["Internal Loads"]
[null,"Equipment","Internal Electric Power Density","W/ft2","-",null,1,1,null,null,null,1,1,null,null,null,1,1,null,null,null,1,1]
[]
["HVAC System"]
[null,null,"HVAC system type",null,null,null,"VAV with Reheat, Chilled Water, Electric Resistence","VAV with Reheat, Chilled Water, Electric Resistence",null,null,null,"VAV with Reheat, Chilled Water, Electric Resistence","VAV with Reheat, Chilled Water, Electric Resistence",null,null,null,"VAV with Reheat, Chilled Water, Electric Resistence","VAV with Reheat, Chilled Water, Electric Resistence",null,null,null,"VAV with Reheat, Chilled Water, Electric Resistence","VAV with Reheat, Chilled Water, Electric Resistence"]
[]
[null,null,"Electric Resistence"]
[]
[null,null,"Water Chilling Package Minimum Efficiency:"]
[null,null,"Electrically Operated: "]
[null,null,"Path A: Centrifugal"]
[null,"Chiller","Central Centrifugal Chiller Efficiency: ASHRAE","kW/ton","MAX",null,"0.576 FL, 0.549 IPLV","6.01 COP",null,null,null,"0.576 FL, 0.549 IPLV","6.01 COP",null,null,null,"0.576 FL, 0.549 IPLV","6.01 COP",null,null,null,"0.576 FL, 0.549 IPLV","6.01 COP"]
[null,"Chiller","Central Centrifugal Chiller Efficiency: FEC"]
[]
[null,null,"Air Economizer (Yes, or No):"]
[null,"Air Economizer","North Zone System Economizer: ASHRAE ","-","-",null,"No","No",null,null,null,"Yes","Yes",null,null,null,"No","No",null,null,null,"Yes","Yes"]
[null,"Air Economizer","North Zone System Economizer: FEC","-","-"]
[]
[null,"Air Economizer","South Zone System Economizer: ASHRAE ","-","-",null,"No","No",null,null,null,"Yes","Yes",null,null,null,"No","No",null,null,null,"Yes","Yes"]
[null,"Air Economizer","South Zone System Economizer: FEC","-","-"]
[]
[null,"Air Economizer","East Zone System Economizer: ASHRAE ","-","-",null,"No","No",null,null,null,"Yes","Yes",null,null,null,"No","No",null,null,null,"Yes","Yes"]
[null,"Air Economizer","East Zone System Economizer: FEC","-","-"]
[]
[null,"Air Economizer","West Zone System Economizer: ASHRAE ","-","-",null,"No","No",null,null,null,"Yes","Yes",null,null,null,"No","No",null,null,null,"Yes","Yes"]
[null,"Air Economizer","West Zone System Economizer: FEC","-","-"]
[]
[null,"Air Economizer","Core Zone System Economizer: ASHRAE ","-","-",null,"No","No",null,null,null,"Yes","Yes",null,null,null,"No","No",null,null,null,"Yes","Yes"]
[null,"Air Economizer","Core Zone System Economizer: FEC","-","-"]
[]
[]
["Service Water Heating"]
[null,"SWH","SWH Type",null,null,null,"Storage Water Heater","Storage Water Heater",null,null,null,"Storage Water Heater","Storage Water Heater",null,null,null,"Storage Water Heater","Storage Water Heater",null,null,null,"Storage Water Heater","Storage Water Heater"]
[null,"SWH","Fuel Type",null,null,null,"Gas","Gas",null,null,null,"Gas","Gas",null,null,null,"Gas","Gas",null,null,null,"Gas","Gas"]
[null,"SWH","Thermal Efficiency:"]
[null,"SWH","Size <= 75 kBtu/h, Energy Factor (EF) "," EF ","MIN",null,0.63,0.63,null,null,null,0.63,0.63,null,null,null,0.63,0.63]
[null,"SWH","Size > 75 kBtu/h, Thermal Efficiency (Et) ","%","MIN",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,80,80]
[null,"SWH","Size > 75 kBtu/h, Standby Loss ","Btu/h","MAX"]

{"sheet":"Prototype D7","index":5,"n_rows":89,"n_cols":15,"rows_kept":89,"cut":false,"hidden":false,"merged":[[3,5,3,9],[3,10,3,14]]}
[]
["Output Results for Performance Based Code Compliance Reference Design Tests (Envelope Requirements shall use U-Factor for walls and Roofs, and F-Factor for slab-on-grade floors)"]
[]
[null,null,null,null,null,"Test Run 1 (Climate Zone 1)",null,null,null,null,"Test Run 2 (Climate Zone 2)"]
[null,"TYPE","Description of Components","UNITS","MIN / MAX","Sizing Results","Reference Results for Baseline model (ASHRAE)","Compliance Software Baseline Model Results (ASHRAE)","Reference Results for Baseline model (FEC)","Compliance Software Baseline Model Results (FEC)","Sizing Results","Reference Results for Baseline model (ASHRAE)","Compliance Software Baseline Model Results (ASHRAE)","Reference Results for Baseline model (FEC)","Compliance Software Baseline Model Results (FEC)"]
["Envelope Components"]
[null,"Wall","Exterior Wall: U-Value","Btu/(h-ft2-°F)","MAX",null,0.124,0.124,null,null,null,0.124,0.124]
[null,"Wall","Exterior Wall: Thermal Capacity","(Btu/ft2-°F)",null,null,0.6,0.6,null,null,null,0.6,0.6]
[null,"Wall","Exterior Wall: Solar Reflectance","-","MIN",null,"NA","NA",null,null,null,"NA","NA"]
[null,"Wall","Exterior Wall: Solar Absorptance","-","MAX",null,"NA","NA",null,null,null,"NA","NA"]
[null,"Wall","Exterior Wall: Thermal Emittance","-","MIN",null,"NA","NA",null,null,null,"NA","NA"]
[null,"Floor","Floor Slab-on-grade: Unheated F-factor","Btu/(h-ft-°F)","MAX",null,0.73,0.73,null,null,null,0.73,0.73]
[null,"Floor","Floor Slab-on-grade: Thermal Capacity","(Btu/ft2-°F)",null,null,4.84,4.84,null,null,null,4.84,4.84]
[null,"Roof","Exterior Roof: U-Value","Btu/(h-ft2-°F)","MAX",null,6.3E-2,6.3E-2,null,null,null,6.3E-2,6.3E-2]
[null,"Roof","Exterior Roof: Thermal Capacity","(Btu/ft2-°F)",null,null,1.35,1.35,null,null,null,1.35,1.35]
[null,"Roof","Exterior Roof: Solar Reflectance","-","MIN",null,0.6,0.6,null,null,null,0.6,0.6]
[null,"Roof","Exterior Roof: Solar Absorptance","-","MAX",null,"NR","NR",null,null,null,"NR","NR"]
[null,"Roof","Exterior Roof: Thermal Emittance","-","MIN",null,0.9,0.9,null,null,null,0.9,0.9]
[null,"Floor","Internal Floor: Thermal Capacity","(Btu/ft2-°F)",null,null,4.67,4.67,null,null,null,4.67,4.67]
[null,"Floor","Internal Floor: U-Value","Btu/(h-ft2-°F)","MAX",null,6.8099999999999994E-2,6.8099999999999994E-2,null,null,null,6.8099999999999994E-2,6.8099999999999994E-2]
[null,"Fenestration","Exterior Window Non-Residential: U-Value","Btu/(h-ft2-°F)","MAX",null,0.5,0.5,null,null,null,0.37,0.37]
[null,"Fenestration","Exterior Window Residential: U-Value","Btu/(h-ft2-°F)","MAX",null,0.65,0.65,null,null,null,0.65,0.65]
[null,"Fenestration","Exterior SEW Multi-family  Window: SHGC","-","MAX",null,0.25,0.25,null,null,null,0.25,0.25]
[null,"Fenestration","Exterior N Multi-family  Window: SHGC","-","MAX",null,0.25,0.25,null,null,null,0.25,0.25]
[null,"Fenestration","Exterior SEW Non-Residential Window: SHGC","-","MAX",null,0.25,0.25,null,null,null,0.25,0.25]
[null,"Fenestration","Exterior N Non-Residential Window: SHGC","-","MAX",null,0.25,0.25,null,null,null,0.25,0.25]
[null,"Fenestration","Exterior Window: WWR: Non-Residential","(%)","MAX",null,40,40,null,null,null,40,40]
[null,"Fenestration","Exterior Window: WWR: Multi-family ","(%)","MAX",null,40,40,null,null,null,40,40]
[]
["Interior Lighting"]
[null,"Lighting","LPD - Space Method: Retail","W/ft2","MAX",null,1.7,1.7,null,null,null,1.7,1.7]
[null,"Lighting","LPD - Space Method: Office","W/ft2","MAX",null,1.1000000000000001,1.1000000000000001,null,null,null,1.1000000000000001,1.1000000000000001]
[null,"Lighting","LPD - Space Method:Dormitory for Multi-family Units","W/ft2","MAX",null,1.1100000000000001,1.1100000000000001,null,null,null,1.1100000000000001,1.1100000000000001]
[null,"Lighting","LPD - Space Method: Corridor for Multi-family Hallway","W/ft2","MAX",null,0.5,0.5,null,null,null,0.5,0.5]
[]
["Exterior Lighting",null,null,null,""]
[null,"Lighting","Total Lighting Allowance","W","MAX",null,1450,1420,null,null,null,1450,1420]
[]
["Internal Loads"]
[null,"Equipment","Internal Electric Power Density: Retail","W/ft2","-",null,1,1,null,null,null,1,1]
[null,"Equipment","Internal Electric Power Density: Office","W/ft2","-",null,1.5,1.5,null,null,null,1.5,1.5]
[null,"Equipment","Internal Electric Power Density: Multi-family Units","W/ft2","-",null,0.5,0.5,null,null,null,0.5,0.5]
[null,"Equipment","Internal Electric Power Density: Multi-family Hallway","W/ft2","-",null,0.2,0.2,null,null,null,0.2,0.2]
[null,null,null,null,""]
[]
["HVAC System"]
[null,null,"HVAC System Type"]
[null,null,"Retail Floor",null,null,null,"Packaged Roof Top Heat Pump","Packaged Roof Top Heat Pump",null,null,null,"Packaged Roof Top Heat Pump","Packaged Roof Top Heat Pump"]
[null,null,"Office Floors",null,null,null,"Packaged VAV with PFP boxes","Packaged VAV with PFP boxes",null,null,null,"Packaged VAV with PFP boxes","Packaged VAV with PFP boxes"]
[null,null,"Multi-Family Floors",null,null,null,"Packaged Terminal Heat Pump","Packaged Terminal Heat Pump",null,null,null,"Packaged Terminal Heat Pump","Packaged Terminal Heat Pump"]
[]
[]
[null,null,"Heating Efficiency:"]
[null,"Retail - Heating HP","Zone System Efficiency: ASHRAE","COP","COP",null,2.91,2.91,null,null,null,2.91,2.91]
[null,"Office - Heating","Electric Resistenance "]
[null,"Mutli Family - Heating HP","Zone System Efficiency: ASHRAE","COP","COP",null,3.1,3.1,null,null,null,3.1,3.1]
[]
[null,null,"Cooling Efficiency:"]
[null,"Retail - Cooling HP","Zone System Efficiency: ASHRAE","EER","EER",null,9.9600000000000009,9.9600000000000009,null,null,null,9.9600000000000009,9.9600000000000009]
[null,"Office - Cooling DX","Zone System Efficiency: ASHRAE","EER","EER",null,9.5,9.5,null,null,null,9.5,9.5]
[null,"Mutli Family - Cooling HP","Zone System Efficiency: ASHRAE","EER","EER",null,9.1,9.1,null,null,null,9.1,9.1]
[]
[]
[null,null,"Air Economizer Requirement (Yes, or No):"]
[null,"Air Economizer","Retail North Zone System Economizer: ASHRAE ","-","-",null,"No","No",null,null,null,"Yes","Yes"]
[null,"Air Economizer","Retail North Zone System Economizer: FEC ","-","-"]
[]
[null,"Air Economizer","Retail South Zone System Economizer: ASHRAE ","-","-",null,"No","No",null,null,null,"Yes","Yes"]
[null,"Air Economizer","Retail South Zone System Economizer: FEC ","-","-"]
[]
[null,"Air Economizer","Retail East Zone System Economizer: ASHRAE ","-","-",null,"No","No",null,null,null,"Yes","Yes"]
[null,"Air Economizer","Retail East Zone System Economizer: FEC ","-","-"]
[]
[null,"Air Economizer","Retail West Zone System Economizer: ASHRAE ","-","-",null,"No","No",null,null,null,"Yes","Yes"]
[null,"Air Economizer","Retail West Zone System Economizer: FEC ","-","-"]
[]
[null,"Air Economizer","Retail Core Zone System Economizer: ASHRAE ","-","-",null,"No","No",null,null,null,"Yes","Yes"]
[null,"Air Economizer","Retail Core Zone System Economizer: FEC ","-","-"]
[]
[null,"Air Economizer","Office Second Floor System Economizer: ASHRAE ","-","-",null,"No","No",null,null,null,"Yes","Yes"]
[null,"Air Economizer","Office Second Floor System Economizer: FEC ","-","-"]
[]
[null,"Air Economizer","Office Third Floor System Economizer: ASHRAE ","-","-",null,"No","No",null,null,null,"Yes","Yes"]
[null,"Air Economizer","Office Third Floor System Economizer: FEC ","-","-"]
[]
[]
["Elevator Motor"]
[null,null,"Electric Motor Power (HP) ","HP","MAX",null,20,20,null,null,null,20,20]
[null,null,"Electric Motor Efficiency (%) ","%","MAX",null,90,90,null,null,null,90,90]