## Slide 1: EVALUATION OF DRAFTSTOPPING WITHIN TYPE V COMBUSTIBLE CONCEALED ATTIC SPACES
Prepared by:
Steve Welsh
June 27, 2014

## Slide 2: Outline
Literature Review
Field Assessment
Discussion
Gap Assessment

## Slide 3: Current Code
Group R-2 Apartments:
  Required if three or more dwelling units
  subdivide into areas not exceeding 3,000 sq ft or above every two dwelling units, whichever is smaller

## Slide 4: Material Requirements
Draftstopping materials must not be less than:
  0.5-inch gypsum board
  0.375-inch wood structural panel
  0.375-inch particleboard
  1-inch nominal lumber
  cement fiberboard
  batts or blankets of mineral wool or glass fiber
  other approved materials adequately supported.

## Slide 5: Material Requirements
Must extend to the underside of the roof sheathing.
The integrity of draftstops must be maintained.
Openings in the partitions must be protected by self-closing doors with automatic latches.

## Slide 6: Penetrations and Joints
No specific requirements for draftstopping

## Slide 7: Pedestal Buildings
Type VA construction (1-hr rated) allows four stories.
Additionally, IBC Section 510.4 allows a Group S-2 parking garage beneath Group R if the parking garage is open or constructed of Type I (noncombustible) construction.

## Slide 8: Legacy Code History
1927 Edition of the Uniform Building Code (UBC), which was also the first edition of the code
Similar requirements to current codes

## Slide 9: Non-IBC Approaches
Similar requirements to IBC
Fill space with noncombustible materials

## Slide 10: Technical Materials
Limited

## Slide 11: Technical Materials – Calculated Ratings
0.375-inch particleboard
  5 minutes
0.5-inch gypsum board
  10 minutes
  20 minutes with Type X

## Slide 12: Incident Data
Limited
Florida
  Lightning Strikes
NFPA

## Slide 13: Firefighting
Limited Information

## Slide 14: Firefighting
More challenging to access for manual suppression
Hidden fire resulting in delayed detection
Increased fuel load
Rapid fire spread
Accumulation of fire gases
Increased backdraft potential
Direct degradation to structure
Early structural failure

## Slide 15: Firefighting
Indirect approaches to attacking fire

## Slide 16: Field Assessment - Materials
Plywood (wood structural panel) is the most common draftstopping material
Most draftstopping was installed parallel to the trusses.

## Slide 17: Field Assessment - Materials

## Slide 18: Field Assessment - Materials

## Slide 19: Field Assessment - Materials

## Slide 20: Field Assessment - Materials

## Slide 21: Field Assessment - Materials

## Slide 22: Field Assessment - New
Only 1 of the 7 buildings under construction had draftstopping that was deficient.

## Slide 23: Field Assessment - New

## Slide 24: Field Assessment - Existing
All of the existing buildings were draftstopped along every unit separation, even though this was historically not required.

## Slide 25: Field Assessment - Existing

## Slide 26: Field Assessment - Existing

## Slide 27: Field Assessment - Hotels
The two existing R-2 Hotels were both sprinkler protected in the attics, though this is not required.
The two existing R-2 Hotels had draftstopping in the attics, though this was not required due to the sprinkler protection. However, it was not maintained in one of the properties.

## Slide 28: Field Assessment - Business
One of 2 Business buildings was observed without draftstopping.
The Business building with draftstopping had major deficiencies

## Slide 29: Field Assessment - Business

## Slide 30: Field Assessment - Other
Draftstopping is often desired over unit separations to mitigate security concerns.
Lightning strikes can create both instantaneous fires and smoldering (slow-developing) fires.
There were few properties constructed before 1990 in the region where the surveys were conducted.

## Slide 31: Field Assessment - Other

## Slide 32: Field Assessment - Other

## Slide 33: Field Assessment - Other
Type III construction with exterior walls of fire retardant-treated wood.
Interstitial sprinklers still require draftstopping.

## Slide 34: Field Assessment - Other

## Slide 35: Field Assessment - Other

## Slide 36: Field Assessment - Other

## Slide 37: Discussion
The materials currently allowed to serve as draftstopping are common building materials.

## Slide 38: Discussion
There is currently no documented basis for the legacy code requirements.

## Slide 39: Discussion
NFPA 13R versus NFPA 13 sprinkler protection for five-level pedestal buildings should be clarified in the next edition of the Florida Building Code if the Florida Building Commission wants to deviate from the national code.

## Slide 40: Gap Assessment
Prepare a code change to allow only gypsum (Type X).

## Slide 41: Gap Assessment
Prepare a code change as follows: “Draftstopping must be installed parallel to the trusses and aligned with the unit separation walls unless provided above a corridor wall.”

## Slide 42: Gap Assessment
Surveying buildings in a more established and dynamic urban area.

## Slide 43: Gap Assessment
Research options for a limited sprinkler system in attic in lieu of draftstopping.
Full-scale fire testing

## Slide 44: Questions?
Follow us on LinkedIn
  Steve Welsh, P.E.
  (Registered in MD, DE)
  swelsh@koffel.com
  Koffel Associates, Inc.
  8815 Centre Park Drive, Suite 200
  Columbia, MD 21045-2107
  410-750-2246
  www.koffel.com