## Parametric Runs
Test Cases for Florida Code Compliance | [10 empty] | Example Qualitative Tests
Run | Purpose | Prototype | Climate | Occupancy Option | Lighting Power Density, W/ft2 | Equipment Power Density, W/ft2 | Occupancy, Person/1000 ft2 | MIN OA Requirement, cfm/ft2 | HVAC System | Default Schedules | Opaque Envelope Thermal Capacity | Envelope Assembly U-value, and F-Factor | Envelope Substitution | Fenestration U-value | Fenestration SHGC | Fenestration SHGC Adjustment | Window-Wall Ratio | Fenestration Area Adjustment | Fenestration Criteria by Space-Conditioning Category | Skylights U-value | Skylight SHGC | Skylights Area Maximum | Skylight-Roof Area Ratio | Overhangs Projections | Interior Lighting Assumptions | Exterior Lighting Assumptions | Internal Equipment Power Density | HVAC Mapping | HVAC Efficiency | Service Water Equipment Type and Efficiency | Economizer | Elevators | Fan BHP | Schedules | Modeling Unconditioned Spaces | Check Prescribed Modeling Assumptions | Performance Method | Prescriptive Method | Envelope Trade-Off Option Method
1 | Code Compliance | A1 | Miami | Office | 1 | 1 | 5 | 0.1 | PSZ-AC | Yes | P | P | P | P | P |  | P |  | P | P | P | P | P |  | P | P | P | P | P | P | P |  |  | P | na |  | P | P
2 | Code Compliance | A1 | Orlando | Office | 1 | 1 | 5 | 0.1 | PSZ-AC | Yes | P | P | P | P | P |  | P |  | P | P | P | P | P |  | P | P | P | P | P | P | P |  |  | P | na |  | P | P
3 | Code Compliance | A3 | Miami | Office | 1 | 1 | 5 | 0.1 | PVAV | Yes | P | P | P | P | P |  | P |  | P | [5 empty] | P | P | P | P | P | P | P | P |  | P | na |  | P
4 | Code Compliance | A3 | Orlando | Office | 1 | 1 | 5 | 0.1 | PVAV | Yes | P | P | P | P | P |  | P |  | P | [5 empty] | P | P | P | P | P | P | P | P |  | P | na |  | P
5 | Code Compliance | A20 | Miami | Office | 1 | 1 | 5 | 0.1 | VAV | Yes | P | P | P | P | P |  | P | P | P | [5 empty] | P | P | P | P | P | P | P | P |  | P | na |  | P
6 | Code Compliance | A20 | Orlando | Office | 1 | 1 | 5 | 0.1 | VAV | Yes | P | P | P | P | P |  | P | P | P | [5 empty] | P | P | P | P | P | P | P | P |  | P | na |  | P
7 | Code Compliance | B1 | Miami | Retail | 1.9 | 0.9 | 13.1 | 0.27 | PSZ-HP | Yes | P | P | P | P | P | P | P |  | P | P | P | P | P | P | P | P | P | P | P | P | P |  |  | P | na |  | P
8 | Code Compliance | B1 | Orlando | Retail | 1.9 | 0.9 | 13.1 | 0.27 | PSZ-HP | Yes | P | P | P | P | P | P | P |  | P | P | P | P | P | P | P | P | P | P | P | P | P |  |  | P | na |  | P
9 | Code Compliance | B1 | Miami | Supermarket | 1.9 | 1.28 | 7.24 | 0.27 | PSZ-AC | Yes | P | P | P | P | P | P | P |  | P | P | P | P | P | P | P | P | P | P | P | P | P |  |  | P | na |  | P
10 | Code Compliance | B1 | Orlando | Supermarket | 1.9 | 1.28 | 7.24 | 0.27 | PSZ-AC | Yes | P | P | P | P | P | P | P |  | P | P | P | P | P | P | P | P | P | P | P | P | P |  |  | P | na |  | P
11 | Code Compliance | C1 | Miami | Manufacturing | 1 | 1.6 | 1.3 | 0.12 | PSZ-AC | Yes | P | P | P | P | P | P | P |  | P | P | P | P | P | P | P | P | P | P | P | P | P |  |  | P | na |  | P | P
12 | Code Compliance | C1 | Orlando | Manufacturing | 1 | 1.6 | 1.3 | 0.12 | PSZ-AC | Yes | P | P | P | P | P | P | P |  | P | P | P | P | P | P | P | P | P | P | P | P | P |  |  | P | na |  | P | P
13 | Code Compliance | C1 | Miami | Warehouse | 0.58 | 1 | 0.1 | 0.05 | PSZ-HP | Yes | P | P | P | P | P | P | P |  | P | P | P | P | P | P | P | P | P | P | P | P | P |  |  | P | na |  | P | P
14 | Code Compliance | C1 | Orlando | Warehouse | 0.58 | 1 | 0.1 | 0.05 | PSZ-HP | Yes | P | P | P | P | P | P | P |  | P | P | P | P | P | P | P | P | P | P | P | P | P |  |  | P | na |  | P | P
15 | Code Compliance | D7 | Miami | Retail | 1.38 | 1.5 | 13.1 | 0.27 | 4PipeFanCoil | Yes | P | P | P | P | P | P | P |  | P |  |  |  |  | P | P | P | P | P | P | P | P | P |  | P | na |  | P
|  | D7 | Miami | Office | 1.16 | 1 | 5 | 0.1 | VAV | Yes | P | P | P | P | P | P | P |  | P |  |  |  |  | P | P | P | P | P | P | P | P | P |  | P | na |  | P
|  | D7 | Miami | Apartment Units | 1.65 | 1.65 | 2.64 | 0.05 | 4PipeFanCoil | Yes | P | P | P | P | P | P | P |  | P | [5 empty] | P | P | P | P | P | P | P | P |  | P | na |  | P
|  | D7 | Miami | Apartment Hallways | 0.8 | 0.7 | - | 0.05 | None | Yes | P | P | P | P | P | P | P |  | P | [5 empty] | P | P | P | P | P | P | P | P |  | P | P |  | P
16 | Code Compliance | D7 | Orlando | Retail | 1.38 | 1.5 | 13.1 | 0.27 | 4PipeFanCoil | Yes | P | P | P | P | P | P | P |  | P |  |  |  |  | P | P | P | P | P | P | P | P | P |  | P | na |  | P
|  | D7 | Orlando | Office | 1.16 | 1 | 5 | 0.1 | VAV | Yes | P | P | P | P | P | P | P |  | P |  |  |  |  | P | P | P | P | P | P | P | P | P |  | P | na |  | P
|  | D7 | Orlando | Apartment Units | 1.65 | 1.65 | 2.64 | 0.05 | 4PipeFanCoil | Yes | P | P | P | P | P | P | P |  | P | [5 empty] | P | P | P | P | P | P | P | P |  | P | na |  | P
|  | D7 | Orlando | Apartment Hallway | 0.8 | 0.7 | - | 0.05 | None | Yes | P | P | P | P | P | P | P |  | P | [5 empty] | P | P | P | P | P | P | P | P |  | P | P |  | P
17 | Code Compliance | E1 | Miami | Sales / Warehouse | na | na | na | na | na | na | P | P | P | P | P | P | P |  | P | P | P | P | P | [15 empty] | P
18 | Code Compliance | E1 | Orlando |  | na | na | na | na | na | na | P | P | P | P | P | P | P |  | P | P | P | P | P | [15 empty] | P

## Prototype Data
Feature |  | Units
Program
| Prototype Name |  | A1 | A3 | A20 | B1 | C1 | D7 |  |  |  | E1
| Occupancy |  | Office | Office | Office | See Parametric Runs | See Parametric Runs | Retail | Office | Multi-Family | Total | Retail / Warehouse
Form
| Floor Area (ft²) |  | 22500 | 67500 | 450000 | 40000 | 160000 | 13200 | 27000 | 49200 | 89400 | 90000
| Building Shape |  | Square | Square | Square | Square | Square | Rectangle | Rectangle | H | n.a. | Rectangle
| Number of Floors |  | 1 | 3 | 20 | 1 | 1 | 1 | 2 | 4 | 7 | 1
| Thermal Zoning |  | 5/floor | 5/floor | 5/floor | 5/floor | 5/floor |  |  |  |  | 2
| Perimeter Zone Depth (ft) |  | 15 | 15 | 15 | 15 | 15 | n.a. | n.a. | n.a. | n.a. | n.a.
| Plenum |  | No | Yes | Yes | Yes | No | Yes | Yes | No | n.a. | n.a.
| Height Flr-Flr |  | 12 | 12 | 12 | 18 | 24 | 11' 4" | 12' 4" | 10' 3" | n.a. | 20 / 30
| Height Ceiling |  | 8.5 | 8.5 | 8.5 | 14 | 24 | 9' 0" | 9' 0" | 10' 3" | n.a. | n.a.
| Height Plenum |  | 3.5 | 3.5 | 3.5 | 4 | 0 | 2' 4" | 3' 4" | n.a. | n.a. | n.a.
Roof
| Construction | Ref | See Const. Data | See Const. Data | See Const. Data | See Const. Data | See Const. Data | See Const. Data | See Const. Data | See Const. Data | See Const. Data | See Const. Data
| Area | ft² | 22500 | 22500 | 22500 | 40000 | 160000 | 0 | 1200 | 12300 | 13500 | 90000
Walls
| Construction | Ref | See Const. Data | See Const. Data | See Const. Data | See Const. Data | See Const. Data | See Const. Data | See Const. Data | See Const. Data | See Const. Data | See Const. Data
| Front (south) Area | ft² | 1800 | 5400 | 36000 | 3600 | 9600 | 1700 | 3700 | 6600 | 12000 | 12375
| Right (east) Area | ft² | 1800 | 5400 | 36000 | 3600 | 9600 | 1020 | 2220 | 11880 | 15120 | 6000
| Back (north) Area | ft² | 1800 | 5400 | 36000 | 3600 | 9600 | 1700 | 3700 | 6600 | 12000 | 12375
| Left (west) Area | ft² | 1800 | 5400 | 36000 | 3600 | 9600 | 1252.3333 | 2220 | 11880 | 15352.3333 | 6000
| Total Area | ft² | 7200 | 21600 | 144000 | 14400 | 38400 | 5672.3333 | 11840 | 36960 | 54472.3333 | 36750
Foundation
| Foundation Type |  | Slab-On-Grade | Slab-On-Grade | Slab-On-Grade | Slab-On-Grade | Slab-On-Grade | Slab-On-Grade | n.a. | n.a. |  | Slab-On-Grade
| Construction |  | See Const. Data | See Const. Data | See Const. Data | See Const. Data | See Const. Data |  |  |  |  | See Const. Data
| Area |  | 22500 | 22500 | 22500 | 40000 | 160000 | 13500 | 0 | 0 | 13500 | 90000
| Perimeter |  | 600 | 600 | 600 | 800 | 1600 | 480 | 0 | 0 | 480 | 1300
Interior Partitions
| Construction |  | See Const. Data | See Const. Data | See Const. Data | See Const. Data | See Const. Data | See Const. Data | See Const. Data | See Const. Data | See Const. Data | n.a.
| Area |  | 4801.2489 | 14403.7468 | 96024.9783 | 10707.9394 | 37556.4675
Internal Mass
Construction
Dimensions - Total Area (ft2)
Thermal diffusivity (ft2/s)
Air Barrier System
Infiltration (ACH)
Windows
| Construction | Ref | See Const. Data | See Const. Data | See Const. Data | See Const. Data | See Const. Data | See Const. Data | See Const. Data | See Const. Data | See Const. Data | See Const. Data
| Operable Area |  | None | None | None | None | None | None | None |  |  | None
| Front (south) Area | ft² | 550 | 1650 | 25500 | 640 | 1280 | 1350 | 960 | 1728 | 4038 | 400
| Right (east) Area | ft² | 550 | 1650 | 25500 | 0 | 0 | 414 | 576 | 1536 | 2526 | 0
| Back (north) Area | ft² | 550 | 1650 | 25500 | 0 | 0 | 560.25 | 960 | 1728 | 3248.25 | 400
| Left (west) Area | ft² | 550 | 1650 | 25500 | 0 | 0 | 810 | 576 | 1536 | 2922 | 1200
| Total Area | ft² | 2200 | 6600 | 102000 | 640 | 1280 | 3134.25 | 3072 | 6528 | 12734.25 | 2000
| Front (south) WWR | Ratio | 0.30556 | 0.30556 | 0.70833 | 0.17778 | 0.13333 | 0.79412 | 0.25946 | 0.26182 | 0.3365 | 0.032323
| Right (east) WWR | Ratio | 0.30556 | 0.30556 | 0.70833 | 0 | 0 | 0.40588 | 0.25946 | 0.12929 | 0.16706 | 0
| Back (north) WWR | Ratio | 0.30556 | 0.30556 | 0.70833 | 0 | 0 | 0.32956 | 0.25946 | 0.26182 | 0.27069 | 0.032323
| Left (west) WWR | Ratio | 0.30556 | 0.30556 | 0.70833 | 0 | 0 | 0.64679 | 0.25946 | 0.12929 | 0.19033 | 0.2
| Total WWR | Ratio | 0.30556 | 0.30556 | 0.70833 | 0.044444 | 0.033333 | 0.55255 | 0.25946 | 0.17662 | 0.23377 | 0.054422
Skylights
| Area | ft² | 2250 | None | None | 2000 | 3200 | None | None | None | None | 20
| Skylights Assembly U-value | Btu/h.ft2.oF | 1 |  |  | 1 | 1 |  |  |  |  | 1.27
| Skylights Assembly SHGC | - | 0.25 |  |  | 0.25 | 0.25 |  |  |  |  | 0.68
| Skylights Assembly Tvis |  | - | [8 empty] | 0.66
Horizontal Overhang Shade
| Front (South) Horizontal Depth | ft | None | None | None | 8 | 8 | 10 | 5 | None |  | None
| Front (South) Projection Factor | - | 0 | 0 | 0 | 1 | 1 | 1.1111 | 0.55556 | 0 |  | 0
| Right (East) Horizontal Depth | ft | None | None | None | None | None | 10 | 5 | None |  | None
| Right (East) Projection Factor | - | 0 | 0 | 0 | 0 | 0 | 1.1111 | 0.55556 | 0 |  | 0
| Left (West) Horizontal Depth | ft | None | None | None | None | None | 10 | 5 | None |  | None
| Left (West) Projection Factor | - | 0 | 0 | 0 | 0 | 0 | 1.1111 | 0.55556 | 0 |  | 0
| Back (North) Horizontal Depth | ft | None | None | None | None | None | None | None | None |  | None
| Back (North) Projection Factor | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
Interior Lighting
| Lighting Power Density | W/ft² | See Parametric Runs | See Parametric Runs | See Parametric Runs | See Parametric Runs | See Parametric Runs | See Parametric Runs | See Parametric Runs | See Parametric Runs | See Parametric Runs | n.a.
| Schedule |  | Default | Default | Default | Default | Default | See Parametric Runs | See Parametric Runs | See Parametric Runs | See Parametric Runs | n.a.
Exterior Lighting
| Total Lighting Allowance | W | 846 | 846 | 1420 | 712 | 824 | 1420 | None | None | 1420 | n.a.
| Schedule |  | When Sun is off | When Sun is off | When Sun is off | When Sun is off | When Sun is off | When Sun is off | When Sun is off | When Sun is off | When Sun is off | n.a.
Equipment
| Equipment Power Density |  | See Parametric Runs | See Parametric Runs | See Parametric Runs | See Parametric Runs | See Parametric Runs | See DetailsD7 | See DetailsD7 | See DetailsD7 | See DetailsD7 | n.a.
| Refrigeration Power Density (W/ft2) |  | None | None | None | 0.14 (Supermarket only) | None | None | None | None | None | n.a.
| Number of Elevators |  | 0 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 2 | n.a.
| Elevator Electric Motor (General Purpose) Peak Power | HP | 0 | 7.5 | 20 | 0 | 0 | 0 | 0 | 0 | 15 | n.a.
| Elevator Electric Motor (General Purpose) Efficiency | % |  | 88 | 92 | 0 | 0 | 0 | 0 | 0 | 90 | n.a.
| Schedule |  | None | Default | Default | None | None | None | None | None | Default | n.a.
Occupancy | [7 empty] | `
| Occupants | Person/1000 ft2 | 5 | 5 | 5 | See Parametric Runs | See Parametric Runs | 13.1 | 5 | 2.64 | 4.55 | n.a.
| Schedule |  | See Parametric Runs | See Parametric Runs | See Parametric Runs | See Parametric Runs | See Parametric Runs | See Parametric Runs | See Parametric Runs | See Parametric Runs | See Parametric Runs | n.a.
Ventilation Air Requirement
| Minimum Outdoor Air Amount | cfm/ft2 | 0.1 | 0.1 | 0.1 | See Parametric Runs | See Parametric Runs | 0.27 | 0.1 | 0.05 | 0.09 | n.a.
| Schedule |  | Default | Default | Default | Default | Default | Default | Default | Default | Default | n.a.
Infiltration Air
| Normalized Infiltration Rate at 0.016 in W.g. (4Pa), Peak | cfm/ft2 | 0.0177 | 0.0052 | 0.0061 | 0.0092 | 0.0073 | 0.0057 | 0.0051 | 0.0049 | 0.0049 | n.a.
| Infiltration Rate Per floor, Peak | cfm | 127.4 | 37 | 43.5 | 132.7 | 281.4 | 33.3 | 29.8 | 44.9 | 38.9 | n.a.
| Schedule |  | Default | Default | Default | Default | Default | Default | Default | Default | Default | n.a.
HVAC
| DX Cooling SEER, Capacity < 65 kBtu/h | Btu/W-h | 19 | None | None | 17 | 15 | None | None | None | None | n.a.
| DX Cooling EER / IEER, Capacity >= 65 kBtu/h | Btu/W-h | 12.8 / 12.9 | 12.8 / 12.9 | None | 12.6 / 12.7 | 12.2 / 12.3 | None | None | None | None | n.a.
| Chiller Cooling Efficiency (EIR / IPLV) | kW/ton | None | None | 0.60 / 0.52 | None | None | 0.62 / 0.54 | 0.62 / 0.54 | 0.62 / 0.54 | 0.62 / 0.54 | n.a.
| Chiller Compressor Type | - | None | None | Centrifugal | None | None | Reciprocating | Reciprocating | Reciprocating | Reciprocating | n.a.
| Thermal Efficiency (Gas / Elecric ) | - | 0.9 / 1 | 0.9 | 0.9 | 0.9 / 1 | 0.9 / 1 | 0.86 | 0.86 | 0.86 | 0.86 | n.a.
| DX Heating HSPF, Cooling Capacity < 65 kBtu/h | Btu/W-h | None | None | None | 8.4 | 8.2 | None | None | None | None | n.a.
| DX Heating COP, Cooling Capacity >= 65 kBtu/h, 47F db/43F wb | - | None | None | None | 3.5 | 3.4 | None | None | None | None | n.a.
| DX Heating COP, Cooling Capacity >= 65 kBtu/h, 17F db/15F wb | - | None | None | None | 2.4 | 2.3 | None | None | None | None | n.a.
| Leaving Chilled Water Temperature (ºF ) | ºF | None | None | 44 | None | None | 44 | 44 | 44 | 44 | n.a.
| Hot Water Coil Rated Inlet Temperature (ºF ) | ºF | None | 180 | 180 | None | None | 180 | 180 | 180 | 180 | n.a.
| Space Type |  | Conditioned | Conditioned | Conditioned | Conditioned | Conditioned | Conditioned | Conditioned | Conditioned | See DetailsD7 | conditioned / Semiheated
| System Type |  | See Parametric Runs | See Parametric Runs | See Parametric Runs | See Parametric Runs | See Parametric Runs | See Parametric Runs | See Parametric Runs | See Parametric Runs | n.a. | n.a.
| Fan Efficiency / Motor Efficiency |  | 0.6 / 0.9 | 0.6 / 0.9 | 0.6 / 0.9 | 0.6 / 0.9 | 0.6 / 0.9
Service Water Heating
| SWH Type |  | Storage Water Heater | Storage Water Heater | Central Hot Water Boiler | Storage Water Heater | Storage Water Heater | Central Hot Water Boiler | Central Hot Water Boiler | Central Hot Water Boiler | Central Hot Water Boiler | n.a.
| Fuel |  | Electric | Gas | Oil | Electric | Gas | Gas | Gas | Gas | Gas | n.a.
| Size <= 12 kW, Energy Factor (EF) | - | 0.89 | NA | NA | 0.89 | NA | NA | NA | NA | NA | n.a.
| Size > 12 kW, Size > 20 gal, Standby Loss Max Btu/h | Btu/h | 290 | NA | NA | 290 | NA | NA | NA | NA | NA | n.a.
| Size <= 75 kBtu/h, Energy Factor (EF) | EF | NA | 0.58 | NA | NA | 0.58 | NA | NA | NA | NA | n.a.
| Size > 75 kBtu/h, Thermal Efficiency | % | NA | 84 | NA | NA | 84 | NA | NA | NA | NA | n.a.
| Boiler Thermal Efficiency (%) | % | NA | NA | 90 | NA | NA | 86 | 86 | 86 | 86 | n.a.
| Temperature Setpoint (ºF ) | ºF | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | n.a.
| Storage Size Per Floor (gal) / Number of Units |  | 80 / 2 | 80 / 2 | None | 80 / 4 | 80 / 3 | None | None | None | None | n.a.
n.a.
Schedules (defaults)
| Occupancy |  | Default | Default | Default | Default | Default | Default | Default | Default | Default | n.a.
| Lighting |  | Default | Default | Default | Default | Default | Default | Default | Default | Default | n.a.
| HVAC System Operation |  | Default | Default | Default | Default | Default | Default | Default | Default | Default | n.a.
| Service Hot Water |  | Default | Default | Default | Default | Default | Default | Default | Default | Default | n.a.
| Elevators |  | None | Default | Default | None | None | Default | Default | Default | Default | n.a.

## Construction Data
Construction Details
Prototype Building A1 (Wood-Framed Equivalent Wall)
| Layers (outer to inner) | Thickness, | Conductivity | Density | Specific heat | Thermal Resistance
|  | in | Btu-in/(h×ft2×°F) | lbm/ft3 | Btu/(lbm×°F) | (h·ft2·°F)/Btu
External Wall
| Built-in Wood Framed Wall | 7.87 | 0.46 | 26.1 | 0.23 | 17.1087
Ceiling
| Ceiling Gypsum | 0.5 | 1.11 | 49 | 0.2 | 0.45045
Roof
| Built-in Roof | 6.77 | 0.37 | 22.5 | 0.22 | 18.2973
Partition Wall
| Gypsum Board Partition Wall | 1 | 1.11 | 50 | 0.2 | 0.9009
Floor
| Slab-on-Grade | 4 | 9.08 | 140 | 0.2 | 0.44053
Exterior wood stud wall with R-13 and no continuous insulation
Roof has continuous insulation of R-17
Floor has no insulation
Window (Non-Metal Framing)
Reflective Double Glazing, 0.236 in glass thickness. Assembly U-value 0.90 / SHGC 0.19 for climate zone 1, and U-value 0.60/ SHGC 0.19 for climate zone 2
Prototype Building A3 and A20 (Steel-Framed Equivalent Wall)
| Layers (outer to inner) | Thickness, | Conductivity | Density | Specific heat | Thermal Resistance
|  | in | Btu-in/(h×ft2×°F) | lbm/ft3 | Btu/(lbm×°F) | (h·ft2·°F)/Btu
External Wall
| Composite stell-framed Wall | 8.27 | 0.54 | 20.5 | 0.22 | 15.31
Ceiling
| Gypsum | 0.5 | 1.11 | 49 | 0.2 | 0.45
Roof
| Composite Roof | 6.46 | 0.35 | 23.9 | 0.21 | 18.46
Internal Floor
| Int-Floor | 8.27 | 0.62 | 74.9 | 0.19 | 13.34
Partition Wall
| Gypsum Board | 1 | 1.11 | 50 | 0.2 | 0.9
Floor
| Slab-on-grade | 4 | 9.08 | 140 | 0.2 | 0.44
Window (Metal Framing)
Reflective Double Glazing, 0.236 in glass thickness. Assembly U-value 0.90 / SHGC 0.20 for climate zone 1, and U-value 0.60/ SHGC 0.20 for climate zone 2
Prototype Building B1 and C1 (Mass Equivalent Wall) ( C1 does not have Celing)
| Layers (outer to inner) | Thickness, | Conductivity | Density | Specific heat | Thermal Resistance
|  | in | Btu-in/(h×ft2×°F) | lbm/ft3 | Btu/(lbm×°F) | (h·ft2·°F)/Btu
External Wall
| CMU Mass Wall | 10 | 5.06 | 129 | 0.2 | 1.98
Ceiling
| Gypsum Board | 0.5 | 1.11 | 49 | 0.2 | 0.45
Roof
| Composite Roof | 6.9 | 0.32 | 23.4 | 0.21 | 21.56
Partition Wall
| Gypsum Board | 1 | 1.11 | 50 | 0.2 | 0.9
Floor
| Slab-on-grade | 4.3 | 2.61 | 127.9 | 0.18 | 1.65
Exterior Wall concrete block with filled core but no interior or exterior insulation
Roof has continuous insulation of R-20
Floor has no insulation
Fenestration (Metal Framing, Front Door)
Double Glazing, 0.236 in glass thickness. Assembly U-value 0.9 / SHGC 0.50 for climate zone 1, and U-value 0.60/ SHGC 0.40 for climate zone 2
Prototype Building D7 (Steel-Framed Equivalent Wall)
| Layers (outer to inner) | Thickness, | Conductivity | Density | Specific heat | Thermal Resistance
|  | in | Btu-in/(h×ft2×°F) | lbm/ft3 | Btu/(lbm×°F) | (h·ft2·°F)/Btu
External Wall
| Composite steel-framed Wall | 11.54 | 0.67 | 40.8 | 0.23 | 17.33
Ceiling
| Gypsum | 0.5 | 1.11 | 49 | 0.2 | 0.45
Roof
| Composite Roof | 6.46 | 0.35 | 23.9 | 0.21 | 18.62
Internal Floor
| Int-Floor | 8.35 | 0.62 | 74.9 | 0.19 | 13.37
Partition Wall
| Gypsum Board | 1 | 1.11 | 50 | 0.2 | 0.9
Floor
| Slab-on-grade | 4 | 9.08 | 140 | 0.2 | 0.44
Window (Metal Framing)
See DetailD7 tab
Prototype Building E1 (Mass Wall): Envelope Trade Off Option
| Building Envelope Components | Units | Climate Zone 1 | Climate Zone 2
| Roof Insulated: U-Value | Btu/(h·ft2·°F) | 0.063 | 0.048
| Roof Insulated: R-Value | (h·ft2·°F)/Btu | R-15 | R-20
| Roof Insulated: HC | (Btu/ft2·°F) | 12 | 12
| Exterior Wall Insulated: U-Value | Btu/(h·ft2·°F) | 0.078 | 0.078
| Exterior Wall Insulated: R-Value | (h·ft2·°F)/Btu | R-11 | R-11
| Exterior Wall Insulated: HC | (Btu/ft2·°F) | 12 | 12
| Exterior Wall Uninsulated: U-Value | Btu/(h·ft2·°F) | 0.5 | 0.5
| Exterior Wall Uninsulated: R-Value | (h·ft2·°F)/Btu | 0 | 0
| Exterior Wall Uninsulated: HC | (Btu/ft2·°F) | 12 | 12
| Floor Uninsulated: F-Factor | Btu/(h·ft·°F) | 0.7 | 0.7
Note:
Equivalent material layer represent multi-layer construction assumbly. The equivalent assembly U-value calculated from these single layer materials should include the exterior and interior air film resistances. The following exterior and interior film resistances can be used depending on the envelope type (Adopted from Appendix A ASHRAE 90.1 -2010):
R-Exterior Air Fim Resistance R-Interior Air Film Resistance
Roof Insulation entirely above deck: R-0.17 R-0.61
Wood Framed Walls above grade: R-0.17 R-0.68
Steel Framed Walls above grade: R-0.17 R-0.68
Mass Walls above grade: R-0.17 R-0.68

## DetailsD7
Prototype Building D7
Surface Areas and Fenestration Properties of Prototype Building D7
Space Category | Orientation | Wall Area, ft2 | Window Area, ft2 | Window-Wall-Ratio | Climate Zone 1 Proposed U-Value/SHGC | Climate Zone 2 Proposed U-Value/SHGC
Residential | North | 6600 | 1728 |  | 1.00/0.25 | 0.60/0.25
| Non-North | 30360 | 4800 |  | 1.00/0.25 | 0.60/0.25
Residential Total |  | 36960 | 6528 | 17.66%
Nonresidential
Retail | North | 1700 | 560 |  | 0.90/0.56 | 0.60/0.56
Office | North | 3700 | 960 |  | 0.90/0.25 | 0.60/0.25
Retail | Non-North | 3972 | 2574 |  | 0.90/0.56 | 0.60/0.56
Office | Non-North | 8140 | 2112 |  | 0.90/0.40 | 0.60/0.40
Nonresidential Total |  | 17512 | 6206 | 35.44%
Lighting and Equipment Electric Power of Prototype Building D7
Area Description | Area | Lighting Power |  | Equipment Power
|  | Watts | W/ft² | Watts | W/ft²
Retail | 11300 | 15594 | 1.38 | 16950 | 1.5
Office | 27000 | 31320 | 1.16 | 27000 | 1
Apartment Units | 43600 | 71940 | 1.65 | 71940 | 1.65
Multi-family Hallway | 5600 | 4480 | 0.8 | 3920 | 0.7
Totals | 87500 | 123334 | 1.41 | 119810 | 1.37
Area Description | Area | Lighting Power |  | Equipment Power
|  | Watts | W/ft² | Watts | W/ft²
Multi-Family | 49200 | 76420 | 1.55 | 75860 | 1.54
Occupancy and Minimum Ventilation Air Requirement of Prototype Building D7
Area Description | Area | Occupancy |  | Ventilation Air Requirement
|  | Persons | Person / 1000 ft2 | cfm | cfm/ft2
Retail | 11300 | 148 | 13.1 | 3051 | 0.27
Office | 27000 | 135 | 5 | 2700 | 0.1
Apartment Units | 43600 | 115 | 2.64 | 2180 | 0.05
Multi-family Hallway | 5600 | - | - | 280 | 0.05
Totals | 87500 | 398 | 4.5486 | 8211 | 0.09384