TABLE 508.3.3

REQUIRED SEPARATION OF OCCUPANCIES (HOURS)

OCCUPANCY 	Ae, E, D 	I 	Rd 	F-2, F-3, S-2c,d, Ud 	Bb, F-1, Mb, S-1 	H-1 	H-2 	H-3, H-4, H-5

S 	NS 	S 	NS 	S 	NS 	S 	NS 	S 	NS 	S 	NS 	S 	NS 	S 	NS

Ae, Ee, D 	N 	N 	1 	2 	1 	2 	N 	1 	1 	2 	NP 	NP 	3 	4 	2 	3a

I 	— 	— 	N 	N 	1 	NP 	1 	2 	1 	2 	NP 	NP 	3 	NP 	2 	NP

Rd 	— 	— 	— 	— 	N 	N 	1 	2 	1 	2 	NP 	NP 	3 	NP 	2 	NP

F-2, F-3, S-2c,d, Ud 	— 	— 	— 	— 	— 	— 	N 	N 	1 	2 	NP 	NP 	3 	4 	2 	3a

Bb, F-1, Mb, S-1 	— 	— 	— 	— 	— 	— 	— 	— 	N 	N 	NP 	NP 	2 	3 	1 	2a

H-1 	— 	— 	— 	— 	— 	— 	— 	— 	— 	— 	N 	NP 	NP 	NP 	NP 	NP

H-2 	— 	— 	— 	— 	— 	— 	— 	— 	— 	— 	— 	— 	N 	NP 	1 	NP

H-3, H-4, H-5 	— 	— 	— 	— 	— 	— 	— 	— 	— 	— 	— 	— 	— 	— 	N 	NP

For SI:   1 square foot = 0.0929 m2.

S 	= 	Buildings equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1.

NS 	= 	Buildings not equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1.

N 	= 	No separation requirement.

NP 	= 	Not permitted.

a. For Group H-5 occupancies, see Section 903.2.4.2.

b. Occupancy separation need not be provided for storage areas within Groups B and M if the:

1. Area is less than 10 percent of the floor area;

2. Area is equipped with an automatic fire-extinguishing system and is less than 3,000 square feet; or

3. Area is less than 1,000 square feet.

c. Areas used only for private or pleasure vehicles shall be allowed to reduce separation by 1 hour.

d. See Section 406.1.4.

e. Commercial kitchens need not be separated from the restaurant seating areas that they serve.