TABLE 403.3

REQUIRED OUTDOOR VENTILATION AIR

| OCCUPANCY CLASSIFICATION | ESTIMATED MAXIMUM OCCUPANT LOAD, PERSONS PER 1,000 SQUARE FEETa | OUTDOOR AIR [Cubic feet per minute (cfm) per person] UNLESS NOTEDe |
| --- | --- | --- |
| Correctional facilities Cells without plumbing fixtures with plumbing fixturesg, h Dining halls Guard stations | 20 20 100 40 | 20 20 15 15 |
| Dry cleaners, laundries Coin-operated dry cleaner Coin-operated laundries Commercial dry cleaner Commercial laundry Storage, pick up | 20 20 30 10 30 | 15 15 30 25 35 |
| Education Auditoriums Classrooms Corridors Laboratories Libraries Locker roomsh Music rooms Smoking loungesb,g Training shops | 150 50 - 30 20 - 50 70 30 | 15 15 0.10 cfm/ft2 20 15 0.50 cfm/ft2 15 60 20 |
| Food and beverage service Bars, cocktail lounges Cafeteria, fast food Dining rooms Kitchens (cooking)f,g | 100 100 70 20 | 30 20 20 15 |
| Hospitals, nursing and convalescent homes Autopsy roomsb Medical procedure rooms Operating rooms Patient rooms Physical therapy Recovery and ICU | - 20 20 10 20 20 | 0.50 cfm/ft2 15 30 25 15 15 |
| Hotels, motels, resorts and dormitories Assembly rooms Bathroomsg, h Bedrooms Conference rooms Dormitory sleeping areas Gambling casinos Living rooms Lobbies | 120 - - 50 20 120 - 30 | 15 35 30 cfm per room 20 15 30 30 cfm per room 15 |
| Offices Conference rooms Office spaces Reception areas Telecommunication centers and data entry | 50 7 60 60 | 20 20 15 20 |

(continued)

TABLE 403.3-continued REQUIRED OUTDOOR VENTILATION AIR

| OCCUPANCY CLASSIFICATION | ESTIMATED MAXIMUM OCCUPANT LOAD, PERSONS PER 1,000 SQUARE FEETa | OUTDOOR AIR (Cubic feet per minute (cfm) per person) UNLESS NOTEDe |
| --- | --- | --- |
| Private dwellings, single and multiple |  |  |
| Garages, common for multiple unitsb | - | 1.5 cfm/ft2 |
| Garages, separate for each dwelling | - | 100 cfm per car |
| Kitchensg | - | 100 cfm intermittent or 25 cfm continuous |
| Living areasc | Based upon number of bedrooms. first bedroom: 2; each additional bedroom: 1 | 0.35 air changes per houra or 15 cfm per person, whichever is greater |
| Toilet rooms and bathroomsg, h | - | Mechanical exhaust capacity of 50 cfm intermittent or 20 cfm continuous |
| Public spaces Corridors and utilities Elevator carg Locker roomsh Shower rooms (per shower head)g,h Smoking loungesb,g Toilet roomsg,h | - - 70 | 0.05 cfm/ft2 1.00 cfm/ft2 0.5 cfm/ft2 50 cfm intermittent or 20 cfm continuous 60 50cfm per water closet or urinal |
| Retail stores, sales floors and showroom floors Basement and street Dressing rooms Malls and arcades Shipping and receiving Smoking loungesb Storage rooms Upper floors Warehouses | - - - - 70 - - - | 0.30 cfm/ft2 0.20 cfm/ft2 0.20 cfm/ft2 0.15 cfm/ft2 60 0.15 cfm/ft2 0.20 cfm/ft2 0.05 cfm/ft2 |
| Specialty shops Automotive motor- fuel-dispensing stations Barber Beauty Clothiers, furniture Embalming roomb Florists Hardware, drugs, fabrics | - 25 25 - 8 8 | 1.5 cfm/ft2 15 25 0.30 cfm/ft2 2.0 cfm/ft2 15 15 |

(continued)

TABLE 403.3-continued REQUIRED OUTDOOR VENTILATION AIR

| OCCUPANCY CLASSIFICATION | ESTIMATED MAXIMUM OCCUPANT LOAD, PERSONS PER 1,000 SQUARE FEETa | OUTDOOR AIR (Cubic feet per minute (cfm) per person) UNLESS NOTEDe |
| --- | --- | --- |
| Specialty shops-continued |  |  |
| Nail salonb, i | - | 50 cfm intermittent or 20 cfm continuous per station |
| Pet Shops | - | 1.00 cfm/ft2 |
| Reducing salons | 20 | 15 |
| Supermarkets | 8 | 15 |
| Sports and amusement Ballrooms and discos Bowling alleys (seating areas) Game rooms Ice arenas Playing floors (gymnasiums) Spectator areas Swimming pools (pool and deck area) | 100 70 70 - 30 150 - | 25 25 25 0.50 cfm/ft2 20 15 0.50 cfm/ft2 |
| Storage Repair garages, enclosed parking garagesd Warehouses | - - | 1.5 cfm/ft2 0.05 cfm/ft2 |
| Theaters Auditoriums Lobbies Stages, studios Ticket booths | 150 150 70 60 | 15 20 15 20 |
| Transportation Platforms Vehicles Waiting rooms | 100 150 100 | 15 15 15 |
| Workrooms Bank vaults Darkrooms Duplicating, printing Meat processingc Pharmacy Photo studios | 5 - - 10 20 10 | 15 0.50 cfm/ft2 0.50 cfm/ft2 15 15 15 |

For SI:   1 cubic foot per minute = 0.0004719m3/s, 1 ton = 908 kg, 1 cubic foot per minute per square foot = 0.00508m3/(s m2), °C = [(°F) -32]/1.8, 1 square foot = 0.0929m2.

a. Based upon net floor area.

b. Mechanical exhaust required and the recirculation of air from such spaces as permitted by Section 403.2.1 is prohibited (see Section 403.2.1, Items 1 and 3).

c. Spaces unheated or maintained below 50°F are not covered by these requirements unless the occupancy is continuous.

d. Ventilation systems in enclosed parking garages shall comply with Section 404.

e. Where the ventilation rate is expressed in cfm/ft2, such rate is based upon cubic feet per minute per square foot of the floor area being ventilated.

f. The sum of the outdoor and transfer air from adjacent spaces shall be sufficient to provide an exhaust rate of not less than 1.5 cfm/ft2.

g. Transfer air permitted in accordance with Section 403.2.2.

h. Mechanical exhaust is required and recirculation is prohibited except that

recirculation shall be permitted where the resulting supply air stream consists of not

more than 10 percent air recirculated from these spaces (see Section 403.2.1, Items 2 and 4).

i.   The required exhaust system shall capture the contaminants and odors at their source.