| Florida Building Code – Building with “2009 Supplement” |  |  |  |  |
| --- | --- | --- | --- | --- |
| 2004 FBCR |  | 2007 FBCR |  | Analysis |
| Section | Requirement | Section | Requirement |  |
| Preface |  |  |  |  |
|  |  | Preface | Adds missing language to the preface from the 2006 International Codes which explains the letters in brackets at the beginning of the paragraphs. Add text after the section, Adoption and Maintenance, to read as follows: Letter Designations in Front of Section Numbers In each code development cycle, proposed changes to the code are considered at the Code Development Hearings by the ICC Fire Code Development Committee, whose action constitutes a recommendation to the voting membership for final action on the proposed change. Proposed changes to a code section that has a number beginning with a letter in brackets are considered by a different code development committee. For example, proposed changes to code sections that have [F] in front of them (e.g. [F] 903.1.1.1) are considered by the ICC Fire Code Development Committee at the code development hearings. The content of sections in this code that begin with a letter designation are maintained by another code development committee in accordance with the following: [E] = International Energy Conservation Code Development Committee; [EB] = International Existing Building Code Development Committee; [EL] = ICC Electrical Code Development Committee; [F] = International Fire Code Development Committee; [FG] = International Fuel Gas Code Development Committee; [M] = International Mechanical Code Development Committee; and [P] = International Plumbing Code Development Committee. |  |
| Chapter 1: Administration |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| 105.1 | Required permits | 105.1 | Required permits | Revised to require a permit for erecting, installing, enlarging, alterering, repairing, removing, converting or replacing "impact-resistant coverings". |
| 105.3.1.2 | Documents required for permit issuance | 105.3.1.2 | Documents required for permit issuance | Deleted Item 1 which required a registered engineer to prepare electrical documents for any new building or addition which requires an aggregate service capacity of 600 amperes (240 volts) or more on a residential electrical system or 800 amperes (240 volts) or more on a commercial or industrial electrical system and which costs more than $50,000 |
|  |  | 105.15 | Unsafe Structures and Equipment | When any activity requiring a building permit that is applied for on or after July 1, 2008, and for which the estimated cost is $50,000 or more for a building that is located in the wind borne debris region as defined in the Florida Building Code and that has an insured value of $750,000 or more, or, if the building is uninsured or for which documentation of insured value is not presented, has a just valuation for the structure for purposes of ad valorem taxation of $750,000 or more. |
| 106.1 | Submittal documents | 106.1 | Submittal documents | Revised to replace "special inspection and structural observation programs" with "statement of special inspections." |
| 109.3 | Required inspections | 109.3 | Required inspections | The listed inspection for Building Framing Inspection (Item 2) has been revised to include verifying that rough opening dimensions are within tolerances. New Item 9 added requiring inspections and criteria for impact-resistant coverings. |
| - | - | 110.4 | Certificate of completion | New section defining a certificate of completion that is intended to allow connection to utility systems prior to issuance of a certificate of occupancy. |
| Chapter 2: Definitions |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
|  | - |  | ACC Masonry | Added AAC Masonry term due to additions of references in several code sections. |
|  | Adjusted Shear Resistance |  | - | Removed term definition for steel construction. ANSI's new methodology for determining deflection in shear walls is not addressed in the IBC and meaning is shown elsewhere in the code as reference to the ANSI std. |
|  | Adjusted Shear Resistance |  | - | Removed term definition for wood construction. ANSI's new methodology for determining deflection in shear walls is not addressed in the IBC and meaning is shown elsewhere in the code as reference to the ANSI std. |
|  | Admixtue |  | - | Definition deleted. Concrete terms are now defined in ACI 318. |
|  | Aggregate |  | - |  |
|  | Aggregate, lightweight |  | - |  |
|  | - |  | Aisle accessway | Added the definition for clarification between what is considered an aisle and an aisle accessway, as they relate to mercantile occupancies. |
|  | - |  | Term: Approved | Revised wording to include acceptable by AHJ, not just per the Bldg Official. |
|  | - |  | Autoclaved aerated concrete (AAC) | New text added in 2102 utilizing AAC term. |
|  | - |  | Baled cotton | Added term due to clarifications in hazardous materials sections of the code (occupancy and quantity) |
|  | - |  | Baled cotton, densely packed | Added term due to clarifications in hazardous materials sections of the code (occupancy and quantity) |
| 202 | Agricultural, Building. | 202 | Agricultural, Building. | Delete definition and reserve term. Reserved. |
|  | Base Shear |  | - | Removed term definition due to ANSI's new methodology for determining deflection in shear walls is not addressed in the IBC and meaning is shown elsewhere in the code as reference to the ANSI std. |
|  | Basement |  | Basement | Removed definition text and replaced with reference: See Section 502.1. |
|  | Boundry Element |  | - | Definition deleted - no longer utilized. |
|  | Boundry Members |  | - |  |
|  | Brittle |  | - |  |
|  | Brittle Steel Element |  | - |  |
|  | Building Enclosed |  | - |  |
|  | Cantilevered Column System |  | - |  |
| - | - | 202 | Carbon Monoxide Alarm | Ad a definition for CO Alarm which is now regulated by the code as a result of legislation. A device for the purpose of detecting carbon monoxide, that produces a distinct audible alarm, and is listed or labeled with the appropriate standard, either ANSI/UL 2034 - 96, Standard for Single and Multiple Station CO Alarms, or UL 2075 - 04, Gas and Vapor Detector Sensor, in accordance with its application. |
|  | Cementimous Material |  | - | Definition deleted. Concrete terms are now defined in ACI 318. |
|  | Collector Elements |  | - | Definition deleted - no longer utilized.. |
|  | Component |  | - |  |
|  | Components and Cladding |  | - |  |
|  | Concrete, Specified Compressive Strength Of. |  | - |  |
|  | Confined Region |  | - |  |
|  | - |  | Congregate Living Facilities | Added term to clarify Group R with added distinction between R2 and R3 based on 16 person threshold. |
|  | Contraction Joint |  | - | Definition deleted. Concrete terms are now defined in ACI 318. |
|  | - |  | Decorative Materials | Added definition to clarify the term used throughout IFC and several chapters of IBC. |
|  | Deformability |  | - | Term was previously not referred to or used in the code and therefore removed. |
|  | Deformation |  | - |  |
|  | Deformed Reinforcement |  | - |  |
|  | - |  | Design Displacement | Term added and now utilized in ACI and Section 1908. |
| - | - | 202 | Design Displacement | Delete definition and reserve term. Reserved. |
|  | - |  | Design Earthquake Ground Motion | Term added and now utilized in Section 1613. |
|  | - |  | Designated Seismic System | Definition added. |
|  | - |  | Detailed Plain Concrete Structural Wall | Definition added. |
|  | Ductile Steel Element |  | - | Definition deleted - no longer utilized. |
|  | Effective Depth of Section |  | - | Definition deleted. |
|  | Effective Embedment Depth |  | - | Definition deleted. |
|  | Element |  | - | Definition deleted. |
|  | - |  | Equipment Platform | Definition revised to read equipment platform instead of industrial equipment platform to clarify its use for both industrial and commercial use. |
|  | Equipment Support |  | - | Definition deleted. |
|  | - |  | Exit Horizontal | Term is utilized in Ch.10 but was not previously listed. |
|  | - |  | Fabric Partitions | Added definition to clarify the term used in Ch.16. |
|  | - |  | Family Day Care Homes | Clarification of definition to define the client numbers and ages allowed. |
|  | - |  | Fiber Cement Siding | Definition added. |
|  | - |  | Fire Alarm Box, Manual | Term now defined in 902.1 |
|  | - |  | Fire Lane | Definition added (taken from IFC). Term was not previously defined in Ch.2 but is utilized in IBC. |
|  | Flame Resistance |  | - | Definition deleted. |
|  | Flexible Buildings and Other Structures |  | - |  |
|  | Flexible Equipment Connections |  | - |  |
|  | Flexible Plan Buildings |  | - |  |
| - | - | 202 | Fossil Fuel | Definition added as a part of the Carbon Monoxide regulation. Coal, kerosene, oil, fuel gases, or other petroleum or hydrocarbon product that emits carbon monoxide as a by-product of combustion. |
|  | Garden Mausoleum |  | - | Definition deleted. |
|  | Habitable Space |  | Habitable Space | Definition revised to clarify the addition of: screen enclosures, sunroom Categories I, II and III as defined in the AAMA/NPEA/NSA 2100, |
|  | Importance Factor, I. |  | - | Definition deleted. Wind Factor was removed from Table 1604.5. |
|  | - |  | Masonry, Unreinforced (plain) masonry | Definition added for consistency with ACI for masonry structures. |
|  | Mean Roof Height |  | - | Definition deleted. |
|  | Nonvisitation Crypt Mausoleum |  | - |  |
|  | Occupancy Importance Factor |  | - |  |
|  | - |  | Ordinary Precast Structural Wall | Definition added for consistency with ACI. |
|  | - | 202 | Ordinary Precast Structural Wall | Delete definition and reserve term. Reserved. |
|  | - |  | Ordinary Reinforced Concrete Structural Wall | Definition added for consistency with ACI. |
|  | - | 202 | Ordinary Reinforced Concrete Structural Wall | Delete definition and reserve term. Reserved. |
|  | - |  | Ordinary Structural Plain Concrete Wall | Definition added for consistency with ACI. |
|  | - | 202 | Ordinary Structural Plain Concrete Wall | Delete definition and reserve term. Reserved. |
|  | Pedestal |  | - | Definition deleted. Concrete terms are now defined in ACI 318. |
|  | Plain Concrete |  | - |  |
|  | Precast Concrete |  | - |  |
|  | - |  | Prefabricated Wood I-Joist |  |
|  | Prestressed Concrete |  | - |  |
|  | Reinforced Concrete |  | - |  |
|  | Reshores |  | - |  |
|  | Shear Panel |  | - | Definition deleted |
|  | Shear Wall |  | Shear Wall | Definition revised to remove sub-categories definitions and provide a single definition as follows: Shear Wall- A wall designed to resist lateral forces parallel to the plane of the wall. |
|  | Shores |  | - | Definition deleted. Concrete terms are now defined in ACI 318. |
|  | Shotcrete |  | - |  |
|  | Side-Face Blowout Strength |  | - |  |
|  | Space Frame |  | - | Definition deleted. |
|  | Spiral Reinforcement |  | - | Definition deleted. Concrete terms are now defined in ACI 318. |
|  | Story |  | Story | Removed the term "basement" from within definition. |
|  | Story Above Grade Plane |  | Story Above Grade Plane | Revision to this definition as well as the definition for "basement" eliminates redundant conditions from the determination of whether or not a basement is a story above plane. New definition revised to state that < 12 ft above finished ground level at any point. |
|  | Strength |  | Strength | Added term "Required strength" and section reference: 1602.1 and 2102.1. |
|  | Structural Concrete |  | - | Definition deleted. Concrete terms are now defined in ACI 318. |
| - | - | 202 | Sunroom | Definition moved to Chapter 12 See Section 1202.1 |
| - | - | 202 | Sunroom, Addition | Delete definition and reserve term. Reserved |
|  | Tendon |  | - | Definition deleted. Concrete terms are now defined in ACI 318. |
|  | Torsional Force Distribution |  | - | Definition deleted. |
| - | - | 202 | Townhouse | Revise definition to be consistent FBC-R A single-family dwelling unit constructed in a group of three or more attached units with property lines separating each unit in which each unit extends from foundation to roof and with open space on at least two sides. |
|  | Unadjusted Shear Resistance |  | - | Definition deleted. |
| Chapter 3: Use and Occupancy Classification |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| 302.1 | General | 302.1 | General | Editorial change to incorporate 2006 IBC language as intended in the development of the 2007 Florida Building Code, Building. Revise section to read: Structures or portions of structures shall be classified with respect to occupancy in one or more of the groups listed below. A room or space that is intended to be occupied at different times for different purposes shall comply with all of the requirements that are applicable to each of the purposes for which the room or space will be occupied. Structures with multiple occupancies or uses shall comply with Section 508. Where a structure is proposed for a purpose that is not specifically provided for in this code, such structure shall be classified in the group that the occupancy most nearly resembles, according to the fire safety and relative hazard involved. 1. Assembly (see Section 303): Groups A-1, A-2, A-3, A-4 and A-5 2. Business (see Section 304): Group B 3. Educational (see Section 305): Group E 4. Factory and Industrial (see Section 306): Groups F-1, F-2 and F-3. 5. High Hazard (see Section 307): Groups H-1, H-2, H-3, H-4 and H-5 6. Institutional (see Section 308): Groups I-1, I-2 and I-3 7. Mercantile (see Section 309): Group M 8. Residential (see Section 310): Groups R-1, R-2, R-3 as applicable in Section 101.2, and R-4 9. Storage (see Section 311): Groups S-1 and S-2 10. Utility and Miscellaneous (see Section 312): Group U 11. Day care (see Section 313): Group D |
| - | - | 508.1 | Mixed use and occupancy | General scoping statement for mixed uses and occupancies. |
| 302.1.1 | Incidental use areas | 508.2 | Incidental uses | Text relocated to Section 508. Language revised to clarify that incidental uses areas to be in accordance with this section or considered a mixed occupancy. |
|  |  | 508.2.1 | Occupancy classification |  |
| 302.1.1.1 | Separation | 508.2.2 | Separation | Language reorganized for clarity. Section 706 is specifically referenced for construction of fire barriers and Section 711 is specifically referenced for horizontal assemblies. |
|  |  | 508.2.2.1 | Construction of separation |  |
| - | - | 508.2.3 | Protection | New language clarifying that where an automatic fire-extinguishing system or automatic sprinklers system is provided per Table 508.2, only the incidental use areas have to be equipped with such a system. |
| Table 302.1.1 | Incidental use areas separation requirements | Table 508.2 | Incidental use areas separation and/or requirements | Hydrogen cut-off rooms was revised to clarify the requirements only applied to those not classified as Group H. Requirements for boilers was revised to clarify that the 15 psi and 10 horsepower limit applies to the largest piece of equipment in a room with a boiler. |
| 302.2 | Accessory use areas | 508.3.1 | Accessory occupancies | Language reorganized for clarity. Now requires accessory use areas to not exceed the tabular values in Table 503 without height and area increases as specified in Sections 504 and 506. Assembly areas accessory to Group E are not considered separate occupancies except when applying the assembly occupancy requirements of Chapter 11. |
| 302.2.1 | Accessory assembly areas | 508.3.1.3 | Separation |  |
| - | - | 508.3.1.1 | Occupancy classification | Requires accessory occupancies to be classified in accordance with 302.1. Requires all code requirements to apply to each portion of the building based on the classification of the accessory space. |
| - | - | 508.3.1.2 | Allowable height and area | Requires allowable height and area of accessory occupancies to be based on the allowable area and height for the main occupancy. Restricts the height of accessory occupancies to the tabular value in Table 503 without height and area increases. |
| 302.3 | Mixed occupancies | 508.3 | Mixed occupancies | Section and provisions reformatted for coordination with relocation of mixed use provisions. |
| 302.3.1 | Nonseparated uses | 508.3.2 | Nonseparated uses | Requirements reorganized but primarily the same. Revised to require the most restrictive requirements of Chapter 9 and Section 403 as applicable to the entire building instead of just the nonseparated uses. |
|  |  | 508.3.2.1 | Occupancy classification |  |
|  |  | 508.3.2.2 | Allowable height and area |  |
|  |  | 508.3.2.3 | Separation |  |
| 302.3.2 | Separated uses | 508.3.3 | Separated uses | Requirements reorganized but primarily the same. |
|  |  | 508.3.3.1 | Occupancy classification |  |
|  |  | 508.3.3.2 | Allowable area |  |
|  |  | 508.3.3.3 | Allowable height |  |
|  |  | 508.3.3.4 | Separation |  |
| Table 302.3.2 | Required separation of occupancies | Table 508.3.3 | Required separation of occupancies | Table significantly revised. Group H occupancies require separation from each other and all other occupancies. Groups B, F-1, M, and S-1 require no separation from each other but are required to be separated from other occupancies. Groups A, E, and D require no separation from each other but are required to be separated from other occupancies except for fully sprinklered Groups F-2, F-3 and S-2. |
| 302.4 | Spaces used for different purposes | - | - | Section deleted. |
| 303.1 | Assembly Group A | 303.1 | Assembly Group A | Section reformatted to place provisions that are exceptions to the requirements as Exceptions 1, 2, and 3. Places of religious worship located in A-3. |
| 304.1 | Business Group B | 304.1 | Business Group B | Revised to include Training and skill development not within a school or academic program in Group B list. |
| 307.1 | High-Hazard Group H | 307.1 | High-Hazard Group H | Revised to provide a direct connection to Section 414 and the Florida Fire Prevention Code. Exceptions in Section 307.9 relocated as exceptions to Section 307.1 |
| 307.2 | High-Hazard Definitions | 307.2 | High-Hazard Definitions | Added new definitions for "Baled Cotton" and "Baled Cotton, Densely Packed." Revised definition of "Combustible Fibers" to replace "fibers" with "materials in a fibrous or shredded form" and exclude densely packed baled cotton. Revised definition of "Control Area" by deleting that the area be enclosed and bounded by exterior walls, fire walls, fire barriers, and roofs. Added new definition for "Day Box." Revised definition of Class 2 "Water-Reactive Material" |
| Table 307.7(1) | Max quantities per control area of hazardous materials posing a physical hazard | Table 307.7(1) | Max quantities per control area of hazardous materials posing a physical hazard | Added "Day Box" for increasing quantities by 100%. Added new note "o" pertaining to densely packed baled cotton. Added new not "p" pertaining to liquid and gaseous fuels. |
| 310.1 | Residential Group R | 310.1 | Residential Group R | Group R-2 revised to permit congregate living facilities with 16 or fewer occupants to comply with R-3. R-2 provisions reformatted. R-3 revised to include congregate living facilities with less than 16 occupants. |
| 310.2 | Residential Group R definitions | 310.2 | Residential Group R definitions | Definitions added for "Congregate Living Facilities" and "Transient." |
| 311.2 | Moderate-hazard storage Group S-1 | 311.2 | Moderate-hazard storage Group S-1 | Group S-1 list revised to include "Dry boat storage (indoor)." |
| Chapter 4: Special Detailed Requirements Based on Use and Occupancy |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| 402.1 | Covered Mall Buildings | 402.1 | Covered Mall Buildings | Revised term "grade" in the scope to "grade plane" for consistency. |
| 402.4.2 | Number of means of egress | 402.4.2 | Number of means of egress | Revised wording to state, "load of 50 or more" as opposed to "exceeds an occupant load of 50." |
| 402.7.3 | Anchor building separation | 402.7.3 | Anchor building separation | Revised term "grade" in the exception to "grade plane" for consistency. |
| - | - | 402.11 | Children's playground structures | New section added to include children's indoor playground structures to clarify fire safety requirements. |
| 402.11 | Security grilles and doors | 402.12 | Security grilles and doors | Revised wording to state, "50 or more persons" as opposed to "50 persons." |
| 402.14 | Plastic Signs | 402.15 | Plastic Signs | Editorial clarification - no change in definition or requirements. |
| 403.3.1 | High rise buildings: Type of construction | 403.3.1 | High rise buildings: Type of construction | Added "for buildings not greater than 420 feet in height" to 1 to comply with new height limitations for fire resistance ratings. |
| 403.3.2 | High rise buildings: Shaft enclosures | 403.3.2 | High rise buildings: Shaft enclosures | Added "for buildings not greater than 420 feet in height" to comply with new height limitations for fire resistance ratings. |
| 403.10.1 | Special requirements for standby power systems | 403.10.1 | Special requirements for standby power systems | Clarification provides specific compliance for fire rated barrier for enclosed room. |
| 403.10.2 | Standby power loads | 403.10.2 | Standby power loads | Revised referenced sections to add 1007.4. |
| 404.3 | Atrium: Automatic sprinkler protection | 404.3 | Atrium: Automatic sprinkler protection | Removed "horizontal assembly or both" from exception 1 description as requirements are already described in section 706. |
| 404.4 | Atrium: Smoke control | 404.4 | Atrium: Smoke control | Added exception for clarification of original intent of atrium definition as well as to provide consistency with BOCA and UBC requirements. |
| 404.5 | Enclosure of atriums | 404.5 | Enclosure of atriums | Removed language referring to computation of atrium volume. |
| 405.4.2 | Underground buildings: smoke barrier penetration | 405.4.2 | Underground buildings: smoke barrier penetration | Section revised to comply with requirements of fire doors to be automatically closing by smoke detection. |
| 405.4.3 | Underground buildings: Elevators | 405.4.3 | Underground buildings: Elevators | Section revised to comply with requirements of fire doors to be automatically closing by smoke detection. |
| 406.1.2 | Motor-vehicle-related occupancies: Area increase | 406.1.2 | Motor-vehicle-related occupancies: area increase | For Group U occupancies, exterior wall requirements no longer refer to Group R-1 or R-2. Update states wall shall not be required to have a fire-resistance rating and the area of opening shall not be limited when the fire separation distance is 5 feet, thus providing an exemption from the separation requirement. |
| 406.1.4 | Motor-vehicle-related occupancies: Separation | 406.1.4 | Motor-vehicle-related occupancies: Separation | Section revised to add, "doors shall be self-closing, self-latching." |
| - | - | 406.2.4 | Parking garages: vehicle barriers | Added exception. |
| 406.2.5 | Parking garages: ramps | 406.2.5 | Parking garages: ramps | Revised language to provide information specific to parking structures and to eliminate confusion with Ch. 10 egress requirements. |
| 406.3.6 | Open parking garages area and height increases | 406.3.6 | Open parking garages area and height increases | Revised language removes Type IB type of construction and provides a section option for ventilation requirements. |
| 406.4.1 | Enclosed parking garage heights and areas | 406.4.1 | Enclosed parking garage heights and areas | Added referenced sections to clarify that the enclosed parking garages also comply with applicable increases provided for other structures. |
| - | - | 406.5.2.1 | Canopies used to support gaseous hydrogen systems | Added new section to assist with growing need for hydrogen motor fuel-dispensing facilities. |
| 407.3 | Group I-2 corridor walls | 407.3 | Group I-2 corridor walls | Added reference section 710 to clarify existing requirement. |
| 407.6 | Group I-2 automatic fire detection | 407.6 | Group I-2 automatic fire detection | Added specific reference for hospital requirements to correlate with IFC. |
| 408.3.6 | Group I-3 exit enclosures | 408.3.6 | Group I-3 exit enclosures | Removed the term "vertical" for consistency in terminology throughout the code. |
| 408.7.1 | Group I-3 Subdivision of resident housing areas, occupancy conditions 3 and 4 | 408.7.1 | Group I-3 Subdivision of resident housing areas, occupancy conditions 3 and 4 | Removed the term "exit access" for consistency in terminology throughout the code. |
| 408.7.2 | Group I-3 Subdivision of resident housing areas, occupancy condition 5 | 408.7.2 | Group I-3 Subdivision of resident housing areas, occupancy condition 5 | Removed the term "exit access" for consistency in terminology throughout the code. |
| 410.2 | Definition: Stages and Platforms | 410.2 | Definition: Stages and Platforms | Measuring requirements for stage removed from definition and are shown in stage construction section. |
| 410.3.5 | Stages and Platforms: Proscenium curtain | 410.3.5 | Stages and Platforms: Proscenium curtain | Revised language to be consistent with code relating to fire-rated wall and openings. |
| 410.3.6 | Stages and Platforms: Scenery | 410.3.6 | Stages and Platforms: Scenery | Reference to "flame resistance" of materials has been revised to "fire propagation performance criteria of NFPA 701" consistent with terminology in NFPA 701. |
| 410.5.1 | Separation from stage in dressing and appurtenant rooms | 410.5.1 | Separation from stage in dressing and appurtenant rooms | Removed "wall and horizontal assemblies" since fire barrier in general is described in Section 702. |
| 410.5.3 | Opening Protectives | - | - | Removed unnecessary Section. |
| 410.5.4 | Stage Exits | 410.5.3 | Stage Exits | Section relocated. |
| 410.6 | Stages and Platforms: Automatic sprinkler system | 410.6 | Stages and Platforms: Automatic sprinkler system | Revised language to current terminology and added Exception 3: Sprinklers are not required in portable orchestra enclosures on stage. |
| Table 412.1.2 | Height and Area Limitations for Airport Traffic Control Towers | Table 412.1.2 | Height and Area Limitations for Airport Traffic Control Towers | Added footnote a for measurement clarification. |
| 412.2.1 | Exterior walls. | 412.2.1 | Exterior walls. | Revise section by addition of language inadvertently left out of code at printing. Exterior walls located less than 30 feet (9 144 mm) from property lines, lot lines or a public way shall have a fire-resistance rating not less than 2 hours. |
| 412.2.3 | Aircraft related occupancies floor surface | 412.2.3 | Aircraft related occupancies floor surface | Added exception to this section to provide an exemption from the separation requirement, similar to exemption for motor vehicle repair occupancies. |
| 412.2.4 | Aircraft related occupancies: Heating equipment | 412.2.4 | Aircraft related occupancies: Heating equipment | Added "vented infrared radiant heating equipment" to exception 1. |
| 412.3.2 | Aircraft related occupancies: Fire separation | 412.3.2 | Aircraft related occupancies: Fire separation | Revised language from "walls" to "fire barrier" for code term consistency. |
| 412.5.2 | Heliport and helistops sizes | 412.5.2 | Heliport and helistops sizes | Removed the term touchdown. |
| 412.5.4 | Heliport and helistops means of egress | 412.5.4 | Heliport and helistops means of egress | Removed the terms platform or roof. |
| 414.2.1 | Hazardous materials: Construction requirements | 414.2.1 | Hazardous materials: Construction requirements | Added "or horizontal assemblies constructed in accordance with Section 711, or both" since previous reference to 706 for fire barriers simply refers the reader to 711. |
| 414.2.3 | Hazardous materials: Separation | 414.2.4 | Hazardous materials: Fire-resistance rating requirements | Section relocated and title revised to better reflect subsection requirements and added exception. |
| 414.2.4 | Hazardous material in Group M display and storage areas and in Group S storage areas | 414.2.5 | Hazardous material in Group M display and storage areas and in Group S storage areas | Revisions in language and added paragraphs 2 and 3 to better correlate with information in the IFC, which provides tables and cross-reference requirements for better determination of maximum allowable quantities. |
| Table 414.2.5 | Maximum Allowable Quantity Per Indoor and Outdoor Control Area in Group M and S Occupancies | Table 414.2.5(1) | Maximum Allowable Quantity Per Indoor and Outdoor Control Area in Group M and S Occupancies | Revised Table number to denote Table 1 due to the addition of a Table 2. |
| - | - | Table 414.2.5(2) | Maximum Allowable Quantity of Flammable and Combustible Liquids in Wholesale and Retail Sales Occupancies per Control Area | Added Table 2 to better correlate with information in the IFC. New table provides more detail in requirements for better determination of maximum allowable quantities. |
| 414.5.4 | Hazardous materials: Standby emergency power | 414.5.4 | Hazardous materials: Standby emergency power | Added "or the ICC Electrical Code" to existing language. |
| 414.6.1 | Hazardous materials: Outdoor storage, dispensing and use | 414.6.1 | Hazardous materials: Weather protection for outdoor storage, dispensing and use | Revised language clarifies the original intent of allowable obstruction. |
| - | - | 414.6.1.1 | Hazardous materials: Outdoor storage, dispensing and use walls | Added section to clarify the original intent of allowable obstruction. |
| - | - | 414.6.1.2 | Hazardous materials: Outdoor storage, dispensing and use separation distance | Added section to clarify the original intent of allowable obstruction. |
| - | - | 414.6.1.3 | Hazardous materials: Outdoor storage, dispensing and use of noncombustible construction | Added section and exception to clarify the original intent of allowable obstruction. |
| - | - | 415.2 | Groups H-1, H-2, H-4, and H-5 Definition: Physiological Warning Threshold Level | Added definition to correlate with the Permissible Exposure Limit (PEL) in 20 CFR. |
| 415.3 | Location on Property | 415.3 | Fire Separation Distance | Revised title as well as language to change H2 "or" H-3 to H2 "and" H3. |
| 415.3.1 | Group H minimum distance to lot lines | 415.3.1 | Group H occupancy minimum fire separation distance | Revised title as well as language for consistency with current code. |
| 415.3.2 | Group H minimum distance to lot lines | 415.3.2 | Group H-1 and H-2 or H-3 detached buildings | Revised title as well as language for consistency with current code. |
| 415.6 | Smoke and Heat Venting | - | - | Removed section. |
| 415.6.1.2 | Group H-2 grinding rooms | 415.6.1.2 | Group H-2 grinding rooms | Removed "wall and horizontal assemblies" since fire barrier in general is described in Section 702. |
| - | - | 415.6.3.5.2 | Common construction in areas of liquefied petroleum gas-distribution facilities | Provides clarity for scoping and technical provisions for fire barriers. |
| 415.8.3 | Separation - highly toxic solids and liquids | 415.7.3 | Separation - highly toxic solids and liquids | Revised language from "walls" to "fire barrier" for code term consistency. |
| 415.9.2.6 | Group H-5 ventilation | 415.8.2.6 | Group H-5 ventilation | Revised language to clarify that the ventilation requirements are for areas within H-5 where materials are used and stored. |
| 415.9.2.7 | Group H-5 Transporting hazardous production materials to fabrication areas | 415.8.2.7 | Group H-5 Transporting hazardous production materials to fabrication areas | Removed the term "exit access" for consistency in terminology throughout the code. |
| Table 415.9.2.1.1 | Quantity Limits for Hazardous Materials in a Single Fabrication Area in Group H-5 | Table 415.8.2.1.1 | Quantity Limits for Hazardous Materials in a Single Fabrication Area in Group H-5 | Added footnote C and revised "combustible fiber" in table to add footnote C. |
| 415.9.3 | Group H-5 Corridors | 415.8.3 | Group H-5 Corridors | Removed the term "exit access" from section and exception for consistency in terminology throughout the code. |
| 415.9.4.2 | Group H-5 Service corridors use conditions | 415.8.4.2 | Group H-5 Service corridors use conditions | Removed the term "exit access" for consistency in terminology throughout the code. |
| 415.9.5.1 | Storage of hazardous production materials | 415.8.5.1 | Storage of hazardous production materials | Removed reference to Table 307 and added new reference to Section 1804.2 of the IFC. |
| 415.9.6.3 | Piping installations in exit access corridors and above other occupancies | 415.8.6.3 | Piping installations in corridors and above other occupancies | Removed the term "exit access" from title for consistency in terminology throughout the code. Revised the language in condition 4 and 5 to utilize "fire barrier" and remove the term "exit access." |
| 415.9.7 | Continuous gas detection systems | 415.8.7 | Continuous gas detection systems | Revised language to utilize the term "physiological warning threshold level" to correlate with the Permissible Exposure Limit (PEL) in 20 CFR. |
| 415.9.7.1.4 | Exit access corridors | 415.8.7.1.4 | Corridors | Removed the term "exit access" from title and section for consistency in terminology throughout the code. |
| 415.9.9 | Emergency control station | 415.8.9 | Emergency control station | Revised section to include specific subsections and added correlated information to the Florida Fire Prevention Code. |
| 415.9.9.3 | Group H-5 signals | 415.8.9.3 | Group H-5 signals | Revised section to include items 7 and 8 for system types and added correlated information to the Florida Fire Prevention Code. |
| 415.9.10.1 | Required electrical systems | 415.8.10.1 | Required electrical systems | Revised to require emergency power for additional systems outlined in items 9-11. |
| 415.9.11.1 | Exhaust ducts for HPM | 415.8.11.1 | Exhaust ducts for HPM | Revised terminology used to include "gases" to clarify intent. |
| 415.9.11.2 | Metallic and noncombustible nonmetallic exhaust ducts | 415.8.11.2 | Metallic and noncombustible nonmetallic exhaust ducts | Revised terminology used to include "gases" to clarify intent. |
| 416.2 | Application of flammable finishes in spray rooms | 416.2 | Application of flammable finishes in spray rooms | Removed "wall and horizontal assemblies" since fire barrier in general is described in Section 702. |
| 419 | Group I-1, R-1, R-2, R-3 | 438 | Group I-1, R-1, R-2, R-3 | Section moved to newly created section number 438. |
| 419.1 | Hospitals - scope | 419.1 | Hospitals - scope | Added to comply with "all applicable requirements of the code" |
| 419.2.1 | Hospitals - codes and standards | 419.2.1 | Hospitals - codes and standards | Revised scope to state "as described in Section 105 of the code" as well as language revisions for clarity. |
| 419.2.1.2 | Guidelines for design and construction | 419.2.1.2 | Guidelines for design and construction | Revised from chapter references to "Part I - Part 3" per new reference in AIA |
| 419.3.2 | Patient rooms | - | - | Section removed. |
| 419.3.3 | Critical care units | 419.3.2 | Critical care units | Reference to Section 7.3 was removed to reference the overall Guidelines. |
| 419.3.3.1 | Critical care units toileting facilities | 419.3.2.1 | Critical care units toileting facilities | Revised language from "built in" to "under cabinet modular" toilets. Removed the information pertaining to toilet provisions within the critical care room and added "shall not be permitted" statement. |
| 419.3.3.2 | Critical care units sliding doors | 419.3.2.2 | Critical care units sliding doors | Removed reference to break away and recessed track features. Revised term "resistant" to "resistive." |
| 419.3.4 | Newborn intensive care units | 419.3.3 | Newborn intensive care units | Reference to Section 7.3E was removed to reference the overall Guidelines. |
| 419.3.4.1 | Newborn intensive care unit categories | 419.3.3.1 | Newborn intensive care unit categories | Added "in the State of Florida" to first sentence. Reference to Section 7.3E was removed to reference the overall newborn intensive care unit guidelines. |
| 419.3.4.2 | Labor and delivery rooms | 419.3.3.2 | Labor and delivery rooms | Reference to Section 7.4.B1 was removed to reference the overall Guidelines. |
| 419.3.8.1 | Mobile testing and treatment facilities | 419.3.4.1 | Mobile testing and treatment facilities | Revised first sentence to add, "In addition to any other state of Florida required permits." |
| 419.3.8.3 | Mobile testing and treatment facilities - electrical connections | 419.3.4.3 | Mobile testing and treatment facilities - electrical connections | Removed reference to Chapter 27. |
| - | - | 419.3.4.8 | Mobile testing and treatment facilities | Added new section to include the requirement of a code blue station connected to the hospital response team. |
| 419.3.8.8 | Mobile testing and treatment facilities - electrical systems | 419.3.4.9 | Mobile testing and treatment facilities - electrical systems | Reference to Section 7.32 was removed to reference the overall Guidelines as well as Section 419.3.15. (revised reference) |
| 419.3.8.9 | Mobile testing and treatment facilities - mechanical systems | 419.3.4.10 | Mobile testing and treatment facilities - mechanical systems | Reference to Section 7.31 was removed to reference the overall Guidelines as well as Section 419.3.11. (revised reference) |
| 419.3.5 | Outpatient surgery | 419.3.5 | Outpatient surgery | Deleted information and Section is now "Reserved" |
| 419.3.6 | Obstetrical facilities | 419.3.6 | Obstetrical facilities | Deleted information and Section is now "Reserved" |
| 419.3.7 | Administration and public areas | 419.3.7 | Administration and public areas | Deleted information and Section is now "Reserved" |
| 419.3.8 | Mobile testing and treatment facilities | 419.3.8 | Mobile testing and treatment facilities | Moved information to new section 419.4.3.1 and Section is now "Reserved" |
| 419.3.9 | Hospital details and finishes | 419.3.9 | Hospital details and finishes | Reference to Section 7.28 was removed to reference the overall Guidelines. |
| - | - | 419.3.9.9 | Hospital details and finishes | Added new section stating that sliding or folding doors to patient toilets shall not be permitted. |
| 419.3.10 | Hospital details and finishes - elevators | 419.3.10 | Hospital details and finishes - elevators | Reference to Section 7.30.B was removed to reference the overall Guidelines. The "code" was revised to read "The Florida Building Code, Building." |
| 419.3.11.6 | Hospital details and finishes - HVAC | 419.3.11.6 | Hospital details and finishes - HVAC | Section was increased to clarify that metal liner must be used unless it meets the additional four criteria: 1) The duct conforms to UL Class 1 Air Duct, Standard 181 with minimum rated air velocity of 4,000 feet per minute, and is pressure rated for a minimum of 4 inches water gage positive pressure and 1-inch water gage negative pressure. 2) The inner core of the duct is constructed of Chlorinated Polyethylene (CPE) material encircling a steel helix bonded to the CPE. 3) The duct has a fire-retardant metalized vapor barrier that is reinforced with crosshatched fiberglass scrim having a permanence of not greater than 0.05 perms when tested in accordance with ASTM E96 Procedure A. 4) The duct has passed an impact test equal to the UL 181 standard, conducted by a nationally recognized testing laboratory except it shall use a 25-pound weight dropped from a height of 10 feet. As a result of the test, the inner and outer surfaces of the sample shall not have ruptured, broken, torn, ripped, collapsed or separated in order for the duct to pass the test. In addition, the helix shall rebound to a cross-sectional elliptical area not less than 80 percent of the original test sample diameter. |
| - | - | 419.3.12.4 | Carbon monoxide detector. | Section added to clarify Carbon Monoxide Alarms are required to be provided in this occupancy. See Section 913.1. |
| 419.3.15 | Electrical requirements | 419.3.15 | Electrical requirements | Reference to Section 7.32 was removed to reference the overall Guidelines. Added "as complying with applicable standards of Underwriter's Laboratories, Inc. or other similarly established standards" for clarity. |
| 420 | Hydrogen cutoff rooms | 439 | Hydrogen cutoff rooms | Section moved to newly created section number 439. |
| 420.1 | Nursing homes scope | 420.1 | Nursing homes scope | Added to comply with "all applicable requirements of the code" |
| 420.3.2.2 | Resident room square footages | 420.3.2.2 | Nursing homes room square footages | Revised the items that are exclusive of the space included in the minimum for square footages from "vestibules" to "door swings into the room or entrance vestibules, whichever is greater." Planning length for bed is revised from 7'-6" to 8'. |
| 420.3.2.6 | Resident rooms toilet rooms | 420.3.2.6 | Resident rooms toilet rooms | Revised section to add statement that toilet room door cannot impede the swing of any other door into the resident room. |
| 420.3.2.7 | Resident wardrobe areas | 420.3.2.7 | Resident wardrobe areas | Revised language to include that wardrobe locker or closet will be available "at all times" and then statement, "When the wardrobe, locker or closet is designed to meet the requirements for accessibility per Chapter 11 of this code, it shall include additional accessible storage area(s) for full-length garments." |
| 420.3.3.7 | Service area sanitizer | 420.3.3.7 | Service area sanitizer | Revised section to state that a sanitizer is required 'if by the functional program as defined by the Guidelines." |
| 420.3.3.8 | Medicine preparation room | 420.3.3.8 | Medicine preparation room | Revised section to add, "If there is no linen storage in the clean utility room," medicine preparation may be part of the clean utility room in which case an additional 20 square feet dedicated for this purpose shall be required. |
| 420.3.3.9 | Equipment storage | 420.3.3.9 | Equipment storage | Minimum square footage of storage area for nursing unit equipment revised from 1 sq.ft. per bed to 2 sq.ft per bed. |
| 420.3.3.11 | Linen storage | 420.3.3.11 | Linen storage | Section revised to state that storage space be large enough to accommodate the storage of linen carts. Also added that if in compliance with the Florida Fire Prevention Code, a closed-cart system may be used and stored in an alcove open to the corridor. |
| - | - | 420.3.13.16 | Carbon monoxide detector. | Section added to clarify Carbon Monoxide Alarms are required to be provided in this occupancy. See Section 913.1. |
| 420.3.17.2 | Plumbing fixtures and minimum trim | 420.3.17.2 | Plumbing fixtures and minimum trim | Added Eye wash station(s) to room function and fixture legend. Revised title "Trim Legend" to "Fixture Legend." Revised "drinking fountain" in fixture legend to "electric drinking fountain.' Revised K, sanitizer, to state, "if required by the functional program in The Guidelines." Added footnote 2, which includes the ANSI standard for eyewash and shower equipment. |
| 420.3.22.1 | Receptacles | 420.3.22.1 | Receptacles | Revised "receptacle" to "duplex receptacle" |
| 421.1.1 | Ambulatory surgical centers scope | 421.1.1 | Ambulatory surgical centers scope | Added to comply with "all applicable requirements of the code" |
| 421.2.1.2 | Ambulatory surgical centers codes and standards | 421.2.1.2 | Ambulatory surgical centers codes and standards | Revised from chapter references to "Part I - Part 3" Ambulatory Care Facilities per new reference in AIA |
| 421.3.2 | Operating rooms | 421.3.2 | Operating rooms | Reference to Section 9.5.F was removed to reference the overall Guidelines. |
| 421.3.3 | Recovery area | 421.3.3 | Recovery area | Deleted information and Section is now "Reserved" |
| 421.3.4 | Ambulatory surgical centers details and finishes | 421.3.4 | Ambulatory surgical centers details and finishes | Reference to Section 9.5.H was removed to reference the overall Guidelines. |
| 421.3.4.1 | Drinking fountains, phone booths and vending machines | - | - | Section removed. |
| 421.3.4.3 | Threshold and expansion joint covers | - | - | Section removed. |
| 421.3.4.5 | Paper towel and soap dispensers | 421.3.4.3 | Paper towel and soap dispensers | Moved requirements in section 421.3.5 to 421.3.4.3. Revised language to state "permanently installed" single service paper towel dispensers. |
| 421.3.4.6 | Ceiling height | - | - | Section removed. |
| 421.3.4.7 | X-ray film illuminator | - | - | Section removed. |
| 421.3.5 | Elevator | 421.3.5 | Elevator | Reference to Section 9.30.B was removed to reference the overall Guidelines. |
| 421.3.5.1 | Elevator | 421.3.5.1 | Elevator | Removed reference to Chapter 69A 47, Florida Administrative Code, "uniform Fire Safety Standards for Elevators." |
| 421.3.6.4 | Ambulatory surgical centers - HVAC | 421.3.6.4 | Ambulatory surgical centers - HVAC | Section was increased to clarify that metal liner must be used unless it meets the additional four criteria: 1) The duct conforms to UL Class 1 Air Duct, Standard 181 with minimum rated air velocity of 4,000 feet per minute, and is pressure rated for a minimum of 4-inches water gage positive pressure and 1-inch water gage negative pressure.2) The inner core of the duct is constructed of ChlorinatedPolyethylene (CPE) material encircling a steel helix bonded to the CPE.3) The duct has a fire-retardant metalized vapor barrierthat is reinforced with crosshatched fiberglass scrim having a permanence of not greater than 0.05 perms when tested in accordance with ASTM E 96 Procedure A.4) The duct has passed an impact test equal to the UL181 standard, conducted by a nationally recognizedtesting laboratory (NRTL) except it shall use a 25-pound weight dropped from a height of 10 feet. As a result of the test, the inner and outer surfaces of the sample shall not have ruptured, broken, torn, ripped, collapsed or separated in order for the duct to pass the test. In addition, the helixshall rebound to a cross-sectional elliptical area not less than 80 percent of the original test sample diameter. |
| 421.3.6.5 | Ambulatory surgical centers - HVAC filter frame | - | - | Section removed. |
| 421.3.10 | Electrical requirements | 421.3.10 | Electrical requirements | Reference to Section 9.32 was removed to reference the overall Guidelines. |
| 421.3.10.1 | Electrical equipment | 421.3.10.1 | Electrical equipment | Revised to add that materials "and equipment shall be factor listed" and removed the statement regarding field labeling of equipment and materials. |
| 423.5.16 | Educational facility definitions | 423.5.16 | Educational facility definitions | Revised definition of separate building to include the purpose: "of separate fire alarm systems or sprinkler systems" and removed as required "by a 4-hour fire wall." |
| 423.11.1 | Fire-retardant treated wood | - | - | Removed section. |
| 423.11.2 | Fire-retardant treated wood | - | - |  |
| 423.11.3 | Fire-retardant treated wood - inspection panels | 423.11.2 | Fire-retardant treated wood - inspection panels | Moved requirements in section 423.11.3 to 423.11.2. |
| 423.11.4 | Evidence of compliance | 423.11.3 | Evidence of compliance | Moved requirements in section 423.11.4 to 423.11.3. |
| 423.11.5 | Interior applications | - | - | Removed section. |
| 423.11.6 | Exterior applications | - | - |  |
| 423.11.7 | Educational facility construction type - noncombustible | 423.8.1.3 | Educational facility construction type - noncombustible | Moved requirements in section 423.11.7 to 423.8.1.3 and revised to remove "wood studs" |
| 423.13.6 | Hardware in educational facilities | 423.13.6 | Hardware in educational facilities | Removed second sentence, "Projecting hardware on doors swinging into a means of egress is not considered an obstruction if the door opens flat against the wall." Revised section to include, "Smoke doors in walls used to divide corridors into separate atmospheres shall be provided with push-pull plates and are not required to have positive latching. As an exception to Section 1008.1.8.6, delayed egress locks may be used in media centers, alternative education centers, and exceptional student education centers. Delayed egress locks are prohibited at time-out rooms at all locations." |
| 423.13.7 | Safety glazing: panels and storefronts | 423.13.7 | Safety glazing: panels and storefronts | Added "In addition to the requirements of Section 2406.3, the following is considered a hazardous location and requires safety glazing" and removed specific requirements listed "shall be tempered glass, safety glass, or in fire-rated assembled impact resistant fire rated glass" as requirements in Section 2406. |
| 423.13.7.1 | Glazing requirements reference | 423.13.7.1 | Glazing requirements reference | Added glazing requirements reference to Section 2406 and removed language stating, "Storefronts shall use tempered or safety glass for all glazing below door head height." |
| 423.13.7.3 | Glazing requirements | - | - | Removed section. |
| 423.14.2.1 | Emergency rescue windows. | 423.14.2.1 | Emergency rescue windows. | Coordination with the Florida Fire Prevention Code which requires emergency rescue windows in public educational occupancies to open into an area having access to a public way. Windows for emergency rescue shall comply with NFPA 101, Florida Edition, as adopted by the Florida Fire Prevention Code, shall be operable from the inside by a single operation, and shall be labeled “EMERGENCY RESCUE – KEEP AREA CLEAR.” Hinged emergency rescue windows shall swing in the direction of egress. |
| 423.14.3 | Other potential hazards in facilities | 423.14.3 | Other potential hazards in facilities | Remove "uninsulated hot water" and added "ductwork, fans, light fixtures." |
| 423.15.1 | Conceal piping | 423.15.1 | Gas and fluid piping | Revised section title. |
| - | - | 423.15.1.1 | Flammable liquids/gases | Revised section 423.15.1 into three separate sub-sections for clarity. 423.15.1.1 added the exception "piping may be located within corridors provided that they are enclosed in a minimum one (1) hour fire rated enclosure." |
| - | - | 423.15.1.2 | Piping systems |  |
| - | - | 423.15.1.3 | Main supply valve |  |
| 423.15.2 | Return air | 423.15.2 | Air Plenums | Revised title and added fire rating construction requirements for plenum spaces between corridor ceiling and floor or roof above as well as exception. |
| 423.15.3 | Residential range hood for facilities | 423.15.3 | Residential range hood for facilities | Revised section to add that residential ranges may be used, "for staff use or student education." In addition, Hood fire suppression systems are not required to be installed. |
| - | - | 423.15.5 | Chemistry and Science classrooms | Added new section for ventilation requirements in labs. Systems in labs must be designed so that chemicals originating from the space are not recirculated. Also added exception to provide requirements for emergency exhaust. |
| - | - | 423.15.6 | Air make-up | Added new section for air make-up requirements for HVAC systems for educational facilities. |
| 423.16.1 | Plumbing standards for educational facilities | 423.16.1 | Plumbing standards for educational facilities | Revised exception to state single unisex toilet room included in ESE classrooms and "Unisex toilets shall not be provided in addition to group toilets in assembly occupancies." |
| - | - | 423.16.1.1 | Toilet facilities for educational assembly occupancies | Added new sub-section outlining requirements for assembly occupancies. |
| - | - | 423.16.1.2 | Toilet locations for educational facilities | Added new sub-section outlining requirements for locations and path of travel. |
| - | - | 423.16.12 | Floor drains in equipment rooms of educational facilities | Added new section stating equipment rooms which are also used as plenum shall not have a floor drain. |
| 423.18.1.1 | Assembly occupancy calculations for auditorium | 423.18.1.1 | Assembly occupancy calculations for auditorium | Revised number of fixed seats requirement from 13 net square feet to 15 net square feet per person. |
| 423.18.1.2 | Assembly occupancy calculations for gymnasium/gymnatorium with stage | 423.18.1.2 | Assembly occupancy calculations for gymnasium/gymnatorium with stage | Revised number of fixed seats and telescoping bench type seats requirement from 13 net square feet to 15 net square feet per person. |
| 423.18.1.3 | Assembly occupancy calculations for dining rooms/cafetorium with state/multipurpose room | 423.18.1.3 | Assembly occupancy calculations for dining rooms/cafetorium with state/multipurpose room | Revised the main floor area requirement from 13 net square feet to 15 net square feet per person. |
| 423.20.3 | State educational facility custodial closets and storage | 423.20.3 | State educational facility custodial closets and storage | Revised language from "conveniently located" to "located" and added that the travel distance to the nearest custodial closet shall not exceed one hundred fifty (150) feet. |
| 423.28 | Existing relocatable buildings and factor built schools | - | - | Removed section. |
|  |  | 424.1 | Public swimming pools and bathing places. | Revise language to be consistent with changes made in Rule 64E-9. Public swimming pools and bathing places shall comply with the design and construction standards of this section. NOTE: Other administrative and programmatic provisions may apply. See Department of Health (DOH) Rule 64E-9, Florida Administrative Code and Chapter 514, Florida Statutes. “Bathing load" means the maximum number of persons allowed in the pool or bathing place at one time. |
|  |  |  |  | "Collector tank" means a reservoir, with a minimum of 2.25 square feet water surface area open to the atmosphere, from which the recirculation or feature pump takes suction, which receives the gravity flow from the main drain line and surface overflow system or feature water source line. |
|  |  |  |  | “Effective Barrier” – A barrier which consists of a building, or equivalent structure, plus a 48 inch minimum height fence on the remaining sides or a continuous 48 inch minimum height fence. All access through the barrier must have one or more of the following safety features: alarm, key lock or self-locking doors and gates. Safety covers that comply with the American Society for Testing Materials standard F1346 may also be considered as an effective barrier. |
|  |  |  |  | “Marking” or “Markings” – Refers to the placement and installation of visual marking cues to help patrons identify step, bench and swimout outlines, slope break location, depth designations, and NO ENTRY and NO DIVING warnings. When markings are specified by code to be dark the term dark shall mean a Munsell Color Value from zero to four. |
|  |  |  |  | "Wet deck area" means the 4-foot-wide (1219 mm) unobstructed pool deck area around the outside of the pool water perimeter, curb, ladders, handrails, diving boards, diving towers, or pool slides, waterfalls, water features, starting blocks, planters, or lifeguard chairs. |
|  |  | 424.1.1 | Sizing | Revise language to be consistent with changes made in Rule 64E-9. The bathing load for conventional swimming pools and special purpose pools shall be computed on the basis of one person per five gallons per minute (gpm) of recirculation flow. The bathing load for wading pools and interactive water features shall be established by averaging one person per 20 square feet of pool area and one person per 5 gallons per minute of filter rate. The bathing load for spa type pools shall be based on one person per each 10 square feet of surface area. The filtration system shall be capable of meeting all other requirements of these rules while providing a flowrate of at least one gallon per minute for each living unit at transient facilities and three-fourths gallon per minute at non-transient facilities. All other types of projects shall be sized according to the anticipated bathing load and proposed uses. For the purpose of determining minimum pool size only, the pool turnover period used cannot be less than three hours. |
|  |  | 424.1.2.1 | Pool structure. | Revise language to be consistent with changes made in Rule 64E-9. Pools shall be constructed of concrete or other impervious and structurally rigid material. All pools shall be watertight, free from structural cracks and shall have a nontoxic smooth and slip-resistant finish. Floors and walls shall be white or pastel in color and shall have the characteristics of reflecting rather than absorbing light. Tile used in less than 5 feet (1524 mm) of water must be slip resistant. A minimum 4 inch tile line shall be installed at the water line, but shall not exceed 12 inches in height if a dark color is used. Gutter type pools may substitute 2-inch tile along the pool wall edge of the gutter lip. |
| 424.1.2.2.2 | Walls and corners. | 424.1.2.2.2 | Walls and corners. | Revise language to be consistent with changes made in Rule 64E-9. All pool walls shall have a clearance of 15 feet (4572 mm) perpendicular to the wall. Offset steps and spa coves are exempt from this clearance requirement. Where interior steps protrude into the pool resulting in less than 15 feet of clearance from any wall such protrusion shall not exceed six feet on any perpendicular line from a tangent to any pool wall from which the steps emanate. The upper part of pool walls in areas 5 feet deep or less shall be within 5 degrees (4572 mm) vertical for a minimum depth of 2½ feet (762 mm) from which point the wall may join the floor with a maximum radius equal to the difference between the pool depth and 2½ feet. The upper part of pool walls in areas over 5 feet deep shall be within 5 degrees vertical for a minimum depth equal to the pool water depth minus 2½ feet (762 mm) from which point the wall may join the floor with a maximum radius of 2½ feet (762 mm). Corners shall be a minimum 90-degree angle. The corner intersections of walls which protrude or angle into the pool water area shall be rounded with a minimum radius of 2 inches (51 mm). |
| 424.1.2.2.3.2 |  | 424.1.2.2.3.2 |  | Revise language to be consistent with changes made in Rule 64E-9. Any transition in floor slope shall occur at a minimum of 5 feet (1524 mm) of water depth. A slope transition must have a 2 to 6 inch wide dark contrasting tile marking across the bottom and must extend up both sides of the pool at the transition point. The marking shall be continuous except for recessing grouting. A slope transition must have a safety line mounted by use of recessed cup anchors, 2 feet (610 mm) before the contrasting marking, towards the shallow end. The safety line shall have visible floats at maximum 7-foot (2134 mm) intervals |
| 424.1.2.3.1 | Depth markings. | 424.1.2.3.1 | Depth and markings. | Revise language to be consistent with changes made in Rule 64E-9. Clarify marking of pool depth. Depth and markings shall meet the following criteria: 1. The minimum water depth shall be 3 feet in shallow areas and 4 feet in deep areas. 2. Permanent depth markings followed by the appropriate full or abbreviated words "FEET", “FT” or "INCHES", “IN” shall be installed in minimum 4-inch-high (102 mm) numbers and letters on a contrasting background. Depth markers shall indicate the actual pool depth, within 3 inches (76 mm), at normal operating water level when measured 3 feet (914 m3) from the pool wall. Symmetrical pool designs with the deep point at the center may be allowed provided a dual marking system is used which indicates the depth at the wall and at the deep point. 3. At a minimum, the markings shall be located on both sides of the pool at the shallow end, slope break, deep end wall and deep point (if located more than five feet from the deep end wall). Depth markings shall be legible from inside the pool and also from the pool deck. The maximum perimeter distance between depth markings is 25 feet (7620 mm). Pool size and geometry may necessitate additional depth marking placements about all sides of the pool to meet this requirement. 4. When a curb is provided, the depth markings shall be installed on the inside and outside or top of the pool curb. When a pool curb is not provided, the depth markings shall be located on the inside vertical wall at or above the water level and on the edge of the deck within 2 feet of the pool water. When open type gutter designs are utilized, depth markers shall be located on the back of the gutter wall. 5. When deck level perimeter overflow systems are utilized, additional depth marking signs shall be posted nearby or placed on adjacent fencing or walls and the size shall be increased so they are recognizable from inside the swimming pool. Alternatively tile depth markers may be placed at the top of the pool wall just under the water level. Depth markers placed on the pool deck shall be within 3 feet of the water. 6. Those areas of the pool that are not part of an approved diving bowl shall have dark contrasting tile 4-inch-high (102 mm) "NO DIVING" markings installed along the perimeter of the pool on the top of the pool curb or deck within 2 feet (610 mm) of the pool water with a maximum perimeter distance of 25 feet (7620 mm) between markings. A 6-inch tile with a 4-inch (102 mm) or larger red, international "NO DIVING" symbol may be substituted for the "NO DIVING" markings. 7. All markings shall be tile, except that pools constructed of fiberglass, thermoplastic or stainless steel may substitute other type markings when it can be shown that said markings are permanent and will not fade over time. This exemption does not extend to concrete pools that are coated with fiberglass. Tile alternative examples include stone or manufactured plaques with engraved or sandblasted numbers and characters with permanent paint. Permanent appliqués may be used for fiberglass, thermoplastic or stainless steel pools. All markings installed on horizontal surfaces shall have a slip resistant finish. Markings shall be flush with the surrounding area where placed and recessed if necessary to provide a smooth finish that will avoid creation of an injury hazard to bathers. Pools that are not conducive to tile can employ other equivalent markings as stated above. |
| 424.1.2.3.3 | Lane markings. | 424.1.2.3.3 | Lane markings. | Revise language to be consistent with changes made in Rule 64E-9. Clarify when and where lane marking may be used. Pools that are not intended to be utilized for officially sanctioned competition may install lap lane markings provided they meet the following criteria: the markings must be 2 to 6 inches (102 mm) wide, they must terminate 5 feet (1524 mm) from the end wall in a "T" with the "T" bar at least 18 inches (1524 mm) long, they must be placed at 7-foot (2134 mm) intervals on center and be no closer than 4 feet (1219 mm) from any side wall, steps or other obstructions. Floating rope lines associated with lap lanes must not obstruct the entrance or exit from the pool and are prohibited when the pool is open for general use. |
| 424.1.2.3.4 | Targets. | 424.1.2.3.4 | Targets. | Revise language to be consistent with changes made in Rule 64E-9. ools that are not intended for officially sanctioned competition may have a 2 to 6 inch (102 mm) wide 18-inch by 18-inch (457 mm by 457 mm) targets (+) installed on the pool wall. |
| 424.1.2.5.1 | Ladders. | 424.1.2.5.1 | Ladders. | Revise language to be consistent with changes made in Rule 64E-9. Ladders shall be of the cross-braced type and shall be constructed of corrosion-resistant materials and be securely anchored into the pool deck. Clearance between the ladder and pool wall shall be between 3 to 6 inches (76 mm to 152 mm). Ladders shall extend at least 28 inches (711 mm) above the pool deck. Ladder bottom braces shall have intact end caps or bumpers that rest firmly against the pool wall. |
| 424.1.2.5.3 | Stairs. | 424.1.2.5.3 | Stairs. | Revise stair design criteria including a max. width. Stairs shall have a minimum tread width of 10 inches (254 mm) and a maximum width of 48 inches for a minimum tread length of 24 inches (610 mm) and a maximum riser height of 10 inches (254 mm). Treads and risers between the top and bottom treads shall be uniform to within 1/2 inch in width and height. The riser heights shall be measured at the marked step edges and the differences in elevation shall be considered the riser heights. The front ¾ to 2 inches (19.1 to 51 mm) of the tread and the top 2 inches (51mm) of the riser shall be tile, dark in color, contrasting with the interior of the pool. Tile shall be slip resistant. Bullnose tile may be used when the ¾ inch (19 mm) segment is placed on the tread or horizontal surface and the 2-inch (51 mm) segment is placed on the riser or vertical surface. |
|  |  | 424.1.2.5.4 | Swimouts. | Revise language to be consistent with changes made in Rule 64E-9. Swimouts shall extend 18 to 24 inches (610 mm) back from the pool wall, shall be 4 to 5 feet (1219 mm to 1524 mm) wide, shall be a maximum of 12 inches (305 mm) below the deck, unless stairs are provided in the swimout, and shall be located only in areas of the pool greater than 5 feet (1524 mm) deep. Pools that do not utilize a continuous perimeter overflow system must provide a wall return inlet in the swimout for circulation. A permanent dark contrasting colored band of tile shall be installed at the intersection of the pool wall and the swimout and must extend 2 inches (51 mm) on the horizontal and vertical surfaces. Tile must be slip resistant. Bullnose tile may be substituted and installed in accordance with Section 424.1.2.5.3 above. |
| 424.1.2.5.5 | Handrails and grabrails. | 424.1.2.5.5 | Handrails and grabrails. | Revise language to be consistent with changes made in Rule 64E-9. Delete requirement for grab rails at swimouts. Handrails shall be provided for all stairs, shall be anchored in the bottom step and the deck. Where "figure 4" deck- mounted type handrails are used, they shall be anchored in the deck and extend laterally to any point vertically above the bottom step. Grabrails must be mounted in the pool deck at each side of recessed steps. Handrails and grabrails shall extend at least 28 inches (28 mm) above the step edge and deck. |
| 424.1.2.5.6 | Disabled access. | 424.1.2.5.6 | Disabled access. | Editorial correction. Permanent or portable steps, ramps, handrails, lifts or other devices designed to accommodate handicapped individuals in swimming pools may be provided. Lifts mounted into the pool deck shall have a minimum four 4-foot-wide (1219 mm) deck behind the lift mount. |
| 424.1.2.6 | Obstructions. | 424.1.2.6 | Obstructions. | Revise language to be consistent with changes made in Rule 64E-9. Clarify when pool design may include obstructions. The pool water area shall be unobstructed by any type structure unless justified by engineering design as a part of the recirculation system. Engineering design and material specifications shall show that such structures will not endanger the pool patron, can be maintained in a sanitary condition and will not create a problem for sanitary maintenance of any part of the pool, pool water, or pool facilities. Structures in accord with the above shall not be located in a diving bowl area or within 15 feet (4572 mm) of any pool wall. Exceptions: 1. Stairs, ladders and ramps, necessary for entrance/exit from the pool are not considered obstructions. 2. Underwater seat benches may be installed in areas less than five feet (1524 mm) deep. Bench seats must be 14 to 18 inches (356 to 457 mm) wide and must have a dark contrasting tile marking on the seat edge extending two inches (51 mm) on the horizontal and vertical surface. tile must be slip resistant. Bullnose tile may be substituted and installed in accordance with Section 424.1.2.5.3. Benches shall not protrude into the 15 foot clearance requirement of Section 424.1.2.6. |
| 424.1.2.7 | Diving areas. | 424.1.2.7 | Diving areas. | Revise language to be consistent with changes made in Rule 64E-9. Diving facilities shall meet the minimum requirements of the FINA dimensions for diving facilities in accordance with the 1998-2000 FINA Handbook and include the following: 1. Diving boards or platforms with heights of less than the established standard shall meet the dimensional requirements of the next greater height. 2. Diving boards, platforms and ladders shall have a nonabsorbent, slip-resistant finish and be of sufficient strength to safely carry the anticipated loads. Diving equipment one meter and greater shall have guard rails which extend to the edge of the pool wall. All diving boards over 21 inches (533 mm) from the deck shall be provided with a ladder. Diving boards or platforms shall not be installed on curved walls where the wall enters into the defined rectangular diving area specified in this section. Adjacent platform and diving boards shall be parallel. 3. The location of pool ladders shall be such that the distance from the ladder to any point on a diving board or platform centerline is not less than the plummet to side wall dimension (b) indicated in the FINA standards. Trampoline-type diving facilities are prohibited. 4. Diving targets may be installed in accordance with FINA standards |
|  |  | 424.1.3.1.6 | Ten percent of the deck along the pool perimeter may be obstructed. | Revise language to be consistent with changes made in Rule 64E-9. Obstructions shall have a wet deck area behind or through them, with the near edge of the walk within 15 feet (4572 mm) of the water except approved slide obstructions shall have the near edge of the walk within 35 feet of the water. These obstructions must be protected by a barrier or must be designed to discourage patron access. When an obstruction exists in multiple areas around the pool the minimum distance between obstructions shall be 4 feet (1219 mm). |
| - | - | 424.1.3.1.9. | All public pools shall be surrounded by a minimum 48 inch high fence | Add new section to require fences around public pools. The fence shall be continuous around the perimeter of the pool area that is not otherwise blocked or obstructed by adjacent buildings or structures and shall adjoin with itself or abut to the adjacent members. Access through the barrier other than from doored exits of adjacent building(s) shall be through self-closing self-latching lockable gates of 48 inch minimal height with the latch located a minimum of 54 inches from the bottom of the gate or at least 3 inches below the top of the gate on the pool side. Gates shall open outward away from the pool area. Consideration shall be given to the U.S. Consumer Product Safety Commission (CPSC) Pub. No. 362 guidelines. Safety Covers that comply with ASTM F 1346 do not satisfy this requirement. |
| 424.1.4.2.1 | Outdoor pool lighting | 424.1.4.2.1 | Outdoor pool lighting | Clarify minimum overhead lighting requirement is for wet deck surfaces. Overhead lighting shall provide a minimum of 3 footcandles (30 lux) of illumination at the pool water surface and the pool wet deck surface. Underwater lighting shall be a minimum of ½ watt per square foot of pool water surface area. |
| 424.1.4.2.2 | Indoor pool lighting | 424.1.4.2.2 | Indoor pool lighting | Revise language to be consistent with changes made in Rule 64E-9. Clarify minimum lighting requirement is for wet deck surfaces. Overhead lighting shall provide a minimum of 10 foot candles of illumination at the pool water surface and the pool wet deck surface. Underwater lighting shall be a minimum of 8/10 watt per square foot of pool surface area. |
| 424.1.4.2.3 | Underwater lighting | 424.1.4.2.3 | Underwater lighting | Revise language to be consistent with changes made in Rule 64E-9. Provides the Department of Health shall be the final authority in determining criteria for underwater lighting. Underwater lighting shall utilize transformers and low-voltage circuits with each underwater light being grounded. The maximum voltage for each light shall be 15 volts and the maximum incandescent lamp size shall be 300 watts. The location of the underwater lights shall be such that the underwater illumination is as uniform as possible and shall not be less than 18 inches (457 mm) below the normal operating water level. All underwater lights which depend upon submersion for safe operation shall have protection from overheating when not submerged. Underwater lighting requirements can be waived when the overhead lighting provides at least 15 footcandles (150 lux) of illumination at the pool water surface and pool wet deck surface. Alternative lighting systems which do not utilize electricity in the pool or on the pool deck, such as fiber-optic systems, may be utilized if the applicant demonstrates to reasonable certainty that the system development has advanced to the point where the department is convinced that the pool illumination is equal to the requirements in Sections 424.1.4.2.1 and 424.1.4.2.2 above. |
| 424.1.4.2.4 | Overhead wiring | 424.1.4.2.4 | Overhead wiring | Revise language to be consistent with changes made in Rule 64E-9.Minimum criteria for clearance from overhead conductors in addition to the requirement of the Electrical Code. Overhead service wiring shall not pass within an area extending a distance of 10 feet horizontally away from the inside edge of the pool walls, diving structures, observation stands, towers, or platforms. Electrical equipment wiring and installation including the grounding of pool components shall comply with Chapter 27 of the Florida Building Code, Building. |
| 424.1.5.1 | Equipment | 424.1.5.1 | Equipment | Revise language to be consistent with changes made in Rule 64E-9.Minimum criteria for the protection of equipment and piping. Equipment designated by the manufacturer for outdoor use may be located in an equipment area, all other equipment must be located in an equipment room or enclosure. Plastic pipe subject to a period of prolonged sunlight exposure must be coated to protect it from ultraviolet light degradation. An equipment area shall be surrounded with a fence at least 4 feet (1219 mm) high on all sides not confined by a building or equivalent structure. A self-closing and self-latching gate with a permanent locking device shall be provided if necessary for access. An equipment room shall be protected on at least three sides and overhead. The fourth side may be a gate, fence, or open if otherwise protected from unauthorized entrance. An equipment enclosure shall be lockable or otherwise protected from unauthorized access. |
| 424.1.5.3 | Materials. | 424.1.5.3 | Materials. | Revise language to be consistent with changes made in Rule 64E-9. Clarify the requirement is includes ancillary equipment not just equipment rooms. The equipment enclosure, area or room floor shall be of concrete or other nonabsorbent material having a smooth slip-resistant finish and shall have positive drainage, including a sump pump if necessary. Ancillary equipment, such as a heater, not contained in an equipment enclosure or room shall necessitate an equipment area as described above |
| 424.1.5.6 | Size. | 424.1.5.6 | Size. | Revise language to be consistent with changes made in Rule 64E-9. Clarify the requirement is to equipment enclosures not just equipment. The size of the equipment enclosure, room or area shall provide working space to perform routine operations. Clearance shall be provided for all equipment as prescribed by the manufacturer to allow normal maintenance operation and removal without disturbing other piping or equipment. In rooms with fixed ceilings, the minimum height shall be 7 feet (2137 mm). |
| 424.1.5.8 | Storage. | 424.1.5.8 | Storage. | Revise language to be consistent with changes made in Rule 64E-9. larify the requirement is to equipment enclosures not just equipment. Equipment enclosures, rooms or areas shall not be used for storage of chemicals emitting corrosive fumes or for storage of other items to the extent that entrance to the room for inspection or operation of the equipment is impaired. |
| 424.1.6.1 | Sanitary facilities. | 424.1.6.1 | Sanitary facilities. | Revise language to be consistent with changes made in Rule 64E-9. Establish the distance as a sanitary facilities as a walking distance. Separate sanitary facilities shall be provided and labeled for each sex and shall be located within a 200-foot (60 960 mm) walking distance of the nearest water’s edge of each pool served by the facilities. Exception: Where a swimming pool serves only a designated group of residential dwelling units and not the general public, poolside sanitary facilities are not required if all living units are within a 200-foot (60 960 mm) radius of the nearest water’s edge, are not over three stories in height unless serviced by an elevator, and are each equipped with private sanitary facilities. |
| 424.1.6.1.1 | Required fixtures. | 424.1.6.1.1 | Required fixtures. | Revise language to be consistent with changes made in Rule 64E-9. Add requirement for diaper changing station to resteoom requirement. Fixtures shall be provided as indicated on Table 424.1.6.1. When multiple fixture sets are required and separate facilities are provided for each sex the fixtures used in ancillary family style restrooms can be used to meet the requirements of Section 424.1..6.1.1 Diaper changing tables shall be provided at facilities that cater to families with small children. |
| 424.2 | Definition: Swimming pool main outlet | 424.2 | Definition: Swimming pool main suction outlet | Revised title from Main outlet to Main "suction" outlet. |
| 424.2.3 | Swimming pool mechanical requirements | 424.2.3 | Swimming pool mechanical requirements | Revised language from "plumbing' system to "process piping" system. |
| 424.2.6.1 | Private swimming pool conformance standard | 424.2.6.1 | Private swimming pool conformance standard | Added ANSI/APSP 7 to list of standards. |
| 424.2.6.3 | Private swimming pool water velocity | 424.2.6.3 | Private swimming pool water velocity | Added information to section, "Main suction outlet velocity must comply with ANSI/APSP 7." |
| 424.2.6.6 | Private swimming pool entrapment protection | 424.2.6.6 | Private swimming pool entrapment protection | Added information to section, "Outlets must be installed in accordance with requirements of ANSI/APSP 7." Removed all subsections of 424.2.6.6. |
| 424.2.8.4 | Combination valves | 424.2.8.4 | Combination valves | Revised section to remove requirement for approval from administrative authority to state, "be installed per manufacturer's installation instructions." |
| 424.2.19 | Final inspection | 424.2.19 | Final inspection | Revised language to clarify that "electrical and barrier code" inspections will be completed after pool is completely filled with water. Added exception that vinyl liner and fiberglass pools are required to be filled with water upon installation. |
| 424.2.20 | Filters | 424.2.20 | Filters | Removed 'the entire design of matched" language for clarity. |
| 428.4 | Residential manufactured buildings design plan and systems approval | 428.4 | Residential manufactured buildings design plan and systems approval | Revised language within the requirements of third party plan review: to remove the term "permanent foundation" to state "foundation" and removed "and is not designed to be moved once so erected or installed." Added "in accordance with this code" |
| 430.6.2 | Mausoleum and columbarium mechanical system crypt requirements | 430.6.2 | Mausoleum and columbarium mechanical system crypt requirements | Added information to exception 2: "except that for Family Mausoleum Units where all crypts are bordering an exterior wall, pressure relief ventilation shall be provided from the crypt to the outside of the mausoleum through the exterior wall or roof." |
| 430.7.2 | Crypt relief vent | 430.7.2 | Crypt relief vent | Revised section to remove requirement for two pressure relief vents and clarified to include requirements for when crypt borders and exterior wall and crypts not bordering an exterior wall. |
| 434.3 | Physical Plant standards | 434.3 | Assisted living facilities codes and standards | Revised title of section to "Codes and standards for the design and construction of Assisted Living Facilities." Relocated information in subsections to 434.4 and revised section scope to include referenced code, statutes, and guidelines. |
| 434.3 | Physical plant | 434.4 | Additional physical plant requirements for assisted living facilities | Removed sections 434.3.1.1 and 434.3.1.2. Section revision added "In addition to the codes and standards referenced in section 434.3 of the code, the following minimum essential facilities shall apply to all new assisted living facilities." |
| 434.3.1.3 | Indoor radon testing | 434.4.1 | Indoor radon testing | Relocated section. |
| 434.4 | Extended congregate care | 434.5 | Extended congregate care | Added new section number for relocated requirements. |
| 437.2.2.2 |  | 437.2.2.2 |  | Hospice patient rooms must be accessible. Inpatient sleeping rooms shall be made accessible in accordance with the requirements of the Florida Building Code, Section11-6.1(1). |
| - | - | 437.2.6.1.1 | Carbon monoxide detector. | Section added to clarify Carbon Monoxide Alarms are required to be provided in this occupancy. See Section 913.1. |
| Chapter 5: General Building Heights and Areas |  |  |  |  |
| Section | Requirement | Section | Requirement |  |
| 502.1 | Definitions | 502.1 | Definitions | Basement - revised definition by replacing "grade" with "grade plane." Deleted Item 3 criteria for a basement to be considered a story when the finished floor surface of the floor above the basement is more than 12 feet above the finished ground level at any point. Revised "Industrial Equipment Platform" to read "Equipment Platform." Mezzanine - revised definition by deleting requirement for the mezzanine to not have an aggregate floor area of not more than one-third of the area of the room or space in which located. |
| - | - | 503.1.1 | Special industrial occupancies | Unlimited area permitted for certain special industrial occupancies. |
|  |  | 503.1.1 | Special industrial occupancies | Delete requirement and reserve section. Reserved. |
| 503.1.1 | Basements | 503.1.4 | Basements | Section relocated. |
| 503.1.2 | Group A and E basements | 503.1.5 | Group A and E basements | Section relocated. |
| 503.1.3 | Buildings on same lot | 503.1.2 | Buildings on same lot | Section relocated. |
| 503.1.4 | Type I construction | 503.1.3 | Type I construction | Section relocated. |
| Table 503 | Allowable Height and Building Areas | Table 503 | Allowable Height and Building Areas | Group H-5 permitted one additional story for Type I construction (4 stories max for Type IA and 3 stories max for Type IB).New footnote identifies general exceptions to Table 503 throughout this chapter.New note d refers to Section 415.5 for limitations on Groups H-2 and H-3. |
| 504.2 | Automatic sprinkler system increase | 504.2 | Automatic sprinkler system increase | Exceptions 1 and 2 revised to clarify that the reference is to "fire areas" with an occupancy in the groups specified |
| 505.1 | Mezzanines, general | 505.1 | Mezzanines, general | First sentence revised to specifically state mezzanines in compliance with Section 505 instead of "this section". |
| 505.2 | Area limitation | 505.2 | Area limitation | Reference to area revised to read "floor area". Mezzanine area permitted to not exceed one half of the area of the room for Type I or II construction where building is equipped with sprinklers system and an emergency voice/alarm communication system. |
| 505.3 | Egress | 505.3 | Egress | Reference to accessible means of egress relocated as an exception to Section 505.3 |
| 505.4 | Openness | 505.4 | Openness | Deleted existing Exception 5 applicable only to Group F and added new Exception 5 applicable to all groups except H and I permitting the mezzanine to not be open to the room it is located provided requirements specified are met. |
| 505.5 | Industrial equipment platforms | 505.5 | Equipment platforms | "Industrial equipment platforms" revised to read "Equipment platforms." |
| 505.5.1 | Area limitation | 505.5.1 | Area limitation | "Industrial equipment platforms" revised to read "Equipment platforms." |
| 505.5.2 | Fire suppression | 505.5.2 | Fire suppression | "Industrial equipment platforms" revised to read "Equipment platforms." |
| 506.1 | Area modifications, general | 506.1 | Area modifications, general | Area increase calculations for frontage and sprinklers have been simplified by eliminating the need to multiply and divide by 100. |
| 506.1.1 | Basements | 506.1.1 | Basements | Language revised to clarify that to qualify for this section, the basement must not be counted as a story above grade plane and that the area of such basement does not exceed the area permitted for a building with no more than one story above grade plane. |
| 506.2 | Frontage increase | 506.2 | Frontage increase | Area increase calculations for frontage have been simplified by eliminating the need to multiply by 100. |
| 506.2.1 | Width limits | 506.2.1 | Width limits | Language regarding the calculation of W has been modified to clarify that the W/30 limitation is applied for each segment of frontage, rather than after the weighted average is calculated. Provisions relating to the value of W/30 up to 2.0 has also been revised for clarity. |
| 506.3 | Automatic sprinkler system increase | 506.3 | Automatic sprinkler system increase | Area increase calculations for sprinklers have been simplified by eliminating the need to multiply by 100. Exceptions have been modified to clarify that the sprinkler system increase does not apply to Group H-1, H-2, or H-3. Also, with Groups H-2 and H-3, increases are permitted in mixed us buildings providing the allowable area is to be calculated in accordance with Section 508.3.3.2 (sum of areas ratio for separated uses) with the sprinkler increase only applicable to the portions of the building not classified as Groups H-2 or H-3. |
| 506.4 | Area determination | 506.4 | Area determination | "Story" revised to read "story above grade plane." "Floor" revised to read "story." |
| - | - | 506.4.1 | Mixed occupancies | New provision addresses the application of Section 506.4 (maximum total building area) when mixed occupancies are separated in accordance with 508.3.3. Limits the maximum total building area such that the sum of the ratios for each such area on all floors as calculated according to Section 508.3.3.2 does not exceed 2 for two-story buildings and 3 for buildings three stories and higher. |
| - | - | 507.1 | Unlimited area buildings, general | New general scoping statement added regarding application of the unlimited area provisions of Section 507. |
| 507.2 | Sprinklered, one story | 507.3 | Sprinklered, one story | Exceptions 1 modified by requiring compliance with Section 903.3.1.1 and NFPA 230 for Type I and II rack storage facilities that do not have access by the public. New Exception 3 permits unlimited area Groups A-1 and A-2 occupancies of any construction other than Type V meeting the specified criteria. |
| 507.4 | Reduced open space | 507.5 | Reduced open space | Permits the reduced open space to now apply to buildings in accordance with Section 507.6 (Group A-3) and Section 507.10 (One-story Group A). |
| 507.6 | High-hazard use groups | 507.7 | Group H occupancies | Requirements for limited floor areas of Groups H-2, H-3, and H-4 occupancies in unlimited area buildings containing Groups F and S has been clarified to better establish the requirements for compliance. |
| - | - | 507.11 | Covered mall buildings and anchor stores | New provisions providing a scoping and cross-reference to unlimited area covered mall buildings not exceeding 3 stories in height complying with Section 402.6. |
| 508.2 | Group S-2 enclosed parking garage with Group A, B, M or R above | 509.2 | Group S-2 enclosed or open parking garage with Group A, B, M, R or S above | Section has been modified to now include open parking garages as well as enclosed and permits Group S above as well as other occupancies stated. Condition 3 has been modified to allow multiple Group A uses above the horizontal assembly providing separation from the parking garage and permits Group S above. Condition 4 has been modified to recognize the applicability of open parking garages to this section. Exception 1 is modified to allow multiple Group A uses below the horizontal assembly providing separation from the parking garage. Condition 5 has been modified to clarify that the building height is limited to the building occupancy resulting in the smaller allowable height as measured from grade. |
|  |  | 509.4 | Parking beneath Group R. | Correct incorrect reference. Where a maximum one-story above grade plane Group S-2 parking garage, enclosed or open, or combination thereof, of Type I construction or open of Type IV construction, with grade entrance, is provided under a building of Group R, the number of stories to be used in determining the minimum type of construction shall be measured from the floor above such a parking area. The number of stories to be used in determining the height in stories in accordance with Section 903.6 shall include the parking garage as a story. The floor assembly between the parking garage and the Group R above shall comply with the type of construction required for the parking garage and shall also provide a fire-resistance rating not less than the mixed occupancy separation required in Section 508.3.3 |
| 508.7.1 | Fire suppression (open parking garage beneath Groups A, I, B, M and R) | 509.7.1 | Fire suppression (open parking garage beneath Groups A, I, B, M and R) | Section revised for clarity regarding specific references for the separation assemblies (Fire barriers in accordance with Section 706, Horizontal assemblies in accordance with Section 711, Self-closing doors in accordance with Section 715. |
| - | - | 509.8 | Group B or M with Group S-2 opening parking garage above | New section providing prescriptive alternatives to the general provisions for offices and/or retail stores on the first floor of open parking structures. |
| Chapter 6: Types of Construction |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| 602.2 | Types I and II | 602.2 | Types I and II | Revised section to add, "except as permitted in Section 603 and elsewhere in this code" to add cross reference information needed to eliminate misinterpretation of this section. |
| 602.4 | Type IV - glue laminated timber and sawn wood | 602.4 | Type IV - glue laminated timber and sawn wood | Added statement and reference to Table 602.4 to clarify required dimensions for both glue laminated and sawn wood. |
| 603.1 | Allowable materials for Type I and II construction - Item 1 | 603.1 | Allowable materials for Type I and II construction - Item 1 | Revised section to remove reference to Table 601 and relocated text from Item 3 of Note C in Table 601 as an exception to Item 1.3 in this section. Exception now states: 'In buildings of Type I construction exceeding two stories in height, fire-retardant-treated wood is not permitted in roof construction when the vertical distance from the upper floor to the roof is less than 20 feet." |
| 603.1 | Allowable materials for Type I and II construction - Item 9 | 603.1 | Allowable materials for Type I and II construction - Item 9 | Requirement was revised to add the term "stages" to the requirement for platforms to be constructed in accordance with Section 410. Section also provides new specific referencing by revising "410" to "410.3 and 410.4." |
| 603.1 | Allowable materials for Type I and II construction - Item 10 | 603.1 | Allowable materials for Type I and II construction - Item 10 | Revised language for clarity to remove "similar appendages" and add "similar projections" to the requirement and for consistency with similar terminology changes throughout the code. |
| 603.1 | Allowable materials for Type I and II construction - Item 18 | 603.1 | Allowable materials for Type I and II construction - Item 18 | Added language to requirement, "determined on the basis of fire-resistance tests in accordance with Section 703.2" regarding sprayed fire-resistant materials. |
| Table 601 | Structural frame fire resistance rating requirements | Table 601 | Structural frame fire resistance rating requirements | Revised language in table for structural frame to remove the elements, "including columns, girders, trusses", which is a redundant and incomplete list of what is listed in footnote a. |
| Table 602 | Fire resistance rating requirements for exterior walls | Table 602 | Fire resistance rating requirements for exterior walls | Revised table to incorporate footnote changes as noted below. |
| Table 602 | Note b | Table 602 | - | Deleted existing footnote b that permitted no fire-resistance rating for exterior walls of Group R-3 and Group U accessory to Group R-3, when fire separation distance is 3 feet or more. |
| Table 602 | - | Table 602 | Note b | Added new footnote referencing Section 406.1.2 for special requirements for Group U. |
| Table 602 | - | Table 602 | Note d | Added new footnote to coordinate exterior wall rating requirements for open parking garages with existing specific requirements in Section 406. |
| Table 602 | - | Table 602 | Note d | Add footnote d reference in column headed “GROUP A, B, E, F-2, I, R b , S-2, Ub “ to the fire ratings in rows “10  x < 20” and “20  x < 30”. (See Attachment) |
| - | - | Table 602 | Fire resistance rating requirements for exterior walls | Added footnote e to clarify that the fire resistance rating of each wall in each story of a building must be determined separately. |
| - | - | Table 602.4 | Wood member size | Added Table to clarify and provide an easier determination of required dimensions for both glue laminated and sawn wood. |
| Chapter 7: Fire-Resistance-Rated Construction |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| 702.1 | Definition: fire/smoke damper and smoke damper | 702.1 | Definition: fire/smoke damper and smoke damper | Revised section definition(s) for combination fire/smoke damper and smoke damper to replace "remote command station" to "fire command center" - to correspond with terminology utilized throughout the code. |
| 702.1 | Definition: fire barrier | 702.1 | Definition: fire barrier | Revised section definition for fire barrier to replace "vertical or horizontal" with "wall" for description of assembly. Also revised "openings are protected" to "continuity is maintained." |
| 702.1 | Definitions: fire damper | 702.1 | Definitions: fire damper | Definition revised to clarify the distinction between smoke dampers, fire dampers, ceiling/radiation dampers, and combination fire/smoke damper. Revisions are primarily editorial in nature. The last sentence was modified to clarify that a dynamic fire damper is tested and rated under elevated temperature airflow for consistency with UL 555. |
| 702.1 | Definitions | 702.1 | Definition: fire separation distance | Revised organization of section to outline how distance is measured by providing specific item numbers 1-3. |
| 702.1 | Definitions | 702.1 | Definition: Floor Fire Door Assembly | Revised referenced section from "712.4.6" to "711.8." |
| - | - | 702.1 | Definition: Horizontal Assembly | Added definition to provide a distinction with fire barrier as those terms are used throughout the code. |
| - | - | 702.1 | Definition: Mineral fiber and mineral wool | Added definition(s) to provide a distinction between the two types of insulation and to assist to clarify requirements for each. |
| 704.1 | Exterior walls scope | 704.1 | Exterior walls scope | Scope of section revised for clarity. |
| 704.2 | Projections | 704.2 | Projections | Revised language to remove "architectural appendages" and replace with "projections." |
| 704.2.3 | Combustible projections | 704.2.3 | Combustible projections | Revised section to add "fire-retardant treaded wood" as a permitted material to provide consistency between what is allowed for a balcony versus an eave of the building. |
| Table 704.8 | Maximum area of exterior wall openings | Table 704.8 | Maximum area of exterior wall openings | A number of the footnotes were revised for clarity and consistency. |
|  |  |  |  | Added footnote b to reference 704.7 unexposed surface temperature. (and re-labeled subsequent footnotes) |
|  |  |  |  | Note g was revised to clarify that this note only applies if a fire-resistance rating is not required by Tables 601 or 602. |
|  |  |  |  | Added footnote h for Group U occupancies and reference to 406.1.2. |
| 704.8.2 | First story | 704.8.2 | First story | Revised section to clarify first story "above grade" for consistency of intent and use of term "first story." |
| 704.9 | Vertical separation of openings | 704.9 | Vertical separation of openings | Revised this section(s) to specify required opening protection. Revision is one of several made in Ch.7 to eliminate conflicts and redundancy by providing information directly in section as opposed to relying on other references to sections. This change removes reference to 715.4.8 and adds "with a fire protection rating of at least 3/4 hour." |
| 704.10 | Vertical exposure | 704.10 | Vertical exposure |  |
| 704.11 | Parapets | 704.11 | Parapets | Revised the following exceptions as follows: |
|  |  |  |  | Exception number 3 to add deck "or slab." |
|  |  |  |  | Exception number 4 clarifies the required measurement by adding "measured from the interior side of the wall" to items 4.1 and 4.2. |
|  |  |  |  | Exception number 5 - removed reference to section 101.2. |
| 704.12 | Opening protection | 704.12 | Opening protection | Revised section to clarify that the requirements are for windows in "exterior walls" and to also revise section references. |
|  |  |  |  | Revised exception to add "and shall have an automatic water supply and fire department connection" to correct the conflict with NFPA |
| 705.1 | Fire walls scope | 705.1 | Fire walls scope | Revised language for "groups" to "occupancies" and removed reference to section 503.2 for party walls due to a circular reference. Specific requirements for party walls are now contained in the new 705.1.1 thus removing the need for the reference. |
| 705.1.1 | Party walls | 705.1.1 | Party walls |  |
| 705.5.2 | Horizontal projecting elements | 705.5.2 | Horizontal projecting elements | Revised language from "architectural projections" to "similar projections." |
| 705.6.1 | Stepped buildings | 705.6.1 | Stepped buildings | Language in section revised from "having a 3/4-hour fire projection rating" to "having a fire protection rating of not less than 3/4 hour" for clarity. |
| 705.9 | Penetrations | 705.9 | Penetrations | Editorial change from "penetration through fire walls" to "penetration of fire walls." |
| 706.1 | Scope for fire barriers | 706.1 | Scope for fire barriers | Revised general section to remove the list of applications for a fire barrier because it is imcomplete and could be misleading.. |
| 706.2 | Materials | 706.2 | Materials | Revised section to remove "walls and floor assemblies" to "fire barriers" to provide consistency with other sections regarding the distinction of fire barriers and horizontal assemblies. |
| - | - | 706.2.1 | Fire-resistance rated glazing | New section recognizing the use of fire-resistance rated glazing and requires specific labeling requirements for its usage. |
| 706.3 | Fire -resistance rating | 706.3 | Fire -resistance rating | Revised section to remove "walls and floor assemblies" to "fire barriers." |
| - | - | 706.3.5 | Atriums | New section for cross-referencing. |
| - | - | 706.3.6 | Incidental use areas | New section for cross-referencing. |
| - | - | 706.3.7 | Control areas | Added this section since several references to fire barriers are defined and have applicability through the term control areas. |
| 706.3.7 | Single-occupancy fire areas | 706.3.9 | Single-occupancy fire areas | Revised section to apply to fire barriers, "horizontal assemblies, or both" and revised table reference to "706.3.9." |
| 706.4 | Continuity of fire barrier walls | 706.5 | Continuity | Revised section to remove the term "walls" throughout section to eliminate redundancy. |
| 706.5 | Horizontal fire barriers | - | - | Section deleted. |
| 706.6 | Exterior walls | 706.6 | Exterior walls | Revised section to add fire resistance rated enclosure or "enclosure" to inclusion of scope. The exception was revised to coordinate the applicability of other related section of the code. |
| 706.7 | Openings | 706.6 | Openings | Cross-reference for "exit passageways" added. Maximum size of openings permitted in fire barriers has been increased from 120 square feet to 156 square feet. New language clarifies that the 25% length limitation for fire windows permitted in atrium separation walls is not limited to the 25% length limitation |
| 706.8 | Penetrations | 706.8 | Penetrations | Editorial change from "penetration through fire walls" to "penetration of fire walls." |
| 706.8.1 | Prohibited penetrations | 706.8.1 | Prohibited penetrations | Revised referenced section from "Section 1019.1.2" to "Section 1020.1.2 or 1021.5 respectively." |
| 706.10 | Ducts and air transfer openings | 706.10 | Ducts and air transfer openings | Revised section reference from "712" to "716." |
| 707.1 | Shaft enclosures - general | 707.1 | Shaft enclosures - general | Revised section to add relocated information from 707.4 to specify shaft enclosure shall be constructed as fire barriers in this section. Location is more appropriate since fire barriers relates to more than just fire resistance. |
| 707.2 | Shaft enclosure required | 707.2 | Shaft enclosure required | Item 5 revised to apply to all occupancies other than Group H complying with the provisions for atriums. New Item 11 clarifies that a shaft enclosure isn't required for floor openings created by unenclosed stairs or ramps in accordance with Exceptions 8 or 9 in Section 1020.1. New Item 12 provides an exception to shaft enclosure requirements for floor openings protected by floor fire doors in accordance with 711.8. |
| 707.4 | Fire resistance | 707.4 | Fire resistance | Per change of 707.1, removed shaft enclosure information to new location. |
| 707.5 | Continuity | 707.5 | Continuity | Revised section to eliminate specific requirements and add references for barriers (Section 706), horizontal assemblies (Section 711), continuity (Section 70.5), and fire barriers (Section 711.4). |
| 707.6 | Exterior walls | 707.6 | Exterior walls | Revised section to add to exception requirements for exterior egress balconies, exit enclosures, and exterior exit ramps and stairways. |
| 707.7 | Openings | 707.7 | Openings | Revised language from "such openings" to "doors" for clarity. Also added reference of Section 715.3.7.3 for door requirements. |
| 707.8.1 | Prohibited penetrations for shaft enclosures | 707.8.1 | Prohibited penetrations for shaft enclosures | Prohibitions of and exception for duct penetrations has been removed as these requirements are covered elsewhere. |
| 707.10 | Ducts and air transfer openings | 707.10 | Ducts and air transfer openings | Revised section reference from "712" to "716." |
| 707.11 | Enclosure at the bottom | 707.11 | Enclosure at the bottom | Revised item number 2 to remove term "construction" and adding "fire barrier." |
| 707.12 | Enclosure at the top | 707.12 | Enclosure at the top | Revised section to add the term "sheathing" to clarify where in regards to the roof the intent specifies. |
| 707.13.1 | Refuse and laundry chute enclosures | 707.13.1 | Refuse and laundry chute enclosures | Removed the term "exit access" for consistency. The term corridor is being utilized throughout the code as opposed to exit access corridor. Also, revised item number 2 to remove term "construction" and adding "fire barrier." |
| 707.13.4 | Termination room | 707.13.4 | Termination room |  |
| 707.14 | Elevator and dumbwaiter shafts | 707.14 | Elevator, dumbwaiter and other hoistways | Revised title and section to add, "and other hoistways" and to revise reference from "Section 704.4" to "707." |
| 707.14.1 | Elevator lobby | 707.14.1 | Elevator lobby | Section revised to require elevator lobbies where the elevator shaft enclosure connects at least 4 stories as opposed to when the elevator opens onto fire-resistance rated corridors. Exception 1 has been modified to apply to all occupancies, not just office buildings. Exception 4 revised to apply to buildings having occupied floors located more than 75 feet above the lowest level of fire department vehicle access. New Exception 5 permits pressurization in accordance with Section 707.14.2 in lieu of an elevator lobby. |
| - | - | 707.14.2 | Enclosed elevator lobby pressurization alternative | Revised section to add information regarding pressurization requirements. Previously, reference to section 909.20.5 was utilized; however, gaps in the requirements existed. New sections add requirements for activating the pressurization and standby power etc., previously missing from referenced requirements. |
| 708.1 | Fire partitions scope | 708.1 | Fire partitions scope | Added elevator lobby separation and residential aircraft hangars to scope of exception. New exception provided for mini-warehouse/self-storage buildings that are provided with a sprinkler system employing quick response heads. |
| 708.3 | Fire resistance rating | 708.3 | Fire resistance rating | Revised language to add "fire partitions" and remove the term "walls" to provide an inclusive requirement for fire partitions. |
| 708.4 | Continuity | 708.4 | Continuity | Revised section to add the terms "foundation, ceiling and sheathing" to clarify where in regards to the floor and roof the extension is required. |
| 708.5 | Exterior walls | 708.5 | Exterior walls | Revised the term "enclosure" to "separation" to describe fire-resistance-rated walls. Also added new exception to address exterior egress balconies, exit enclosures and exit ramps and stairways. |
| 708.7 | Penetrations | 708.7 | Penetrations | Editorial change from "penetration of fire walls" to "penetration through fire walls." |
| 708.9 | Ducts and air transfer openings | 708.9 | Ducts and air transfer openings | Revised section to add "in a fire partition" and revised reference from "712" to "716." |
| 709.4 | Continuity | 709.4 | Continuity | Revised section to add "top of the foundation or floor/ceiling assembly below" to clarify where in regards to the floor and roof the extension is required. |
| 709.5 | Openings | 709.5 | Openings | Revised section to add "by smoke detection in accordance with Section 715.3.7.3" to coordinate list of automatic-closing fire door assemblies to close upon actuation of a smoke detector per referenced section. |
| 709.6 | Penetrations | 709.6 | Penetrations | Editorial change from "penetration through fire walls" to "penetration of fire walls." |
| 709.8 | Ducts and air transfer openings | 709.8 | Ducts and air transfer openings | Revised section to add "a smoke barrier" and revised reference from "712" to "716." |
| 710.4 | Continuity | 710.4 | Continuity | Revised section to add "top of the foundation or floor below." |
| 710.5.2 | Smoke and draft control doors | 710.5.2 | Smoke and draft control doors | Editorial change to add "during the test" to clarify that the bottom seal on the door is required for the testing only. |
| 710.5.3 | Self-closing or automatic-closing doors | 710.5.3 | Self-closing or automatic-closing doors | Revised section to add "by smoke detection" to coordinate list of automatic-closing fire door assemblies to close upon actuation of a smoke detector. |
| 710.7 | Ducts and air transfer openings | 710.7 | Ducts and air transfer openings | Revised section requirement for the space around the duct penetrating a smoke partition to be filled with an approved material to limit the free passage of smoke. This assists to eliminate the misconception that both requirements for a firestop material and a damper are needed. |
| 711.4 | Continuity in horizontal assemblies | 711.4 | Continuity in horizontal assemblies | Revised for additional reference to Section 1020.1 for exit enclosures. |
| 711.5 | Penetrations | 711.5 | Penetrations | Editorial change from "penetration through fire walls" to "penetration of fire walls." |
| 711.7 | Ducts and air transfer openings | 711.7 | Ducts and air transfer openings | Revised section to add "in horizontal assemblies" and revised reference from "712" to "716." |
| 712.4.6 | Floor fire doors | 711.8 | Floor fire door assemblies | Revised title to add term "assemblies." Also added requirement to affix label for test standard and fire-resistance rating. |
| 712.1 | Scope for penetrations | 712.1 | Scope for penetrations | Revised scope to include "floor assemblies and fire-resistance rated wall assemblies for inclusive list. |
| 712.3 | Fire-resistance rated walls | 712.3 | Fire-resistance rated walls | Revised section reference from "712.3.1" to "712.3.4" |
| 712.3.1 | Through penetrations | 712.3.1 | Through penetrations | Revised exception to add "tubes" to list of penetrating items. Editorial change to revise "shall be" to "is." Also revised item number 1 of exception to clarify the 144 sq. inches as an "area" and "through the wall." |
| 712.3.2 | Membrane penetrations | 712.3.2 | Membrane penetrations | Section exception revised to include editorial changes: |
|  |  |  |  | Item number 1 clarifies "membrane penetrations" and revises term "total" with "aggregate" and "wall" with "wall or partition." |
|  |  |  |  | Item number 2 removes "are permitted" to remove wordiness and revises language from "wall" with "wall or partition." |
| 712.3.3 | Ducts and air transfer openings | 712.3.3 | Ducts and air transfer openings | Revised section to add compliance section references 712.2 through 712.3.2 and 716 for clarification of requirements both with and without dampers. |
| 712.4 | Horizontal assemblies | 712.4 | Floor assemblies | Revised title to "floor assemblies" and removed information and references regarding penetrations for shaft enclosures. |
| - | - | 712.4.1 | Fire-resistance rated assemblies | Added new section to address penetrations in fire-resistance floor assemblies removed from another section for clarity. |
| 712.4.1 | Through penetrations | 712.4.1.1 | Through penetrations | relocated information from subsequent sections to support new section 712.4.1 added for floor assemblies. |
| 712.4.1.1 | Fire-resistance rated assemblies | 712.4.1.1.1 | Fire-resistance rated assemblies |  |
| 712.4.1.2 | Through-penetration firestop system | 712.4.1.1.2 | Through-penetration firestop system |  |
| 712.4.2 | Membrane penetrations | 712.4.1.2 | Membrane penetrations |  |
| 712.4.4 | Ducts and air transfer openings | 712.4.1.3 | Ducts and air transfer openings | Revised section to removed previous list of references and to add new reference to comply with "716." |
| 712.4.5 | Dissimilar materials | 712.4.1.4 | Dissimilar materials | Relocated section. |
| 712.4.6 | Floor fire doors | 712.4.1.5 | Floor fire doors |  |
| 712.4.3 | Nonfire-resistance-rated assemblies | 712.4.2 | Nonfire-resistance-rated assemblies | Relocated section and revised reference from "712.4.3.1 through 712.4.3.2" to "712.4.2.1 through 712.4.2.3." |
| 712.4.3.1 | Noncombustible penetrating items | 712.4.2.1 | Noncombustible penetrating items | Relocated section. |
| 712.4.3.2 | Penetrating items | 712.4.2.2 | Penetrating items |  |
| - | - | 712.5 | Penetrations in smoke barriers | Added new section to eliminate unenforceable language such as "limit" and revise with quantitative requirements for penetrations in smoke barriers. |
| 713.4 | Exterior curtain wall/floor intersection | 713.4 | Exterior curtain wall/floor intersection | Revised section to add new ASTM E 2307 requirement that provides a test method for perimeter of fire barrier systems. |
| - | - | 713.5 | Spandrel wall | Added new section with requirements and references for spandrel walls as well as reference to 713.4 addressing spandrel wall and floor intersection. |
| - | - | 713.6 | Fire-resistant joints systems in smoke barriers | Added new section to eliminate unenforceable language such as "limit" and revise with quantitative requirements for joint systems in smoke barriers. |
| 714.1 | Requirements for fire-resistance rating of structural members | 714.1 | Requirements for fire-resistance rating of structural members | Revised exception to add "and smoke barriers" and also revised reference to add Section 709.4 concerning continuity. |
| - | - | 714.2.1.1 | Membrane protection | Added section to clarify that king studs and boundary elements must also comply with fire-resistance ratings. |
| 714.2.2 | Column protection above ceilings | 714.2.2 | Column protection above ceilings | Revised section to add "foundation or floor/ceiling assembly below" to clarify where in regards to the floor and roof the intent requires. |
| 715.2 | Fire-resistance-rated glazing | 715.2 | Fire-resistance-rated glazing | References to NFPA 252 and 257 have been deleted. |
| - | - | 715.3 | Alternative methods for determining fire protection ratings | New section added for alternative methods for determining fire protection ratings. Methods recognized include designs documented in approved sources, calculations, engineering analysis, and the provisions of Section 104.11. |
| 715.3 | Fire door and shutter assemblies | 715.4 | Fire door and shutter assemblies | Relocated/renumbered subsequent sections for added information shown above (715.3). |
| Table 715.3 | Fire door and fire shutter fire protection ratings | Table 715.4 | Fire door and fire shutter fire protection ratings | Relocated Table from 715.3 to 715.4. Establishes a 1/3 hour opening assembly rating for other fire partitions with a rating of 0.5 hours. Smoke barriers added to the scope of the table requiring a 1/3 hour opening assembly rating. |
| 715.3.3 |  | 715.4.3 | Door assemblies in corridors and smoke barriers | Revised section to divide section 715.4.3 into user-friendly sections. New sub-sections for smoke and draft control and glazing in door assemblies. Fire door assemblies required to also meet the requirements for a smoke- and draft-control door assembly tested in accordance with Ul 1784. |
| - | - | 715.4.3.1 | Smoke and draft control |  |
| - | - | 715.4.3.2 | Glazing in door assemblies |  |
| 715.3.4 | Doors in exit enclosures and exit passageways | 715.4.4 | Doors in exit enclosures and exit passageways | Relocated section and revised exception for editorial changes in language from "end point" to "rise" regarding max. temperature. Also revised "not required" to "not limited." |
| 715.3.4.1 | Glazing in doors | 715.4.4.1 | Glazing in doors | Relocated section and revised section for editorial changes in language from "end point" to "rise" regarding max. temperature. |
| 715.3.5.1 | Fire door labeling requirements | 715.4.5.1 | Fire door labeling requirements | Revised section to provide inclusion of exit passageways and updates section reference from "715.3.4" to "715.4.4." |
| 715.3.6.2 | Exit and elevator Protectives | 715.4.6.2 | Exit and elevator protectives | Revised section to replace "fire doors" with "fire door assemblies" for code consistency. |
|  |  |  |  | Revised language from "stairway shaft" with "exit" for consistency with inclusive exit enclosure as fire barrier. |
|  |  |  |  | Added term "ramp" for inclusion of those required to provide clear vision of passageway. |
| 715.3.6.3 | Labeling | 715.4.6.3 | Labeling | Revised to add "at a minimum" for this requirement and to add reference 715.4.9.1 for information required on label. |
| - | - | 715.4.6.3.1 | Identification | Added section to require specific four-part identifier on the glazing such that a code official can readily identify that the glazing material is appropriate for the application. |
| 715.3.7 | Door closing | 715.4.7 | Door closing | Revised section to add exception number 2 providing to clarify elevator exemption from requirements of this section. |
| 715.3.7.3 | Smoke activated doors | 715.4.7.3 | Smoke activated doors | "Exit access corridors" changed to "corridors." The list of automatic-closing fire door assemblies as been coordinated with the corresponding sections in the code that require such activation. |
| 715.4 | Fire protection rated glazing | 715.5 | Fire protection rated glazing | Editorial changes for clarity. |
| Table 715.4 | Fire window assembly fire protection ratings | Table 715.5 | Fire window assembly fire protection ratings | Relocated table and moved "and fire partitions" to portion of table covering "smoke barriers." |
| 715.4.8 | Exterior fire window assemblies | - | - | Deleted section. Revisions to other sections makes the information in this section redundant and not necessary. |
| 715.4.2 | Nonsymmetrical glazing systems | 715.5.2 | Nonsymmetrical glazing systems | Relocated section. |
| 715.4.9 | Labeling requirements | 715.5.8 | Labeling requirements | Section revised to simply reference 715.5.8 for information required on the label. |
| - | - | 715.5.8.1 | Identification | Added section to require specific four-part identifier on the glazing such that a code official can readily identify that the glazing material is appropriate for the application. |
| 716.1 | General scope for ducts and air transfer openings | 716.1 | General scope for ducts and air transfer openings | Revised section to remove "fire-resistance-rated" as section covers information beyond fire-resistance-rated assemblies. |
| 716.1.1 | Ducts and air transfer openings without dampers | 716.1.1 | Ducts without dampers | Revision to remove "and air transfer openings." Revisions in several sections are made to correct incongruity in the provisions for ducts and air transfer openings when combined. |
| 716.2 | Membrane penetrations | 716.2 | Membrane penetrations | Section is re-written to provide a division of requirements into three items. This change accomplishes and editorial need for clarification as well as corrects several confusing and incorrect statements regarding radiation dampers. |
| 716.3.2.1 | Smoke damper actuation methods | 716.3.2.1 | Smoke damper actuation methods | Revised to include "or ceiling" in addition to wall installed dampers. Omission of term could lead to confusion. |
| 716.4 | Access and identification | 716.4 | Access and identification | Revised label requirement to add "fire/smoke damper" in clarifying for correct terms and service access. |
| 716.5 | Damper requirements | 716.5 | Damper requirements | Revised to add specific reference to sections 716.5.1 through 716.5.5. |
| 716.5.1 | Fire walls | 716.5.1 | Fire walls | Revised term "approved" to "listed." |
| 716.5.2 | Fire barriers | 716.5.2 | Fire barriers | Added statement to section: "Ducts and air transfer openings shall not penetrate exit enclosures and exit passageways except as permitted by Sections 1019.1.2 and 1020.5, respectively." |
|  |  |  |  | Revised exception number 2 to add ducts for smoke control, "where the use of a fire damper would interfere with the operation of a smoke control system." |
|  |  |  |  | Revised exception number 3 to remove reference to 716.5.4 and add exempted building equipped throughout with an automatic sprinkler system in accordance with 903.3.1 or 903.3.1.2. |
| 716.5.3.1 | Penetrations of shaft enclosures | - | - | Information relocated - now part of 715.5.3. |
| 716.5.4 | Fire partitions | 716.5.4 | Fire partitions | Revised language for exceptions to state, "where any of the following apply" for clarification. Also revised exception number 1 from "and" to "or" to correct intention that a wall be a tenant separation AND corridor wall, but rather either of the two. |
|  |  |  |  | Revised language from "approved" to "listed' and "meets" with "comply with." |
| 716.5.4 | Fire partitions. | 716.5.4 | Fire partitions. | Correct conflicts between FBCB and FBCM revise exception as follows: Ducts and air transfer openings that penetrate fire partitions shall be protected with listed fire dampers installed in accordance with their listing. Exceptions: In occupancies other than Group H, fire dampers are not required where any of the following apply: 1. The partitions are tenant separation or corridor walls in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2 of the Florida Building Code, Building and the duct is protected as a through penetration in accordance with Section 712 of the Florida Building Code, Building. 2. Tenant partitions in covered mall buildings where the walls are not required by provisions elsewhere in the code to extend to the underside of the floor or roof deck above. 3. The duct system is constructed of approved materials in accordance with the Florida Building Code, Mechanical and the duct penetrating the wall complies with all of the following requirements: 3.1. The duct shall not exceed 100 square inches (0.06 m2). 3.2. The duct shall be constructed of steel a minimum of 0.0217-inch (0.55 mm) in thickness. 3.3. The duct shall not have openings that communicate the corridor with adjacent spaces or rooms. 3.4. The duct shall be installed above a ceiling. 3.5. The duct shall not terminate at a wall register in the fire-resistance-rated wall. 3.6. A minimum 12-inch-long (305 mm) by 0.060-inch-thick (1.52 mm) steel sleeve shall be centered in each duct opening. The sleeve shall be secured to both sides of the wall and all four sides of the sleeve with minimum 1 ½ -inch by 1 ½ -inch by 0.060-inch (38 mm by 38 mm by 1.52 mm) steel retaining angles. The retaining angles shall be secured to the sleeve and the wall with No. 10 (M5) screws. The annular space between the steel sleeve and the wall opening shall be filled with rock (mineral) wool batting on all sides. |
| 716.5.5 | Smoke barriers | 716.5.5 | Smoke barriers | Revised to remove "smoke dampers" since section reference is specific to smoke damper actuation specifically. |
| 716.6 | Horizontal assemblies | 716.6 | Horizontal assemblies | Revised reference to "this" section to section 716.6.1 through 716.6.3. |
| 716.6.1 | Through penetrations | 716.6.1 | Through penetrations | Editorial change to add "listed" and "installed" for requirements. |
| 716.6.2 | Membrane penetrations | 716.6.2 | Membrane penetrations | Sections primarily reorganized for clarity and technical consistency. |
| 716.6.2.1 | Ceiling radiation dampers | 716.6.2.1 | Ceiling radiation dampers |  |
| 716.6.3 | Nonfire-resistance-rated floor assemblies | 716.6.3 | Nonfire-resistance-rated floor assemblies | Section reorganized for clarity and consistency. |
| 717.1 | General scope for concealed spaces | 717.1 | General scope for concealed spaces | Revised section to replace "noncombustible" with "of Type I or II construction." |
| 717.2.6 | Architectural trim | 717.2.6 | Architectural trim | Revised section to add requirement that there be no open space exceeding 100 sq. ft. and that wood furring strips be wood of natural decay-resistance or preservative-treated wood. |
| 717.3.1 | Draftstopping materials | 717.3.1 | Draftstopping materials | Revised section to add additional materials as to provide a comprehensive list. Additions include 1-inch nominal lumber, cement fiberboard, batts or blankets of mineral wood or glass fiber. |
| 717.5 | Combustible materials in concealed spaces in Type I or II | 717.5 | Combustible materials in concealed spaces in Type I or II | Editorial change to add "materials" in the title and the section. |
|  |  |  |  | Revised exception number 2 to add "exposed with plenums." |
|  |  |  |  | Revised exception number 3 to add classification in accordance with section 803. |
|  |  |  |  | Revised exception 5 for editorial change to remove "shall be permitted" for wordiness. |
|  |  |  |  | Added exception number 6 to allow combustible material in concealed spaces to provide for insulation and covering on pipe and tubing complying with 719.7. |
| 719.4 | Loose-fill insulation | 719.4 | Loose-fill insulation | Editorial change to add reference to test method CAN/ULC S102.2 to the exception. |
| 719.7 | Insulation and covering on pipe and tubing | 719.7 | Insulation and covering on pipe and tubing | Added exception to provide compliance for piping and tubing in plenum areas. |
| 720.1.2 | Unit masonry protection | 720.1.2 | Unit masonry protection | Revised section title to remove "unit." The term "traverse" was also removed since not an application for masonry. |
|  |  |  |  | Added to scope the application for masonry that doesn't contain horizontal wall reinforcing. |
| Table 720.1(1) | Min. protection of structural parts based on time periods for various noncombustible insulating materials | Table 720.1(1) | Min. protection of structural parts based on time periods for various noncombustible insulating materials | Revised table to add item number 1-9.1 since recent ASTM E199 fire tests have confirmed that a one-hour fire resistance rating can be achieved for a W8X35. (also added corresponding footnote n). |
| Table 720.1(2) | Rated fire-resistance periods for various walls and partitions | Table 720.1(2) | Rated fire-resistance periods for various walls and partitions | Revised table, item number as shown below: |
| - | - |  | Item 15-1.13 | Added new item in table for 12" o.c. option and renumbered subsequent sections. |
|  | Item 15-1.14 |  | Item 15-1.14 | Revised section to remove mineral wood insulation. |
|  | Item 15-1.15 |  | Item 15-1.15 | Revised section to remove "oriented strand board" from exterior covering description. |
|  | Item 15-1.16 |  | Item 15-1.16 |  |
|  | Item 16-1.1 |  | Item 16-1.1 |  |
| - | - |  | Item 16-1.3 | Added new item in table for 2X6 studs and fiberglass insulation option. |
| Table 720.1(3) | Minimum Protection for Floor and Roof Systems | Table 720.1(3) | Minimum Protection for Floor and Roof Systems | Revised table, item number as shown below: |
|  |  |  | Item 22-1.1 | Revised item 22 floor or roof construction from steel joists to wood joists. |
| - | - |  | Item 24.1.1 through item 30-1.1 | Added new items in table for I-joist floor/ceiling assemblies which are more prevalent in use but were not provided in this table. |
| 721.5.1.3 | Spray-applied fire-resistant materials | 721.5.1.3 | Spray-applied fire-resistant materials | Revised section to address requirements of intumescent or mastic coatings. Added statement after equation providing requirement based on fire-resistance tests in accordance with Section 703.2. |
| 721.5.2.2 | Spray-applied fire-resistant materials | 721.5.2.2 | Spray-applied fire-resistant materials | Revised section to removed "unrestrained" term from description of structural beams and girders. Added statement after equation providing requirement of intumescent or mastic coatings based on fire-resistance tests in accordance with Section 703.2. |
| 721.5.2.2.1 | Minimum thickness of material | 721.5.2.2.1 | Minimum thickness of material | Revised section to now contain reference to equation 7-17 and add that it's use is subject to conditions 1 through 4. The equation is applicable to both unrestrained beams and compact restrained beams. The conditions provided also correlates with information provided in the UL Fire Resistance Directory. |
| 721.5.2.3 | Structural steel trusses | 721.5.2.3 | Structural steel trusses | Revised for editorial change by replacing "which" with "that" and added statement providing requirement of intumescent or mastic coatings based on fire-resistance tests in accordance with Section 703.2. |
| Table 721.6.2(3) | Membrane on exterior face of wood stud walls | Table 721.6.2(3) | Membrane on exterior face of wood stud walls | Editorial change in sheathing column to replace term "plywood" with "wood structural panel" for consistency with industry practice terminology. |
| 721.7 | Other reference documents | - | - | Deleted section. Two references no longer exist and the remaining reference provides no additional information not already provided in elsewhere in the code. |
| Chapter 8: Interior Finishes |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| 801.1.2 | Decorative materials and trim scoping requirements | 801.1.2 | Decorative materials and trim scoping requirements | Reference to "flame resistance" of materials has been revised to "flame propagation performance criteria of NFPA 701" consistent with terminology in NFPA 701. |
| 801.1.3 | Applicability | 801.1.3 | Applicability | Correct reference to Chapter 31 not Chapter 16. For buildings in flood hazard areas, see Section 3110. |
| 801.2.1 | Window framing construction | 801.2.1 | Window framing construction | The term "first story" has been revised to "first story above grade plane" for clarity and consistency throughout the code. Clarifies that this section applies to windows in exterior walls. |
| 801.2.2 | Foam plastic use limitations | 801.2.2 | Foam plastic use limitations | New language stating that exposed foam plastics and foam plastics used in conjunction with a textile or vinyl facing or cover are regulated by this section. |
| 802.1 | Definition: Flame resistance | 802.1 | - | The definition of flame resistance has been deleted for consistency in terminology with NFPA 701. |
| 802.1 | Definition: Flame spread index | 802.1 | Definition: Flame spread index | Revised reference to testing method from single numerical value, to a comparative measure of the spread of flames versus the time for a material for consistency with terminology in ASTM E 176. |
| 802.1 | Definition: Interior wall and ceiling finish | 802.1 | Definition: Interior wall and ceiling finish | Provided the inclusion of "water closet privacy" as in interior finish item. |
| 802.1 | Definition: Smoke-developed index | 802.1 | Definition: Smoke-developed index | Revised reference to testing method from single numerical value, to a comparative measure of smoke obscuration versus the time for a material for consistency with terminology in ASTM E 176. |
| 803.2.1 | Acceptance criteria for interior wall or ceiling finishes other than textiles | 803.2.1 | Acceptance criteria for interior wall or ceiling finishes other than textiles | Added additional item for acceptance criteria to be met for the entire test. New Item 3: The peak rate of heat release throughout the NFPA 286 test shall not exceed 800 kW. |
| Table 803.5 | Occupancy interior wall and ceiling finish requirements | Table 803.5 | Occupancy interior wall and ceiling finish requirements | Revise table headings and footnotes- "Vertical exits" to "exit enclosures" and "exit access corridors and other exitways" to "corridors" for consistency in terminology throughout the code. |
| 803.6 | Textiles | 803.6 | Textiles | Added specific reference to carpet as textile. Reformat of section permits compliance with 803.6.1, 803.6.2, or 803.6.3 for clarity in determining whether a material is a textile or not. |
| 803.6.1 | Textile wall coverings | 803.6.1 | Surface burning characteristics for textile wall and ceiling coverings | Added ceiling coverings to the scope of this section as a result of deleting Section 803.6.2 for ceiling coverings. |
| 803.6.1.1 | Textiles: Method A test protocol | - | - | Method A test protocol has been deleted. |
| - | - | 803.6.2 | Textiles: room corner test ceiling and wall finish | Provides specific reference to NFPA 265 and the Method B protocol. |
| 803.6.1.2 | Method B Test Protocol | 803.6.2.1 | Method B Test Protocol | New pass/fail criteria limits smoke released to not exceed 1000 m2. |
| - | - | 803.6.3 | Textiles: room corner test ceiling and wall finish | Permits the use of NFPA 286 for testing textile wall and ceiling coverings. |
| 804.1 | Interior floor finish | 804.1 | Interior floor finish | Revised wording to state specific sections: 804.2 through 804.4.1. Exception revised to include floor finish in scope. |
| 804.3 | Interior floor finish testing and identification | 804.3 | Interior floor finish testing and identification | Revised to include floor finish in scope of section. |
| 804.4.1. | Minimum critical radiant flux | 804.4.1. | Minimum critical radiant flux | Delete reference to group I-4 occupancy. Interior floor finish and floor covering materials in exit enclosures, exit passageways and corridors shall not be less than Class I in Groups I-2 and I-3 and not less than Class II in Groups A, B, E, H, I-4, M, R-1, R-2 and S. In all areas, floor covering materials shall comply with the DOCFF-1 “pill test” (CPSC 16 CFR, Part 1630). Exception: Where a building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2, Class II materials are permitted in any area where Class I materials are required, and materials complying with the DOC FF-1 “pill test” (CPSC 16 CFR, Part 1630) are permitted in any area where Class II materials are required. |
| 804.4 | Interior floor finish: application | 805.1 | Application of combustible materials in type I and II construction | Clarification of terms and moved requirements in Section 804.4 to new Section 805.5 Combustible Materials in Type I and II Construction. |
| 804.4.1 | Subfloor construction | 805.1 | Subfloor construction | Section relocated. |
| 804.4.2 | Wood finish flooring | 805.1.2 | Wood finish flooring | Section relocated. |
| 804.4.3 | Insulating boards | 805.1.3 | Insulating boards | Section relocated. |
| 804.5 | Interior floor finish requirements | 804.4 | Interior floor finish requirements | Terminology regarding exits and corridors revised for consistent terminology throughout the code. |
| 804.5.1 | Minimum critical radiant flux | 804.4.1 | Minimum critical radiant flux | Revised to include floor coverings in scope of section. Exception now permits of the use sprinklers in accordance with Section 903.3.1.2 in addition to Section 903.3.1.1. |
| 805.1 | Decorative materials and trim scoping requirements | 806.1 | Decorative materials and trim scoping requirements | Changed "flame resistant" to " flame propagation performance criteria of NFPA 701. New criteria specific to fixed or movable walls and partitions, paneling, wall pads and crash pads requires to be considered interior finish if they cover more than 10% of the wall or ceiling area. In Group B and M occupancies, fabric partitions suspended from ceiling and not support by the floor required to meet NFPA 701 or be noncombustible. |
| 805.1.2 | Flame-resistant materials | 806.1.2 | Combustible decorative materials | Changed "flame resistant" to " flame propagation performance criteria of NFPA 701. New exception 2 permits unlimited amounts of fabric partitions suspended from ceiling in Groups B and M. |
| 805.2 | Acceptance criteria and reports | 806.2 | Acceptance criteria and reports | Changed "flame resistant" to " flame propagation performance criteria and other terminology for consistency with NFPA 701. |
| 805.5 | Trim | 806.5 | Interior Trim | Specifically excludes foam plastic from scope of this section. |
| Chapter 9: Fire Protection Systems |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| 901.1 | Scope | 901.1 | Scope | Add “Carbon Monoxide Alarms” to the chapter scope. 901.1 Scope. The provisions of this chapter shall specify where fire protections systems are required and shall apply to the design, installation and operation of fire protection systems and carbon monoxide detection alarms. |
| 903.1.1 | Automatic Sprinkler Systems alternative protection | 903.1.1 | Automatic Sprinkler Systems alternative protection | Revised approval entity from "building" to "fire code" official for consistency. |
| 903.2 | Automatic Sprinkler Systems exception | 903.2 | Automatic Sprinkler Systems exception | Language revised for consistency of terms utilized in the technical section for fire separation requirements. |
| 903.2.1.2 | Group A-2 sprinkler systems | 903.2.1.2 | Group A-2 sprinkler systems | Lowered fire area occupant load threshold for when sprinklers are required in all Group A-2 from 300 to 100. |
| 903.2.3 | Group F-1 sprinkler systems | 903.2.3 | Group F-1 sprinkler systems | Revised language in requirement item number 2 from "grade" to "grade plane" for consistency in throughout the code. |
| 903.2.6 | Group M sprinkler system | 903.2.6 | Group M sprinkler system | Revised language in requirement item number 2 from "grade" to "grade plane" for consistency in throughout the code. |
| 903.2.8 | Group S-1 sprinkler system | 903.2.8 | Group S-1 sprinkler system | Revised language in requirement item number 2 from "grade" to "grade plane" for consistency in throughout the code. |
| Table 903.2.13 | Additional Required suppression Systems | Table 903.2.13 | Additional Required suppression Systems | Added to table; 508.2 Incidental use areas and 1025.6.2.3 Smoke-protected assembly seating. |
| 903.3.1.1.1 | NFPA 13 sprinkler system exempt locations | 903.3.1.1.1 | NFPA 13 sprinkler system exempt locations | Revised approval entity from "building" to "fire code" official for consistency with the IFC. |
| 903.3.1.2.1 | NFPA 13R sprinkler system exempt locations | 903.3.1.2.1 | NFPA 13R sprinkler system exempt locations | Revised section to add "and decks" to the title and requirements. |
| 903.3.6 | Automatic Sprinkler Systems - water supply hose threads | 903.3.6 | Automatic Sprinkler Systems - water supply hose threads | Revised section to add "and fittings" in addition to hose threads. Also revised to state "as prescribed by fire code official" as opposed to stating that threads must be compatible with fire department hose threads. |
| 903.4.1 | Sprinkler system monitoring and alarm signals | 903.4.1 | Sprinkler system monitoring and alarm signals | Revised approval entity from "building" to "fire code" official for consistency with the IFC. |
| 904.2 | Automatic fire-extinguishing systems | 904.2 | Automatic fire-extinguishing systems | Revised approval entity from "building" to "fire code" official for consistency with the IFC. |
| 904.11 | Commercial cooking systems | 904.11 | Commercial cooking systems | Revised UL reference in exception from "197" to "710B." |
| 904.11.1 | Commercial cooking systems - manual operation | 904.11.1 | Commercial cooking systems - manual operation | Revised required height location of manual actuation devices to maximum of 48 inches and minimum of 42 inches to provide consistency with NFPA requirements. Also revised language requires the device to clearly identify the hazard being protected. |
| 905.3.1 | Standpipe and building height | 905.3.1 | Standpipe and building height | Added new Exception 5 clarifying the measurement of the lowest fire department vehicle access in relation to recessed loading docks and topography. |
| 905.3.3 | Standpipe in covered mall buildings | 905.3.3 | Standpipe in covered mall buildings | Revised reference section from "905.3" to a more specific "905.3.1." |
| 905.3.4 | Requirement for sandpipe system for stages | 905.3.4 | Requirement for standpipe system for stages | Revised exception to add new reference to NFPA 13 and NFPA 14 and removed language which does not currently coordinate with NFPA 14. |
| - | - | 905.3.7 | Standpipes in marinas and boatyards | Added new section to protect marine facilities not previously listed. |
| 905.4 | Location of Class I standpipe hose connections | 905.4 | Location of Class I standpipe hose connections | Added exception to item number 2, providing a reasonable placement for typical design conditions where horizontal exits are near exit stairways and utilization of a the exempted stair enclosure is a better fire fighting practice. Also revised #6 to revise approval entity from "building" to "fire code" official. |
| 905.5.3 | Class II system 1-inch hose | 905.5.3 | Class II system 1-inch hose | Revised approval entity from "building" to "fire code" official. |
| 907.2 | Fire alarm and detection systems | 907.2 | Fire alarm and detection systems | Revised language for, "installed in accordance with the provisions of this code and NFPA 72" and the requirement to "provide occupant notification in accordance with Section 907.9, unless other requirements are provided by another section of this code" as separate sentences to eliminate the confusion that it may not apply to manual systems as well as to provide a clearer intent of the purpose. |
| 907.2.1 | Group A fire alarm system | 907.2.1 | Group A fire alarm system | Removed "in accordance with NFPA 72" for consistency with other sections that do not reference this standard. |
| - | - | 907.2.3 | Group E manual fire alarm system | Relocated exception from Section 907.3.1 to 907.2.3 as new exception item number 3 for continuity of sections requiring manual fire alarm boxes. |
| 907.2.6 | Group I fire alarm system | 907.2.6 | Group I fire alarm system | Revised language from "as prescribed in this section" to "in accordance with Sections 907.2.6.1 and 907.2.6.2." |
| - | - | 907.2.6.1 | Group I-1 fire alarm system | Added requirements specifically for Group I-1 to clarify for this group as well as Group I-2, the requirements for smoke detection and locations. |
| 907.2.6.2 | Group I-2 fire alarm system | 907.2.6.1 | Group I-2 fire alarm system | Relocated section and added reference to Section 407.2 to comply with change outlined for Group I-1 above. |
| 907.2.7 | Group M fire alarm system | 907.2.7 | Group M fire alarm system | Added "The initiation of a signal from a manual fire alarm box shall initiate alarm notification appliances as required by Section 907.9." for clarification of original intent. |
| 907.2.7.1 | Occupant notification | 907.2.7.1 | Occupant notification | Revised general language to assist in consistent enforcement. |
| 907.2.9 | Group R-2 exceptions | - | - | Deleted Item 2.3 from Exception 2 requiring at least one manual fire alarm box installed at an approved location. |
| 907.2.10 | Single and multi-station smoke alarms | 907.2.10 | Single and multi-station smoke alarms | Requires listed single- and multiple-station smoke detectors to comply with UL 217. |
| 907.2.10.1.3 | Single and multi-station smoke alarms - Group I-1 | 907.2.10.1.3 | Single and multi-station smoke alarms - Group I-1 | Section revised by making last sentence an Exception to the section for clarity. |
| 907.2.12.2 | Emergency voice/alarm communication system | 907.2.12.2 | Emergency voice/alarm communication system | Revised language to clarify speaker requirements and overall intent. Changes include new language, "general or staged evacuation" and added statement, "Speakers shall be provided throughout the building by paging zones. As a minimum, paging zones shall be provided as follows:" Items numbers were also revised to list: 1. Elevator groups; 2. Exit stairways; 3. Each floor. Item number 4 was added as: "4. Areas of refuge as defined in Section 1002.1." |
| 907.2.12.2.1 | Emergency voice/alarm manual override | 907.2.12.2.1 | Emergency voice/alarm manual override | Revised section to include, "on a selective and all-call basis" for paging zone override requirements. |
| 907.2.12.2.2 | Emergency voice/alarm live voice messages | 907.2.12.2.2 | Emergency voice/alarm live voice messages | Revised section to include, "on a selective and all-call basis" replacing language providing specific speaker locations. |
| 907.2.17 | Lumber mills | 907.2.17 | Lumber mills | Editorial change to remove the term "plywood" from title and add, "wood structural panel" to this section. |
| 907.3.1 | Manual fire alarm boxes exemption | 907.3.1 | Manual fire alarm boxes exemption | Removed exemption from this section and relocated exemption to Section 907.2.3, Group E. |
| 907.3.5 | Protective covers for fire alarm boxes | 907.3.5 | Protective covers for fire alarm boxes | Revised authorization entity from "building" to "fire code" official. |
| 907.7 | Presignal system | 907.7 | Presignal system | Revised approval entity from "building" to "fire code" official. |
| 907.8.2 | High-rise buildings | 907.8.2 | High-rise buildings | Revised language regarding "human occupancy" to ensure clarity of high-rise classification. |
| 907.9.1.2 | Alarm notification for employee work areas | 907.9.1.2 | Alarm notification for employee work areas | Revised to require the initial design to have a minimum of 20 percent spare capacity to account for the potential of adding visible notification appliances in the future to accommodate hearing impaired employees, which provides for a more reasonable and cost effective means to meet the original intent. |
| 907.14 | Monitoring | 907.14 | Monitoring | Section revised for clarity |
| 908.3 | Emergency alarm systems in areas of toxic materials | 908.3 | Emergency alarm systems in areas of toxic materials | Revised the exception to replace the term "properties" with the term "threshold level" for consistency in terminology. |
| 909.4.6 | Smoke control systems | 909.4.6 | Smoke control systems | Section revised by placing additional limit of 1.5 times the calculated egress time for continued operation of smoke control systems after detection of the fire event, in addition to the 20 minute limit.. |
| 909.5.1 | Leakage area for smoke barrier | 909.5.1 | Leakage area for smoke barrier | Revised approval entity from "building" to "fire code" official. |
| 909.5.2 | Opening protection | 909.5.2 | Opening protection | Revised language in exception 3 from "fire-rated" to fire-protection-rated" glazing as each have a very specific meaning and for this exception, fire-protection-rated should be used. |
| 909.7 | Airflow design method | 909.7 | Airflow design method | Revised approval entity from "building" to "fire code" official. |
| 909.7 | Airflow design method | 909.7 | Airflow design method | Revised approval entity from "Fire Code Official” to “Building" Official. When approved by the Building Official, smoke migration through openings fixed in a permanently open position, which are located between smoke control zones by the use of the airflow method, shall be permitted. The design airflow shall be in accordance with this section. Airflow shall be directed to limit smoke migration from the fire zone. The geometry of openings shall be considered to prevent flow reversal from turbulent effects |
| 909.8 | Exhaust method | 909.8 | Exhaust method | Revised to require smoke control systems using the exhaust method to be in accordance with NFPA 92B. |
| 909.8 | Exhaust method | 909.8 | Exhaust method | Revised approval entity from "Fire Code Official” to “Building" Official.. When approved by the Building Official, mechanical smoke control for large enclosed volumes, such as in atriums or malls, shall be permitted to utilize the exhaust method. Smoke control systems using the exhaust method shall be designed in accordance with NFPA 92B. |
| 909.8.1 | Smoke layer | 909.8.1 | Exhaust rate | Revised title from "Exhaust rate" to "Smoke layer" to more accurately describe section. Revised section to remove method specifics now contained and reference in NFPA 92B. |
| 909.8.2 | Axisymmetric plumes | - | - | Deleted section. Information is contained in newly reference NFPA 92B. |
| 909.8.3 | Balcony spill plumes | - | - | Deleted section. Information is contained in newly reference NFPA 92B. |
| 909.8.4 | Window plumes | - | - | Deleted section. Information is contained in newly reference NFPA 92B. |
| 909.8.5 | Plume contact will walls | - | - | Deleted section. Information is contained in newly reference NFPA 92B. |
| 909.9 | Design fire | 909.9 | Design fire | Revised approval entity from "building" to "fire code" official. Minimum Q for design fire has been deleted and left specifically to the discretion of the registered design professional. |
| 909.9 | Design fire | 909.9 | Design fire | Revised approval entity from "Fire Code Official” to “Building" Official. The design fire shall be based on a rational analysis performed by the registered design professional and approved by the Building Official. The design fire shall be based on the analysis in accordance with Section 909.4 and this section. |
| 909.9.2 | Design fire separation distance | 909.9.2 | Design fire separation distance | Revised section to retain first sentence but remove specific design requirements listed to allow for more appropriate design methods taking into account additional considerations outlined in section 909. |
| 909.10 | Equipment | 909.10 | Equipment | Revised approval entity from "building" to "fire code" official. |
| 909.10 | Equipment | 909.10 | Equipment | Revised approval entity from "Fire Code Official” to “Building" Official. Equipment including, but not limited to, fans, ducts, automatic dampers and balance dampers, shall be suitable for its intended use, suitable for the probable exposure temperatures that the rational analysis indicates and as approved by the Building Official. |
| 909.15 | Control diagrams | 909.15 | Control diagrams | Revised approval entity from "building" to "fire code" official. |
| 909.15 | Control diagrams | 909.15 | Control diagrams | Revised approval entity from "Fire Code Official” to “Building" Official. Identical control diagrams showing all devices in the system and identifying their location and function shall be maintained current and kept on file with the Building Official, the fire department and in the fire command center in a format and manner approved by the fire chief. |
| 909.16 | Fire-fighters smoke control panel | 909.16 | Fire-fighters smoke control panel | Revised this section to provide delineation for low-rise requirements and for high-rise requirements to eliminate unnecessary space use for low-rise designs. This was accomplished by adding information for low-rise as follows, "In all other buildings, the fire-fighter’s smoke control panel shall be installed in an approved location adjacent to the fire alarm control panel. The fire-fighter’s smoke control panel shall comply with Sections 909.16.1 through 909.16.3." |
| 909.18.8.3.1 | Report filing | 909.18.8.3.1 | Report filing | Revised approval entity from "building" to "fire code" official. |
| 909.18.8.3.1 | Report filing | 909.18.8.3.1 | Report filing | Revised approval entity from "Fire Code Official” to “Building" Official. A copy of the final report shall be filed with the Building Official and an identical copy shall be maintained in an approved location at the building. |
| 909.19 | System acceptance | 909.19 | System acceptance | Revised approval entity from "building" to "fire code" official. |
| 909.19 | System acceptance | 909.19 | System acceptance | Revised approval entity from "Fire Code Official” to “Building" Official. Buildings, or portions thereof, required by this code to comply with this section shall not be issued a certificate of occupancy until such time that the building official determines that the provisions. Exception: In buildings of phased construction, a temporary certificate of occupancy, as approved by the building official, shall be allowed provided that those portions of the building to be occupied meet the requirements of this section. |
| 909.20 | Smokeproof enclosures. | 909.20 | Smokeproof enclosures. | Revised approval entity from "Fire Code Official” to “Building" Official. Where required by Section 1020.1.7, a smokeproof enclosure shall be constructed in accordance with this section. A smokeproof enclosure shall consist of an enclosed interior exit stairway that conforms to Section 1020.1 and an open exterior balcony or ventilated vestibule meeting the requirements of this section. Where access to the roof is required by the Florida Building Code, such access shall be from the smokeproof enclosure where a smokeproof enclosure is required. |
| 909.20.2.1 | Door closers | 909.20.2.1 | Door closers | Revised language moving section 715 reference to proper location in the section to clarify that its not the smoke proof enclosure but the smoke detector that is regulated by the reference. |
| 909.20.4.1 | Vestibule doors | 909.20.4.1 | Vestibule doors | Revised section to correct a reference from 715.3 to 715.4.3 and to add reference for NFPA 105. Revision also removes specific gasket information and adds, "and meet the requirements for a smoke door assembly." |
| 909.20.5 | Stair pressurization alternative | 909.20.5 | Stair pressurization alternative | Revised exterior stairway pressure from "0.15 inch per water 37 Pa" to "0.05 inch per water 12.3 Pa." |
| 909.21 | Underground building smoke exhaust system | - | - | Deleted section to avoid confusion over requirements outlined in section 405.5. |
| 909.21.1 | Exhaust capability | - | - | Section deleted. |
| 909.21.2 | Operation | - | - | Section deleted. |
| 909.21.3 | Alarm required | - | - | Section deleted. |
| 909.22 | Atrium | - | - | Section deleted. |
| 910.1 | Smoke and heat vents | 910.1 | Smoke and heat vents | Added exception number 2 exempting smoke and heat vents from areas of buildings equipped with ESFR sprinklers. |
| 910.2.2 | Smoke and heat vents for Group H | - | - | Section deleted. |
| - | - | 910.3.1 | Design and installation of smoke and heat vents | Added the requirement for smoke and heat vents to be listed and labeled in accordance with UL 793. |
| 910.3.1 | Design and installation vent operation | 910.3.2 | Design and installation vent operation | Relocated section and revised to add referenced sections "910.3.2.1 through 910.3.2.3." |
| 910.3.4 | Draft curtains | 910.3.5 | Draft curtains | Relocated section and revised to add reference, "where required by Table 910.3." |
| Table 910.3 | Requirements for draft curtains and smoke and heat vents | Table 910.3 | Requirements for draft curtains and smoke and heat vents | Revised table information under the column heading "Occupancy Group and Commodity Classification" to combine S-1 with F-1. Remainder of classifications include reference to 910.2.3 options. Also added footnotes c and d for modification to provide method for calculation of vent openings. |
| 910.4 | Mechanical smoke exhaust | 910.4 | Mechanical smoke exhaust | Revised approval entity from "building" to "fire code" official. |
| - | - | 912 | Fire department installation of connections | Added new section for fire department connections. |
| - | - | 913 | Carbon monoxide protection | Add new Section 913 Carbon Monoxide Protection. 913.1 Carbon monoxide protection. Every building for which a permit for new construction is issued having a fossil-fuel-burning heater or appliance, a fireplace, or an attached garage shall have an operational carbon monoxide alarm installed within 10 feet of each room used for sleeping purposes. 913.1.1 Power Source. In new construction, alarms shall receive their primary power from the building wiring when such wiring is served from the local power utility. Such alarms shall have battery backup. 913.1.2 Combination alarms. Combination smoke/carbon monoxide alarms shall be listed or labeled by a Nationally Recognized Testing Laboratory. Exception: An approved operational carbon monoxide detector shall be installed inside or directly outside of each room or area within a hospital, inpatient hospice facility or nursing home facility where a fossil-fuel burning heater, engine, or appliance is located. The carbon monoxide detector shall be connected to the fire-alarm system of the hospital, inpatient hospice facility, or nursing home facility as a supervisory signal. |
| Chapter 10: Means of Egress |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
|  |  | 1001.5 |  | Correct referenced section. Where approved by the building official, existing stairs shall be permitted to be rebuilt in accordance with the dimensional criteria of the building code in effect at the time of original construction provided: - Handrails comply with Section 1009.11 1012, and, - Guardrails comply with Section 1012, 1013, and, - The elevation of the floor surfaces on both sides of the door complies with Section 1008.1.4 |
|  |  | 1001.6 | Special egress requirements by occupancy. | The general requirements of Chapter 10 apply to all occupancies except as modified for specific occupancies in accordance with Section 1025 and Section 1027 through 1034. |
| 1002.1 | Definitions: Accessible means of egress | 1002.1 | Definitions: Accessible means of egress | Definition modified to clarify that the accessible means of egress begins at areas required to be accessible and ends at a public way |
| 1002.1 | - | 1002.1 | Aisle | New definition of aisle added to distinguish from aisle accessway |
| 1002.1 | - | 1002.1 | Definition for Means of Escape | Added new definition of means of escape for compliance with emergency egrees opening requirements when hurricane shutters are installed. |
| 1002.1 | - | 1002.1 | Definition for Merchandise Pad | Added new definition of merchandise pad to deal with aisle accessways in Group M. |
| 1002.1 | - | 1002.1 | Merchandise Pad. | Delete reference to section 105.2 as it is not applicable. A merchandise pad is an area for display of merchandise surrounded by aisles, permanent fixtures or walls. Merchandise pads contain elements such as non-fixed and moveable fixtures, cases, racks, counters and partitions as indicated in Section 105.2 from which customers browse or shop. |
| 1003.3.2 | Free standing objects | 1003.3.2 | Free standing objects | Revised requirement for any object on a post or pylon to not extend more than "4" inches - previously the requirement stated no more than "12" inches. |
| 1004.1 | Occupant load scope | 1004.1 | Occupant load scope | Revisions to these sections are primarily editorial. The fundamental requirements were reorganized in a logical fashion. |
| 1004.1.1 | Occupant load - actual number | 1004.1.1 | Areas without fixed seating |  |
| 1004.1.2 | Number by Table 1004.1.2 | - | - |  |
| 1004.1.3 | Occupant load - number by combination | - | - |  |
| Table 1004.1.2 | Maximum Floor Area Allowances per Occupant | Table 1004.1.1 | Maximum Floor Area Allowances per Occupant | Revised Table number. Column heading was revised from "Occupancy" to "Function of Space." |
| Table 1004.1.2 | Maximum Floor Area Allowances per Occupant | Table 1004.1.1 | Maximum Floor Area Allowances per Occupant | Delete “Exercise Room” requirement as it creates a conflicts within the code. Exercise rooms 50 gross |
| 1004.2 | Increased occupant load | 1004.2 | Increased occupant load | Revised referenced Table from "1004.1.2" to "1004.1.1" and revised the occupant load must not exceed requirement from "5" to "7." |
| 1004.7 | Fixed seating | 1004.7 | Fixed seating | Revised section to add, "The occupant load for areas in which fixed seating is not installed, such as waiting spaces and wheelchair spaces, shall be determined in accordance with Section 1004.1.1 and added to the number of fixed seats" to clarify the space calculation for areas that do not have fixed seating. |
|  |  | 1006.3.5 |  | Correct reference in exception 1. Externally illuminated signs shall have the word "EXIT" or other appropriate wording in plainly legible letters not less than 6 inches (15 2 mm) high with the principal strokes of letters not less than 3/4 inches (19 mm) wide. The word "EXIT" shall have letters of a width not less than 2 inches (51 mm), except the letter "I," and the minimum spacing between letters shall be not less than 3/8 inches (10 mm). Signs larger than the minimum established in this paragraph shall have letter widths, strokes and spacing in proportion to their height. Externally illuminated signs shall be illuminated by not less than 5 foot-candles (50 lux) at the illuminated surface and shall have a contrast ratio of not less than 0.5. Exceptions: 1. Marking required by Section 1009.5.4. 2. Group R-3 and Group R-4 (small facility) occupancies. |
|  |  | 1006.3.6 |  | Correct reference in exception 1. Internally illuminated signs shall be listed in accordance with UL 924, Standard for Safety Emergency Lighting Power Equipment. The visibility of an internally illuminated sign shall be the equivalent of an externally illuminated sign that complies with Section 1006.3.5. Exceptions: 1. Marking required by Section 1009.5.4. 2. Signs in compliance with Sections 1006.3.4 and 1006.3.8.2. |
| 1008.1.1 | Size of doors | 1008.1.1 | Size of doors | Revised exception number 7 to the exception does not apply to Group R1 occupancies. |
| 1008.1.1 | Size of doors. | 1008.1.1 | Size of doors. | Delete exceptions 7 & 8 as they address Type A Type B dwellings which are used in the code. The minimum width of each door opening shall be sufficient for the occupant load thereof and shall provide a clear width of not less than 32 inches (813 mm). Clear openings of doorways with swinging doors shall be measured between the face of the door and the stop, with the door open 90 degrees (1.57 rad). Where this section requires a minimum clear width of 32 inches (813 mm) and a door opening includes two door leaves without a mullion, one leaf shall provide a clear opening width of 32 inches (813 mm). The maximum width of a swinging door leaf shall be 48 inches (1219 mm) nominal. Means of egress doors in a Group I-2 occupancy used for the movement of beds shall provide a clear width not less than 41.5 inches (1054 mm). The height of doors shall not be less than 80 inches (2032 mm). Exceptions: 1. The minimum and maximum width shall not apply to door openings that are not part of the required means of egress in Group R-2 and R-3 occupancies. 2. Door openings to resident sleeping units in Group I-3 occupancies shall have a clear width of not less than 28 inches (711 mm). 3. Door openings to storage closets less than 10 square feet (0.93m2) in area shall not be limited by the minimum width. 4. Width of door leafs in revolving doors that comply with Section 1008.1.3.1 shall not be limited. 5. Door openings within a dwelling unit or sleeping unit shall not be less than 78 inches (1981 mm) in height. 6. Exterior door openings in dwelling units and sleeping units, other than the required exit door, shall not be less than 76 inches (1930 mm) in height. 7. Reserved. 8. Reserved. |
| 1008.1.2 | Door swing | 1008.1.2 | Door swing | Exceptions revised to clarify that egress doors in patient rooms in suites of health care facitlities and doors serving a bathroom in an sleeping unit in Group R1 do not have to be side-hinged swinging. |
| 1008.1.4 | Floor Elevation | 1008.1.4 | Floor Elevation | Revised exception number 3 to clarify this exception applies to Group R-3 units not required to be accessible. Also revised requirement for slope to not exceed "1 units vertical in 50 units horizontal" from previous "0.25 units vertical in 12 units horizontal." |
| 1008.1.8.3 | Locks and latches | 1008.1.8.3 | Locks and latches | "Churches" changed to "places of religious worship." |
| 1008.1.8.5 | Doors and unlatching | 1008.1.8.5 | Doors and unlatching | Revised language to add "door" to previous term "leaf" so that both terms may be utilized for the requirement of a single operation for unlatching. |
| 1008.1.8.7 | Stairway doors | 1008.1.8.7 | Stairway doors | Exception 3 has been revised to require that the doors are capable of being ulocked simultaneously without unlatching upon a signal from the fire command center. |
| 1008.1.9 | Panic and fire exit hardware | 1008.1.9 | Panic and fire exit hardware | The occupant load limit for Groups A and E when panic or fire exit hardware is required has been lowered from 100 to 50.Panic or fire exit hardware is now required on exit access doors from electrical rooms with equipment rated 120 amperes or more and over 6 feet wide that contain overcurrent devices, switching devices, or control devices. |
| 1008.2.1 | Stadium gates | 1008.2.1 | Stadium gates | Revised reference section from "1017" to "1024.6." |
| 1009 | Stairways and handrails | 1009 | Stairways | Revised title. Handrail information now in Section 1012. |
| 1009.1 | Stairway width | 1009.1 | Stairway width | Revised exception number 1 to state the occupant load from "50 or less" to "less than 50." |
| 1009.3 | Stair treads and risers | 1009.3 | Stair treads and risers | Revised scope for this section to relocate dimensional information to Section 1009.3.2. |
| - | - | 1009.3.1 | Winder treads | Added new section. Information was previously included in another section but is provided in separate section for clarity. |
| 1009.3.1 | Stairway dimensional uniformity | 1009.3.2 | Stairway dimensional uniformity | Relocated information regarding min and max stair tread and riser to 1009.3 and added tolerance and uniformity information from the exception in this section to the scope of section. In addition, exception 1 was revised to move information to scope of section and was revised to add information regarding nonuniform risers. Exception 2 added information regarding winders. Information from previous exemption 1 was revised to correct the referenced scope from "8 percent slope" to "8.333 percent slope." |
| 1009.4 | Stairway landings. | 1009.4 | Stairway landings. | Correct reference in exception 1. There shall be a floor or landing at the top and bottom of each stairway. The width of landings shall not be less than the width of stairways they serve. Every landing shall have a minimum dimensioned measured in the direction of travel equal to the width of the stairway. Such dimension need not exceed 48 inches (1219 mm) where the stairway has a straight run. Exceptions: - Aisle stairs complying with Section 1025.11. - No change. - No change. |
| 1009.5.1 | Stairway walking surface and slope | 1009.5.1 | Stairway walking surface and slope | Revised slope from "48 vertical units" to "50 vertical units" (still a 2% slope). |
| 1009.5.2 | Outdoor stairway conditions | 1009.5.2 | Outdoor stairway conditions | Removed requirement for overhang protection to prevent accumulation of excessive water or snow for exterior stairways . |
| 1009.7 | Circular stairways | 1009.7 | Curved stairways | Revised title of section. Language revisions recognizes new terminology used in curved stairways and provides greater parameters of application for this section. Minimum radius is now based on the required width rather than the actual width. |
| 1009.8 | Winders | - | - | Deleted section. |
| 1009.9 | Spiral stairways | 1009.8 | Spiral stairways | Relocated section. |
| 1009.10 | Alternating tread devices | 1009.9 | Alternating tread devices | Relocated section. |
| 1009.11 | Stairway handrails | 1009.10 | Stairway handrails | Provisions for handrails have been relocated to Section 1012 and apply to handrails for stairs and ramps. |
| 1009.13 | Interlocking or scissor stairs | 1009.12 | Interlocking or scissor stairs | Relocated section. |
| 1010.2 | Slope | 1010.2 | Slope | Correct reference in exception 1. Ramps used as part of a means of egress shall have a running slope not steeper than one unit vertical in 12 units horizontal (8.333-percent slope). The slope of other ramps shall not be steeper than one unit vertical in eight units horizontal (12.5-percent slope). Exceptions: 1. Aisle ramp slope in occupancies of Group A shall comply with Section 1025.11. 2. Ramps that provide access to vehicles, vessels, mobile structures and aircraft shall not be required to comply with the maximum slope or maximum rise for a single ramp run. |
| 1010.6.3 | Landing length | 1010.6.3 | Landing length | Added Exception 2 which permits the landing length to be 48 inches where the ramp is not part of an accessible route. New Exception 3 refers to Section 11.4.8.4 for accessible landings. |
| 1010.6.4 | Landing and change in direction | 1010.6.4 | Landing and change in direction | Revised section to remove reference "as applicable in 101.2." |
| 1010.7 | Ramp construction | 1010.7 | Ramp construction | Revised referenced section from "1019" to "1020." |
| 1010.7.2 | Outdoor conditions | 1010.7.2 | Outdoor conditions | Removed requirement to prevent accumulation of excessive water or snow. |
| 1010.8 | Handrails. | 1010.8 | Handrails. | Correct reference in section and exception 2. Handrails shall be provided along both sides of a ramp run with a rise greater than 6 inches (152 mm) and shall conform to the requirements in Section 1012 . If handrails are not continuous, they shall extend at least 18 inches (305 mm) beyond the top and bottom of the ramp segment and shall be parallel with the floor or ground surface. Ends of handrails shall be either rounded or returned smoothly to floor, wall or post. Handrails shall not rotate within their fittings. Top of the handrail gripping surface shall be not less than 34 inches (864 mm) nor more than 38 inches (965 mm) above the ramp surface. Exceptions: 1. Handrails are not required when the total ramp run rise is 6 inches (152 mm) or less and the horizontal projection is 72 inches or less, except where required to be accessible. 2. Aisles in Group A occupancies (see Section 1025). 3. In dwelling units not required to be accessible by Chapter 11, handrails are not required to extend beyond the top and bottom of the ramp segment. 4. Handrails are not required on curb ramps. |
| 1010.9.1 | Railings | - | - | Section combined with Section 1019.2 and renumbered to Section 1019.1 |
| 1010.9.2 | Curb or barrier | 1010.9.1 | Curb, rail, wall or barrier | Relocated section, revised title and added terms "rail and wall" to the scope of this section. |
| - | - | 1012 | Handrails | New section for handrails was added to eliminate confusion between requirements for ramps and stairways. Correlation was also provided where applicale with accessibility requirements. |
|  |  | 1012.5 | Handrail extensions | Correct section reference and dimension of previously adopted Florida Specific amendment. Handrails shall return to a wall, guard or the walking surface or shall be continuous to the handrail of an adjacent stair flight or ramp run. At stairways where handrails are not continuous between flights, the handrails shall extend horizontally at least 12 inches (305 mm) beyond the top riser and continue to slope for the depth of one tread beyond the bottom riser. At ramps where handrails are not continuous between runs, the handrails shall extend horizontally above the landing 18 inches (305 mm) minimum beyond the top and bottom of ramp runs. Exceptions: 1. Handrails within a dwelling unit that is not required to be accessible need extend only from the top riser to the bottom riser. 2. Aisle handrails in Group A occupancies in accordance with Section 1025.13. 3. Accessible handrail extensions shall be as per Section 11-4.8.5(2). |
| 1012.1 | Guards scope | 1013.1 | Guards scope | Revised section to add, "Where glass is used to provide a guard or as a portion of the guard system, the guard shall also comply with Section 2407." |
| 1012.2 | Guards height | 1013.2 | Guards height | Relocated section and removed reference to "applicable in Section 101.2." |
| 1012.3 | Opening limitations | 1013.3 | Opening limitations | Relocated section and added exception number 5: "Within individual dwelling units and sleeping units in Group R-2 and R-3 occupancies, openings for required guards on the sides of stair treads shall not allow a sphere of 4.375 inches (111 mm) to pass through." |
| 1012.5 | Mechanical equipment guards | 1013.5 | Mechanical equipment guards | Revised section to add roof hatch openings to the list of items includes in scope to require guards. Also added, "The guard shall extend not less than 30 inches (762mm) beyond each end of such appliance, equipment, fan or component." |
| - | - | 1013.6 | Roof access | New section added to include guard requirements for roof hatch openings. |
| 1013.2 | Egress through intervening spaces | 1014.2 | Egress through intervening spaces | Revised organization of this section for clarity and so that each requirement can stand on it's own. Scope information has been moved to item number 1. The exception for item number 1 was revised to add Groups S and F. New exception 2 permits egress through a stockroom serving a Group M occupancy under certain conditions. |
| 1013.2.1 | Exit access for multiple tenants | 1014.2.1 | Exit access for multiple tenants | A new exception has been added that permits egress through adjoining tenant spaces where such tenant spaces occupy less than 10 percent of the area of the tenant space through which they pass. Additional stipulations include: 1. Same or similar occupancy 2. Discernable path of egress travel is provided 3. Not subject to locking from the egress side 4. Required means of egress serving the larger tenant space is not permitted to pass through the smaller space |
| 1013.2.2 | Group I-2 suite egress | 1014.2.2 | Group I-2 suite egress | Revised exemption 4 and added exemption 5 for the purpose of clarification and greater flexibility for suite layout, without compromise of original intent. |
| 1013.3 | Common path of egress travel | 1014.3 | Common path of egress travel | Numerous revisions were made to the provisions for common path of egress travel primarily for consistency with the Florida Fire Prevention Code. Notable changes include:1. Groups F, M, and S occupancy are permitted a common path of travel of 100 feet provided the building is equipped with an automatic sprinkler system. Otherwise the common path of egress travel is 75 feet.2. Group R-2 is permitted a common path of egress travel of 125 feet within the dwelling unit provided the building is provided with an automatic sprinkler system.3. Where the occupant load in a tenant space of Group A occupancy exceeds 50, the common path of egress travel is limited to 20 feet.4. Common path of egress travel in Group F and S is limited to 50 feet in unsprinklered buildings.5. Common path of egress travel in Group S2 parking garages is limited to 50 feet.6. Common path of egress travel in Group H occupancies is prohibited |
| - | - | 1014.4.2 | Aisle access ways in Group M | Added new section and exception to provide requirements specific to aisle accessways in Group M, including the introduction of the term merchandise pad. This new section assists with clarity regarding the distinction between aisles and aisle access way. |
| 1013.4.2.1 | Aisle access way for tables and seating | 1014.4.3.1 | Aisle access way for tables and seating | Revised reference in this section from "1013.4.1" to "101.4.3.1." |
| Table 1014.1 | Spaces with One Means of Egress | Table 1015.1 | Spaces with One Means of Egress | Occupant load thresholds were lowered from 50 to 49 for Groups A, B, E, F, M, U, R-2, and R-3. Occupant load threshold for Group S was lowered from 30 to 29. Group D occupant load threshold for a single means of egress has been lowered from 50 to 10. |
| Table 1014.1 | Spaces with One Means of Egress | Table 1015.1 | Spaces with One Means of Egress | Remove conflict with Florida Specific amendment. Delete footnote a. to Table |
| 1014.2.2 | Three or more exits or exit access doorways | 1015.2.2 | Three or more exits or exit access doorways | Majority of the provisions removed and referenced to Section 1015.2.1 for clarity. |
| 1014.3 | Boiler, incinerator and furnace rooms - diagonal dimension requirement | 1015.3 | Boiler, incinerator and furnace rooms - diagonal dimension requirement | Editorial revisions for clarity. |
| Table 1015.1 | Exit Access Travel Distance | Table 1016.1 | Exit Access Travel Distance | Travel distances have been revised for various occupancies for correlation with the FFPC. |
| 1016.2 | Corridor width | 1017.2 | Corridor width | Revised exception number 2 from "50 or less" to "less than 50." |
| 1016.4 | Air movement in corridors | 1017.4 | Air movement in corridors | Revised section to state "corridors" versus "exit access corridors" for code language consistency. |
| 1018.1 | Minimum number of exits | 1019.1 | Minimum number of exits | Revised section reference from "Table 1018.1" to 1019.1." |
| Table 1018.1 | Min Number of Exits for Occupant Load | Table 1019.1 | Min Number of Exits for Occupant Load | Revised column headings to add subheadings. Occupant load has addition "persons per story" and Min number of exits has addition "per story." |
| Table 1018.2 | Buildings with One Exit | Table 1019.2 | Buildings with One Exit | Occupanct number threshold for Groups A, B, D, E, F, M, U was revised from "50" to "49." Occupancy S was revised from "30" to "29." Also added footnote e to clarify requirement of maximum occupant load of 10 for day care. |
| 1019.1 | Scope for vertical exit enclosures | 1020.1 | Scope for vertical exit enclosures | Added statement, "in accordance with Section 706 or horizontal assemblies constructed in accordance with Section 711, or both." Revised language from "shaft enclosure" to "exit enclosure." Also added An exit enclosure shall not be used for any purpose other than means of egress." Revised exception 1 and 3 for language clarity - intent remains the same. Exception(s) 8 and 9 adds, "Unenclosed exit stairways shall be remotely located as required in Section 1015.2." |
| 1019.1.1 | Openings and penetrations | 1020.1.1 | Openings and penetrations | Revised language for clarity to change the term "unexposed" to "unprotected" and added statement, "Elevators shall not open into an exit enclosure." |
| 1019.1.3 | Ventilation and exit enclosures | 1020.1.3 | Ventilation and exit enclosures | Revised section to add reference 1020.1.2 to scope of this section and revised reference to Chapter 7 to 'section 715" for shaft enclosures. |
| 1019.1.4 | Vertical enclosure exterior walls | 1020.1.4 | Exit enclosure exterior walls | Revised title of section and first sentence per new language utilized throughout code to revise "vertical enclosure" to "exit enclosure" terms. Administrative language revision to clarify that it is the exterior wall that shall be protected by opening protectives." |
| 1019.1.5 | Enclosures under stairways | 1009.5.3 | Enclosures under stairways | Relocated information in this section to 1009.5.3. Permits spaces understairways within a dwelling unit in Group R-2 or R-3 to be protected on the enclosed side with 0.5 inch gypsum board. |
| 1019.7 | Stairway floor number signs | 1020.7 | Stairway floor number signs | Revised section per new language to revise "vertical enclosure" to "exit enclosure" terms. |
| 1019.1.8.1 | Enclosure exit | 1020.1.7.1 | Enclosure exit | Revised section to add exception number 3, "A smokeproof enclosure or pressurized stairway shall be permitted to egress through areas on the level of discharge or vestibules as permitted by Section 1024" to add an additional option for exit discharge. |
| 1021.2 | Horizontal exits and separation | 1022.2 | Horizontal exits and separation | Revised language in section to specify a fire-resistance rating of not less than 2 hours versus a 2-hour fire resistance. |
| 1021.3 | Opening protectives | 1022.3 | Opening protectives | Revised section reference from "907.10" to "715.4.7.3." |
| 1021.4 | Capacity of refuge area | 1022.4 | Capacity of refuge area | Revised refuge area computation by removing the statement, "not including areas of stairways, elevators, and other shafts or courts" from area capacity. |
| 1022.2 | Exit ramps and stairway use as means of egress | 1023.2 | Exit ramps and stairway use as means of egress | Revised section language. Basic requirement remains that ramp or stairway may be used if building doesn't exceed 4 stories or is more than 75 feet; however, language was revised to remove "above grade plane" and "above the lowest level of fire department vehicle access." |
| 1022.6 | Exterior ramps and stairway protection | 1023.6 | Exterior ramps and stairway protection | Revised exception 1 language to state "above grade plane" from "above grade." |
| 1023.5.2 | Construction and openings | 1024.5.2 | Construction and openings | Administrative language revision to clarify that it is the exterior wall that shall be protected by opening protectives. Deleted reference to 101.2 to exception number 2. |
| 1023.6 | Access to public way | 1024.6 | Access to public way | Revised term utilized in exemption number 2 from "property" to "lot." |
| 1024.5 | Interior balcony and gallery means of egress | 1025.5 | Interior balcony and gallery means of egress | Revised occupant load from "over 50" to "50 or more." |
| 1024.5.1 | Enclosure of balcony openings | 1025.5.1 | Enclosure of balcony openings | Revised term "churches" to "places of religious worship." |
| 1024.6.1 | Assembly without smoke protection | 1025.6.1 | Assembly without smoke protection | Revised exception 4 - "8-percent slope" to "8.333 percent slope." |
| 1024.6.2 | Assembly smoke-protected seating | 1025.6.2 | Assembly smoke-protected seating | Revised reference in this section from "1024.6.2" to "1025.6.2." Removed "single assembly" term regarding total number of seats in the space. |
| 1024.7 | Assembly travel distance | 1025.7 | Assembly travel distance | Revised travel distances for nonsprinklered buildings from "150 feet" to "200 feet" and for sprinklered buildings from "200 feet" to 250 feet." |
| 1024.9.1 | Minimum aisle width | 1025.9.1 | Minimum aisle width | Revised section exemption for aisles having seating on both sides from "does not serve more than 50 seats" to "serves less than 50 seats." Exception number 6 relocated to Exception number 5, item 2. |
| 1024.9.2 | Means of egress capacity. | 1025.9.2 | Means of egress capacity. | Correct reference in section. The capacity of means of egress shall be in accordance with Section 1005. The width of aisles and other means of egress serving theater-type seating or similar seating arranged in rows shall provide sufficient capacity in accordance with Sections 1025.9.2.1 and 1025.9.2.2. |
|  |  | 1025.9.2.1 |  | Correct reference in section. Minimum clear widths of aisles and other means of egress serving theater-type seating, or similar seating arranged in rows, shall be in accordance with Table 1025.9.2.1. |
|  |  | 1025.9.2.2 |  | Correct reference in Exception 2. The minimum clear widths shown in Table 1025.9.2.1 shall be modified in accordance with all of the following: 1. If risers exceed 7 inches (178 mm)in height, multiply the stair width in the table by factor A, where A = 1 + (riser height - 7 inches) 5 2. Stairs not having a handrail within a 30-inch (762 mm) horizontal distance shall be 25 percent wider than otherwise calculated (i.e., multiply by factor B = 1.25). 3. Ramps steeper than 1:10 slope where used in ascent shall have their width increased by 10 percent (i.e., multiply by factor C = 1.10). Exceptions: 1. Lighting and access catwalks shall meet the requirements for Group F occupancies. 2. Grandstands, bleachers and folding and telescopic seating as permitted by Section 1025.6.2. |
| 1025.1 | Scope of emergency escape | 1026.1 | Scope of emergency escape | Revised last sentence to state that opening will open directly into public way or to a yard or court that opens to a public way. Revision provided for clarity. |
|  |  | 1025.9.3 | Converging aisles | Add text left out of code. Where aisles converge to form a single path of egress travel, the required egress capacity of that path shall not be less than the combined required capacity of the converging aisles. |
|  |  | 1025.10 | Aisle accessways. | Correct reference in section. The aisle accessway between rows of seating shall have a clear width of not less than 12 inches (305 mm), and the minimum width shall be increased in accordance with Section 1025.10.2 for seating not at tables and Section 1025.10.2.2 for seating at tables. The width of aisle accessways shall be the clear horizontal distance from the back of the row ahead and the nearest projection of the row behind. Where chairs have automatic or self-rising seats that comply with ASTM F 851, the measurement shall be made with seats in the raised position. Where any chair in the row does not have an automatic or self-rising seat, the measurements shall be made with the seat in the down position. For seats with folding tablet arms, row spacing shall be determined with the tablet in the useable position. No change to remainder of text. |
|  |  | 1026.4.1 |  | Add exceptions to be consistent with FFPC. Every room or space greater than 250 square feet (23.2 m2) in educational occupancies used for classroom or other educational purposes or normally subject to student occupancy and every room or space normally subject to client occupancy, other than bathrooms, in Group D occupancies shall have not less than one outside window for emergency rescue that complies with the following: 1. Such windows shall be openable from the inside without the use of tools and shall provide a clear opening of not less than 20 inches (508 mm) in width, 24 inches (610 mm) in height, and 5.7 square feet (0.53 m2) in area. 2. The bottom of the opening shall be not more than 44 inches (1118 mm) above the floor, and any latching device shall be capable of being operated from not more than 54 inches (1372 mm) above the finished floor. Exceptions: - Buildings protected throughout by an approved, supervised automatic sprinkler system in accordance with section 903.3.1.1. - Where the room or space has a door leading directly to the outside of the building. |
|  |  | 1027.2 | Handrails and guardrails. | Correct reference in section. Handrails and guardrails shall be in accordance with Sections 1012 and 1013. Exceptions: No change. |
|  |  | 1027.3 | Stairs | Correct reference in section. Spiral stairs complying with Section 1009.8 shall be permitted as a component in a means of egress. |
|  |  | 1029.1 | Handrails and guardrails. | Correct reference in section. Handrails and guardrails shall be installed in accordance with Sections 1009.12 and 1013. Exceptions: No change. |
|  |  | 1029.2 | Stairs. | Spiral stairs complying with Section 1009.8 shall be permitted as a component in a means of egress. |
|  |  | 1030.11.1 |  | Correct reference in section. Travel distance shall not exceed that specified in Table 1016.1. |
|  |  | 1030.12 | Measurement of travel distance to exits | Correct reference in section Travel distance shall be determined in accordance with Section 1016 but shall not exceed: 1. One-hundred feet (30 480 mm) between any room door required as exit access and an exit. 2. One-hundred-and-fifty feet (45 720 mm) between any point in a room and an exit. 3. Fifty feet (15 240 mm) between any point in a sleeping room and the door of that room. No change to remainder of text. |
|  |  | 1030.13.1 |  | Correct reference in section Spiral stairs meeting the requirements of Section 1009.8 are permitted for access to and between staff locations |
|  |  | 1031.13.2 |  | Correct reference in section Alternating tread stairways meeting the requirements of Section 1009.9 are permitted for access to and between staff locations subject to occupancy by no more than three persons all capable of using the alternating tread stairway. |
|  |  | 1030.13.3 |  | Correct reference in section Solid risers, intermediate handrails, latticework or similar facilities required by Sections 1009.3.3 and 1013.3 which would interfere with visual supervision of residents are not required. |
|  |  | 1013.1 | Stairs | Correct reference in section Spiral stairs complying with Section 1009.8 shall be permitted as a component of egress. |
|  |  | 1031.2 | Handrails and guardrails. | Correct reference in section Handrails and guardrails shall be installed in accordance with Sections 1009.12 and 1013. Exceptions: No change. |
|  |  | 1033.2 | Stairs. | Spiral stairs complying with Section 1009.8 shall be permitted as a component of egress. |
|  |  | 1033.3 | Handrails and guardrails. | Correct reference in section Handrails and guardrails shall be installed in accordance with Sections 1009.12 and 1013. Exception: In areas not accessible to the public in Group S, the clear distance between rails or ornamental pattern shall be such as to prevent the passage of a 21-inch (533 mm) diameter sphere. |
|  |  | 1034.2.3 |  | Correct reference in section Doors designed to be normally closed shall comply with Section 715.4.7. |
| Chapter 11: Florida Accessibility Code |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
|  |  | 11-4.3.3 | Width. | The minimum clear width of an accessible route shall be 36 inches (915 mm) except at doors (see Section 11-4.13.5 and 11-4.13.6). If a person in a wheelchair must make a turn around an obstruction, the minimum clear width of the accessible route shall be as shown in Figure 7(a) and Figure 7(b). Exceptions: 1. Curb ramps that are a part of a required means of egress shall be not less than 44 inches (1118 mm) wide. 2. All spaces must be located on an accessible route no less than 44 inches (1118 mm) wide so that users will not be compelled to walk or wheel behind parked vehicles. |
|  |  | 11-4.6.4 | Signage. | Each such parking space must be prominently outlined with blue paint, and must be repainted when necessary, to be clearly distinguishable as a parking space designated for persons who have disabilities and must be posted with a permanent above-grade sign of a color and design approved by the Department of Transportation which is placed on or at a distance of 84 inches above the ground to the bottom of the sign and which bears the international symbol of accessibility, ADAAG Section 4.30.7 and the caption “PARKING BY DISABLED PERMIT ONLY.” Such sign erected after October 1, 1996, must indicate the penalty for illegal use of the space. Remaining text unchanged. |
|  |  | Chapter 11 Part C |  | CHAPTER 11 REQUEST FOR WAIVER FROM ACCESSIBILITY REQUIREMENTS CHAPTER 553, PART V, FLORIDA STATUTES August 1999 PART C See www.floridabuilding.org for the Waiver from Accessibility Requirements form and Florida Administrative Code Chapter 9B-7, |
|  |  | Chapter 11 Part C |  | Delete Form 2002-01 Part C Delete NOTICE OF WAIVER APPLICANTS Delete REQUEST FOR WAIVER FROM ACCESSIBILITY REQUIREMENTS CHAPTER 553, PART V, FLORIDA STATUTES Delete text of Rule 9B-7 |
| Chapter 12: Interior Environment |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
|  |  | 1202.1 | Definitions | Delete definition and Reserve section. SUNROOM ADDITION. Reserved. |
| 1203.2 | Attic spaces, ventilation | 1203.2 | Attic spaces, ventilation | Exception added that permits attics to be unvented provided the space is designed by a Florida-licensed engineer or registered architect. |
| 1203.3.2 | Exceptions, under-floor ventilation | 1203.3.2 | Exceptions, under-floor ventilation | Exception added that permits crawl spaces to be unvented provided the space is designed by a Florida-licensed engineer or registered architect. |
| Chapter 13: Energy Efficiency |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
|  |  | Chapter 13 | General | Removed the “.2” performance-based requirements from both Subchapter 13-4 and 13-6 of the code and put them into Appendices 13-B and 13-C. Deleted the exception in Section 13-103.1.1.1 that typed names and registration numbers may be provided in lieu of a design professional’s signature where all relevant information has been included on signed and sealed plans. Revised the exceptions to code compliance in Section 13-101.5.7 for 1) buildings containing a system designed and sold for dehumidification purposes only and 5) electrical equipment switching buildings in which no-one works on a regular basis to require that the electric power provisions of Section 13-413 shall apply. Revised standards in Subchapter 13-3 to ASHRAE 90.1-2004. Revised ASHRAE 62 to 62.1-2004 for consistency with FBC-Mechanical. In Section 13-101.6, added criteria for demonstrating the efficiency of mechanical systems undergoing alteration. |
|  |  | Chapter 13 | Commercial and High-Rise Residential | Updated Subchapter 13-4 of the code to ASHRAE 90.1-2004 and simplified the text by moving performance criteria to Appendix 13-B. Changed climate zones to ASHRAE Climate Zone 1 (Broward, Miami-Dade, and Monroe counties) and ASHRAE Climate Zone 2 (the rest of the State) Revised the Subchapter 13-4 Baseline features (ASHRAE 90.1-2004) to utilize a 0.85 multiplier, making the commercial energy code provisions 15 percent more stringent. Deleted Methods B and C because of difficulty in making them 15 percent more stringent. Added a new commercial compliance Method B (and Form 400B-08) for shell buildings, renovations, equipment change-outs and other instances where specific components shall meet code for that item(s) alone. Shell buildings shall meet compliance Method A at final build-out to demonstrate that the 15 percent overall increase in code stringency has been met for equipment and lighting as well. Added an exception under Section 13-407.AB.2.4 Off-hour controls, for HVAC systems having a design heating capacity and cooling capacity less than 15,000 Btu/h that are equipped with readily accessible manual on/off controls. Clarified Section 13-407.AB.3.1.1 Equipment efficiency verification criteria per ASHRAE 90.1-2004. Consolidated the water-cooled centrifugal water-chilling package criteria in Section 13-407.AB.3.2.2 into three tables by size of chiller. Deleted Section 13-407.1.ABC.3.4.2, Fan speed control. Clarified Table 13-409.AB.3.3, Maximum damper leakage. Revised Table 13-410.AB.2.2, Minimum Duct Insulation R-values, fixed the R-value for ducts in unconditioned spaces, and deleted the R-8 duct requirement for unvented attic spaces in Broward, Miami-Dade and Monroe counties. |
|  |  | Chapter 13 | Residential | Revised Subchapter 13-6, the Method A code compliance methodology for multiple-family residential up to and including 3 stories and simplified the text by moving performance criteria to Appendix 13-C. Switched to the EnergyGauge USA Fla/Res computer program, which uses hourly simulation modeling, as the Method A residential energy code compliance tool. Moved the Method A Baselines to Table 13-613.A.1-1 [ N1113.A.1-1]. The Baselines are similar to the Standard Reference Design in Table 404.5.2(1) of the 2006 International Energy Conservation Code (IECC). Revised the “2007” Baselines with a 0.85 multiplier to make the residential energy code 15 percent more stringent in the “2008” energy code provisions. Revised the compliance Method B provisions to reflect the 15 percent increase in stringency, including U-0.65, SHGC 0.35 glazing, with a maximum of 16 percent glass to conditioned floor area, and ducts either interior to conditioned space or tested to demonstrate they are “air tight”. Deleted compliance Method C in its entirety. Renovations, equipment change-outs, and small additions were moved to compliance with the component efficiencies in Method B. Kept the old Residential Points System Method (Form 600A) only as a hand calculation; it also has a 0.85 multiplier on the Baseline and can be found in Appendix G-C of the FBC-Residential and in Appendix 13-2C of the FBC-Building. Revised treatment of gas and electric hot water and conditioning systems; they will be compared to the same fuel type Baseline. Added that HVAC sizing calculations shall account for directional orientation of the building. Eliminated the restriction of using the rooftop for outside air intake. |
| Chapter 14: Exterior Walls |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
|  |  | 1401.1 | Scope. | ICC Code change not included in code at printing. The provisions of this chapter shall establish the minimum requirements for exterior walls, exterior wall coverings, exterior wall openings, exterior windows and doors, architectural trim, balconies and similar projections; bay and oriel windows. Exceptions: No change. |
| 1402.1 | Definitions | 1402.1 | Definitions | New definitions added for "Vinyl Siding" and "Water-resistive Barrier." |
| 1403.2 | Weather protection | 1403.2 | Weather protection | Section revised to delete language that eliminated the need for draining water to the exterior if determined that the penetration of water behind the veneer is not detrimental to the building performance. |
| 1403.3 | Vapor retarder | - | - | Deleted for consistency with the Energy Code. |
| - | - | 1404.5.2 | Cold-rolled copper | New section requiring cooper to conform to ASTM B 370. |
| - | - | 1404.5.3 | Lead-coated copper | New section requiring lead-coated copper to conform ASTM B 101. |
| 1405.4 | Wood veneers | 1405.4 | Wood veneers | Section revised for clarity and "grade" changed to "grade plane." |
| 1405.6 | Stone veneer | 1405.6 | Stone veneer | In item 2, "waterproofed paper backing" changed to "water-resistive barrier." |
| - | - | 1405.12.2 | Window sills | New section requiring lowest part of the clear opening of a window to be 24 inches above the finished floor surface where the opening of the sill portion of an operable window is located more than 72 inches above finished grade or other surface below. An exception permits the use of window guards complying with ASTM F 2006 or F 2090 in lieu of the 24 inch minimum height. |
| 1405.13.1 | Application, vinyl siding | 1405.13.1 | Application, vinyl siding | "Weather-resistant" barrier changed to "water-resistive" barrier. |
| 1505.15 | Fiber cement siding | 1505.15 | Fiber cement siding | "Weather-resistant" barrier changed to "water-resistive" barrier. |
| 1406.1 | General, combustible materials on the exterior side of exterior walls | 1406.1 | General, combustible materials on the exterior side of exterior walls | Scope revised to read balconies and similar "projections" instead of "appendages." |
| 1406.2.4 | Fireblocking | 1406.2.4 | Fireblocking | Section revised by deleting opening limitations for fireblocking and exceptions for fireblocking, to reduce conflicts and provide consistency with Section 717.2.6. Opening limitations and previous exceptions to this sections are covered in Section 717.2.6. |
| 1406.3 | Balconies and similar projections | 1406.3 | Balconies and similar projections | Editorial revisions for clarity. |
| - | - | 1407.1.1 | Plastic core, MCM | New section prohibiting the use of foam plastic insulation in the plastic core of MCM. |
| 1407.2 | Exterior wall finish, MCM | 1407.2 | Exterior wall finish, MCM | Editorial revising changing "appendages" to "projections." |
| 1407.10.3 | Thermal barrier not required, MCM | 1407.10.3 | Thermal barrier not required, MCM | Editorial revising changing "appendages" to "projections." |
| Chapter 15: Roof Assemblies and Rooftop Structures |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| 1502.1 | Definitions | 1502.1 | Definitions | Add new definitions: AGGREGATE. In roofing, crushed stone, crushed slag or water-worn gravel used for surfacing for roof coverings. BALLAST. In roofing, ballast comes in the form of large stones or paver systems or light-weight interlocking paver systems and is used to provide uplift resistance for roofing systems that are not adhered or mechanically attached to the roof deck. |
| 1502.1 | Definitions | 1502.1 | Definitions | New definitions added for "Roof Section." |
|  |  | 1503.1 | General. | Roof decks shall be covered with approved roof coverings secured to the building or structure in accordance with the provisions of this chapter. Roof coverings shall be designed, and installed in accordance with this code and the approved manufacturer’s instructions such that the roof covering shall serve to protect the building or structure. |
|  |  | 1504.1.2 Table 1504.1.2 | Alternate Test Method Roof Covering Classification using Alternate Method | Delete Section 1504.1.2 and Table 1504.1.2 |
| 1504.3.2 | Metal panel roof systems | 1504.3.2 | Metal panel roof systems | Testing for metal panel roof systems through fastened or standing seam expanded to include TAS 125. New exception permits metal roofs constructed of cold-formed steel to be designed and tested in accordance with Section 2209.1 when conditions specified are met. |
|  |  | 1504.4 | Ballasted low-slope roof systems. | Correct error made in printing of code. Ballasted low-slope (roof slope < 2:12) single-ply roof system coverings shall be designed in accordance with ANSI/SPRI RP-4. |
| 1504.5 | Edge-securement for low-slope roofs | 1504.5 | Edge-securement for low-slope roofs | Section revised to require metal edge securement for low-slope membrane roofs to be designed and installed for wind loads in accordance with Chapter 16 and tested for resistance in accordance with ANSI/SPRI ES-1 |
| 1504.7 | Impact resistance | 1504.7 | Impact resistance | Revised to reference the "Resistance to Foot Traffic Test" when using FM 4470. Metal roofing systems having a thickness equal to or greater than 22 gage and all non-structural metal roof systems with a thickness equal to or greater than 26 gage are exempt from the impact test. |
| - | - | 1504.8 | Gravel and stone | New section prohibiting the use of gravel or stone on the roof of a building located in a hurricane-prone region. |
|  |  | 1504.8 | Aggregate | Add criteria for aggregate roofing material as required by law. Aggregate shall be permitted as roof surfacing when installed on slopes of 3:12 or less, not less than 400 pound (182 kg) of roofing gravel or 300 pounds (145 kg) of slag per square shall be applied. A minimum of 50 percent of the total aggregate shall be embedded in the flood coat of bitumen or installed in accordance with its product approval. Aggregate shall be dry and free from dirt and shall be in compliance with the sizing requirements set forth in ASTM D 1863. A building official may request a test to confirm compliance with these requirements Delete Table 1504.8 |
| - | - | 1504.9 | Margin of safety | New section requires the use of a 2:1 margin of safety for wind uplift tests unless specified in the applicable standard. Asphalt shingles that are given a mph rating are exempt from the margin of safety. |
| 1505.1 | General, fire classification | 1505.1 | General, fire classification | New exception exempts skylights and sloped glazing comply with Chapter 24 or Section 2610 from the fire classification requirements of Section 1505. |
| 1505.2 | Class A roof assemblies | 1505.2 | Class A roof assemblies | Exception revised to read ferrous or copper shingles or "sheets" instead of "panels." |
| 1506.6 | Screws | 1506.6 | Screws | Section revised for clarity and ASTM B 117 and TAS 114 Appendix E added for corrosion resistance tests. |
| 1506.7 | Clips | 1506.7 | Clips | Corrosion resistance for clips revised to 0.90 oz. per sq. ft. according to ASTM A 90/A or TAS 114 Appendix E. |
|  |  | 1507.2.3 | Underlayment. | Add new standard for underlayment. Unless otherwise noted, required underlayment shall conform to ASTM D 226, Type I or Type II, or ASTM D 4869 Type I or Type II, or ASTM D 6757. |
| 1507.2.5 | Asphalt shingles | 1507.2.5 | Asphalt shingles | New language providing cross-reference for wind resistance of asphalt shingles in accordance with Table 1507.2.10. Permits shingles to have a listing by an approved testing agency in accordance with the requirements of Section 1609.5.2. |
|  |  | 1507.2.5 | Asphalt shingles. | Correct conflict in code regarding asphalt shingle testing and packaging. Asphalt shingles shall have self-seal strips or be interlocking and comply with ASTM D 225 or ASTM D 3462. Shingles shall also comply with Section 1507.2.10. Asphalt shingle packaging shall bear labeling indicating compliance with one of the required classifications as shown in Table 1507.2.10 or a listing by an approved testing agency in accordance with the requirements of Section 1609.5.2. |
| 1507.2.8 | Underlayment application | 1507.2.8 | Underlayment application | New language added stating that distortions in the underlayment are not permitted to interfere with the ability of the shingles to seal. The wind resistance of shingles will be affected if their ability to seal is compromised. |
| 1507.2.9.4 | Crickets and saddles | 1507.2.9.4 | Crickets and saddles | New language clarifying that the measurement of the chimney or penetration, in regards to whether a chimney or saddle is required, is perpendicular to the slope. An exception has been added that eliminates the need for a cricket or saddle for penetrations that permit water to flow around. |
| 1507.3.3.1 | Low-slope roofs, clay and tile underlayment | 1507.3.3.1 | Slope and underlayment requirements, clay and tile | Refers to the FRSA/TRI manual for underlayment and slope requirements for specific tile systems. |
| 1507.3.6 | Fasteners, clay and tile | 1507.3.6 | Fasteners, clay and tile | Section revised to permit fasteners in accordance with the FRSA/TRI manual. Language requiring perimeter fastening areas of three tile courses but not less than 36 inches from either side of hips or ridges and edges of eaves and gable rakes has been deleted. |
| 1507.4.2 | Deck slope, metal roof panels | 1507.4.2 | Deck slope, metal roof panels | Section reformatted in numbered list for clarity. Requires lap sealants to be applied in accordance with the approved manufacturer's installation instructions. |
| 1507.4.3 | Material standards, metal roof panels | 1507.4.3 | Material standards, metal roof panels | New language added requiring corrosion resistance for materials used for metal-sheet roof coverings in accordance with the standards and thicknesses specified in Table 1507.4.3(2) or the material is required to be naturally corrosion resistant. |
|  |  | Table 1507.4.3(1) | Metal Roof Covering | Correct reference to standard for steel roof panel to ASTM A924/A924M |
| - | - | Table 1507.4.3(2) | Minimum corrosion resistance, metal roof panels | New table specifying corrosion resistance standards for metal roof panels. |
| 1507.4.4 | Attachment, metal roof panels | 1507.4.4 | Attachment, metal roof panels | New language clarifying that metal roof panels are required to be fastened to the supports instead of steel framing, as metal roof panels are often fastened to supports other than steel framing. Item 1 requires galvanized fasteners to be used for "steel" roofs instead of "galvanized" roofs. |
| 1507.5.3 | Underlayment, metal roof shingles | 1507.5.3 | Underlayment, metal roof shingles | ASTM D 4869 permitted as compliance option for underlayment. |
| 1507.5.4 | Material standards, metal roof shingles | 1507.5.4 | Material standards, metal roof shingles | New language added requiring corrosion resistance for materials used for metal shingle roof coverings in accordance with the standards and thicknesses specified in Table 1507.4.3(2) or the material is required to be naturally corrosion resistant. |
|  |  | 1507.5.6 | Flashing | Editorial change to correct typo. Roof valley flashing shall be of corrosion-resistant metal of the same material as the roof covering or shall comply with the standards in Table 1507.4.3(1). The valley flashing shall extend at least 8 inches (203 mm) from the centerline each way and shall have a splash diverter rib not less than 0.75 inch (19.1 mm) high at the flow line formed as part of the flashing. Sections of flashing shall have an end lap of not less than 4 inches (102 mm). |
| 1507.6.3 | Underlayment, mineral-surfaced roll roofing | 1507.6.3 | Underlayment, mineral-surfaced roll roofing | ASTM D 4869 added as compliance option for underlayment used in mineral-surfaced roll roofing. |
| 1507.7.3 | Underlayment, slate shingles | 1507.7.3 | Underlayment, slate shingles | ASTM D 4869 added as compliance option for underlayment used for slate shingle roofing. |
|  |  | 1507.7.3 | Underlayment, slate shingles | Clarify the ASTM D4869 is Type II Underlayment shall comply with ASTM D 226, Type II or ASTM D 4869 type II. |
| 1507.8.3 | Underlayment, wood shingles | 1507.8.3 | Underlayment, wood shingles | ASTM D 4869 added as compliance option for underlayment used for wood shingle roofing. |
|  |  | 1507.8.3 | Underlayment, wood shingles | Clarify the ASTM D4869 is Type I Underlayment shall comply with ASTM D 226, Type I or ASTM D 4869 type I. |
|  |  | 1507.8.7 | Flashing. | Allow user to upgrade flashing above minimum. At the juncture of the roof and vertical surfaces, flashing and counterflashing shall be provided in accordance with the manufacturer’s installation instructions, and where of metal, shall comply with Table 1503.2. The valley flashing shall extend at least 11 inches (279 mm) from the centerline each way and have a splash diverter rib not less than 1 inch (25 mm) high at the flow line formed as part of the flashing. Sections of flashing shall have an end lap of not less than 4 inches (102 mm). For roof slopes of three units vertical in 12 units horizontal (25-percent slope) and over, the valley flashing shall have a 36-inch-wide (914 mm) layer of underlayment running the full length of the valley, in addition to other required underlayment. |
| 1507.9.3 | Underlayment, wood shakes | 1507.9.3 | Underlayment, wood shakes | ASTM D 4869 added as compliance option for underlayment used for wood shake roofing. |
|  |  | 1507.9.3 | Underlayment | Clarify the ASTM D4869 is Type I Underlayment shall comply with ASTM D 226, Type I or ASTM D 4869 type I |
| Table 1507.9.5 | Wood shake material requirements | Table 1507.9.5 | Wood shake material requirements | AWPA standard for preservative-treated taper sawn shakes of southern pine has been updated to the AWPA U1 (Commodity Specification A, Use Category 3B and Section 5.6). |
|  |  | 1507.9.8 | Flashing. | Allow user to upgrade flashing above minimum. At the juncture of the roof and vertical surfaces, flashing and counterflashing shall be provided in accordance with the manufacturer’s installation instructions, and where of metal, shall comply with Table 1503.2. The valley flashing shall extend at least 11 inches (279 mm) from the centerline each way and have a splash diverter rib not less than 1 inch (25 mm)high at the flow line formed as part of the flashing. Sections of flashing shall have an end lap of not less than 4 inches (102 mm). For roof slopes of three units vertical in 12 units horizontal (25-percent slope) and over, the valley flashing shall have a 36-inch-wide (914 mm) layer of underlayment running the full length of the valley, in addition to other required underlayment. |
|  |  | 1507.11.2 | Material standards | Add ASTM D 6509 to table under Modified bitumen roof membrane. Modified bitumen roof coverings shall comply with CGSB 37-GP-56M, ASTM D 6162, ASTM D 6163, ASTM D 6164, ASTM D 6222, ASTM D 6223, or ASTM D 6298 or ASTM D 6509. |
| 1507.12.2 | Material standards, thermoset single-ply roofing | 1507.12.2 | Material standards, thermoset single-ply roofing | Reference standards RMA RP-1, RP-2, and RP-3 have been deleted because the standards are not being maintained and are not being published. |
| 1507.13.2 | Material standards, thermoplastic single-ply roofing | 1507.13.2 | Material standards, thermoplastic single-ply roofing | ASTM D 6754 and ASTM D 6878 added as material standard for thermoplastic single-ply roofing. |
| 1507.15.2 | Material standards, liquid-applied coatings | 1507.15.2 | Material standards, liquid-applied coatings | ASTM D 6694 added as material standard for liquid-applied coatings. |
| 1508.1 | General, roof insulation | 1508.1 | General, roof insulation | New exception exempts concrete roof decks with the above-deck thermal insulation covered with an approved covering from the FM 4450 or UL 1256 tests. |
| - | - | 1508.2 Table 1508.2 | Material standards for roof insulation | New scoping section and table referencing material standards for minimum physical properties of roof insulation. |
| 1509.4 | Cooling towers | 1509.4 | Cooling towers | Section revised to clarify that the requirements of this section apply to cooling towers installed on roofs more than 50 feet high, not buildings 50 feet high. |
| 1509.5 | Towers, spires, domes and cupolas | 1509.5 | Towers, spires, domes and cupolas | "Grade" changed to "grade plane." |
| 1510.3 | Recovering versus replacement | 1510.3 | Recovering versus replacement | New exception added that permits the application of a new protective coating over an existing spray polyurethane foam roofing system without tear-off of the existing roof covering. |
| Table 1515.2 HVHZ | Minimum slope | Table 1515.2 HVHZ | Minimum slope | Table revised to delete the minimum slope requirements for structural metal panels. |
| 1517.15.2 HVHZ | Tin caps | 1517.15.2 HVHZ | Tin caps | Editorial revision clarifying that corrosion resistance is to be in accordance with TAS 114. |
| 1518.8.1.1HVHZ | Roof tile mortar | 1518.8.1.1HVHZ | Roof tile mortar | Editorial revision clarifying that job-site mixed roof tile mortar is to be in accordance with RAS 113. |
| 1521.12 HVHZ | Moisture content of existing roofing, reroofing | 1521.12 HVHZ | Moisture content of existing roofing, reroofing | Section revised to change "insulation system" to "commercially manufactured rigid board roof insulation." Existing lightweight insulating concrete, gypsum, and cementious wood fiber roof decks are exempt from moisture content testing. All existing lightweight insulating concrete, gypsum, and cementious wood fiber roof decks are required to be tested in accordance with Section 1521.7 to confirm compliance with Chapter 16 (HVHZ). |
| 1521.21 HVHZ | Existing ventilation | 1521.21 HVHZ | Existing ventilation | New exception permits elimination of attic ventilation provided the attic space is designed by a Florida licensed engineer or registered architect. |
| 1522.2 HVHZ | Rooftop mounted equipment | 1522.2 HVHZ | Rooftop mounted equipment | Section revised to require a permanent means of access where equipment and appliances are installed on roofs or elevated structures at a height exceeding 16 feet. Minimum design criteria provided for the installation of permanent ladders. |
| 1523.6.5.2.6.3 HVHZ | Fiber cement shingles or tile panels, testing | 1523.6.5.2.6.3 HVHZ | Fiber cement shingles or tile panels, testing | Editorial revision to change "TAS 115" to "RAS 115." |
| 1524.1 HVHZ | Required owners notification for roofing considerations | 1524.1 HVHZ | Required owners notification for roofing considerations | Item 2 editorial revised to add "of the Florida Building Code, Building." Exception added to Item 7 permitting elimination of attic ventilation provided the attic space is designed by a Florida licensed engineer or registered architect. |
|  |  | 1525 | HVHZ UNIFORM PERMIT APPLICATION | Change to year on all Uniform Permit Application to 2007 |
| Chapter 16: Structural Design |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| 1602 | Definitions: Boundary members | 1602 | Definitions: Boundary members | Definition deleted. |
| 1602 | Definitions: Cantilevered column system | 1602 | Definitions: Cantilevered column system | Definition deleted. |
| 1602 | Definitions: Collector elements | 1602 | Definitions: Collector elements | Definition deleted. |
| 1602 | Definitions: Confined region | 1602 | Definitions: Confined region | Definition deleted. |
| 1602 | Definitions: Dead load | 1602 | Definitions: Dead load | Definition revised to more specifically identify certain fixed service equipment that is assumed to be a dead load, such as plumbing stacks, risers, electrical feeders, HVAC systems, and fire sprinklers. |
| 1602 | Definitions: Deformability | 1602 | Definitions: Deformability | Definition deleted. |
| 1602 | Definitions: Deformation | 1602 | Definitions: Deformation | Definition deleted. |
| 1602 | Definitions: Diaphragm, flexible | 1602 | Definitions: Diaphragm, flexible | Definition revised to refer to Section 12.3.1 of ASCE 7 for determination of when a diaphragm is considered flexible |
| 1602 | Definitions: Element | 1602 | Definitions: Element | Definition deleted. |
| 1602 | Definitions: Equipment support | 1602 | Definitions: Equipment support | Definition deleted. |
| - | - | 1602 | Definitions: Fabric partition | New definition for fabric partition added for compliance with new Section 1607.13.1. |
| 1602 | Definitions: Flexible equipment connections | 1602 | Definitions: Flexible equipment connections | Definition deleted. |
| 1602 | Definitions: Frame | 1602 | Definitions: Frame | Definition deleted. |
| 1602 | Definitions: Joint | 1602 | Definitions: Joint | Definition deleted. |
| - | - | 1602 | Definitions: Occupancy category | New definition for occupancy category for revised Table 1604.5 |
| 1602 | Definitions: P-delta effect | 1602 | Definitions: P-delta effect | Definition deleted. |
| 1602 | Definitions: Shallow anchors | 1602 | Definitions: Shallow anchors | Definition deleted. |
| 1602 | Definitions: Shear panel | 1602 | Definitions: Shear panel | Definition deleted. |
| 1602 | Definitions: Shear wall | 1602 | Definitions: Shear wall | Definition deleted. |
| 1602 | Definitions: Space frame | 1602 | Definitions: Space frame | Definition deleted. |
| 1602 | Definitions: Special transverse reinforcement | 1602 | Definitions: Special transverse reinforcement | Definition deleted. |
| - | - | 1602 | Definitions: Vehicle barrier system | New definition of vehicle barrier system added. |
| 1602 | Definitions: Wall, load bearing | 1602 | Definitions: Wall, load bearing | Definition deleted. |
| 1602 | Definitions: Wall, nonload bearing | 1602 | Definitions: Wall, nonload bearing | Definition deleted. |
| 1603.1.1 | Floor live load | 1603.1.1 | Floor live load | Section revised to clarify that the use of live load reductions in accordance with Section 1607.9 are to be indicated fro each type of live load used in the design. |
| 1603.4 | Occupancy permits for changed loads | 1603.4 | Occupancy permits for changed loads | Exemption for residential structures for having live loads shown on construction documents has been deleted. Language requiring live loads to be shown on each drawing has been deleted since this requirement is covered elsewhere in the code. |
| Table 1604.3 | Deflection limits | Table 1604.3 | Deflection limits | Note h revised to include skylights and sloped glazing supported by aluminum structural members. |
| 1604.3.3 | Steel, serviceability | 1604.3.3 | Steel, serviceability | Reference standards for determination of deflections of steel structural members have been updated to AISC 360, AISI-NAS, AISI-General, AISI-Truss, ASCE 3, ASCE 8, SJI JG-1.1, SJI K-1.1 or SJI LH/DLH-1.1, as applicable. |
| 1604.4 | Analysis | 1604.4 | Analysis | Section revised to clarify that where diaphragms are flexible the increased forces resulting from torsion due to eccentricity is not applicable. |
| 1604.5 | Importance factor | 1604.5 | Occupancy category | Importance factors are no longer included in Table 1604.5. Buildings are now simply given an occupant category. Importance factors are determined from ASCE 7. Section revised to require that buildings be assigned an occupant category. |
| - | - | 1604.5.1 | Multiple occupancies | New section addressing how to deal with buildings that have multiple occupancies not included in the same group. Requires the building to be assigned the classification having the highest occupancy category unless the occupancies are structurally separated. If the separated occupancies share life safety components, both are required to be assigned the higher category. |
| Table 1604.5 | Classification of buildings and other structures for importance factors | Table 1604.5 | Occupancy category of buildings and other structures | Importance factors have been deleted from the table. Importance factors are now determined from ASCE 7.Criteria from Occupancy Category III has been revised to clarify the applicability of the "where more than 300 people congregate in one area." The language now states, "Covered structures whose primary occupancy is public assembly with an occupant load greater than 300." This clarifies that large commercial structures shouldn't be classified as Occupancy Category III, even if the occupant load exceeds 300, since this type of building is typically not used for public assembly. |
| 1605.2.1 1605.2.2 | Basic load combinations, load and resistance factor design | 1605.2.1 1605.2.2 | Basic load combinations, load and resistance factor design | Load combinations revised by incorporating the effects of F, H, and T in the equations for consistency with ASCE 7. |
| 1605.3.1 1605.3.1.1 1605.3.1.2 | Basic load combinations, allowable stress design | 1605.3.1 1605.3.1.1 1605.3.1.2 | Basic load combinations, allowable stress design | Load combinations revised by incorporating the effects of F, H, and T in the equations for consistency with ASCE 7. Provision permitting the combined effect of multiple transient loads to multiplied by 0.75 and added to the effect of dead load has been specifically included in the load combination equations. However, Item 1 of Section 1605.3.1.1 was inadvertently not deleted. This discrepancy will like be fixed during the 2008 Glitch cycle. |
|  |  | 1605.3.1.1 | Load reduction. | Delete paragraph 1 as load reduction is already reflect in Equation 16-13 so the section reads as follows:. 1. Increases in allowable stress specified in the materials sections of this code or a referenced standard shall not be permitted to be used with load combinations of Sections 1605.3.1. Duration of load increase shall be permitted in accordance with Chapter 23. Exception: Increases in allowable stress shall be permitted in accordance with ACI 530/ASCE 5/TMS 402 provided the load reduction of Section 1605.3.1.1 Item 1 shall not be applied. 2. Simultaneous use of both one-third increase in allowable stress and the 25 percent reduction in combined loads shall not be permitted. |
| 1605.3.2 | Alternate basic load combinations | 1605.3.2 | Alternate basic load combinations | New language requiring that the reduction of foundation overturning from 12.13.4 in ASCE 7 is not permitted to be used when these alternate load combinations are used. See also Section 1609.1.3 below for additional revisions. |
| 1605.5 | Heliports and helistops | 1605.5 | Heliports and helistops | Language revised to remove "touchdown" areas and refer to "landing" area for simplicity and clarification. New exception permits landing areas design for helicopters with gross weights not exceeding 3000 lbs to be designed for a uniform live load of 40 psf, without any live load reductions. Weight limitations required to be posted in bottom right corner of the landing area. |
| 1606.1 | General, dead loads | 1606.1 | General, dead loads | Section revised to simply refer to the definition of dead load in Section 1602.1. New language clarifying that dead loads are considered permanent loads. |
| Table 1607.1 | Minimum uniformly distributed live loads and minimum concentrated live loads | Table 1607.1 | Minimum uniformly distributed live loads and minimum concentrated live loads | Item 4. Assembly - Follow spot, projections and control rooms deleted. Catwalks removed from assembly category and relocated as specific Item 7. Catwalks live loads revised to include a 300 lb concentrated live load. Item 21. Hospitals - Wards deleted from hospitals entry and private rooms changed to "patient rooms." Item 28. Residential - Live loads for attics has been revised to redefine "uninhabitable attics with storage" to "uninhabitable attics with limited storage". New notes "i, j, and k have been added to more specifically define attics "without storage" and attics "with limited storage." Attic spaces served by a fixed stair are required to be designed to support the minimum live load specified for habitable attics and sleeping rooms. 30. Roofs - live loads for roofs have been mostly relocated from Section 1607.11 to Table 1607.1 for consistency with ASCE 7. |
| 1607.5 | Partition loads | 1607.5 | Partition loads | Partition loads in office buildings where partitions are subject to change, has been revised to 15 psf from 20 psf for consistency with ASCE 7. |
| 1607.7.1 | Handrails and guards | 1607.7.1 | Handrails and guards | New sentence added that provides a reference to Section 2407 for glass handrail assemblies and guards. Exception 2 was revised to state "less than 50" from "not greater than 50" for clarity. |
| 1607.9 | Reduction in live loads | 1607.9 | Reduction in live loads | Section revised to preclude the use of live load reductions for roof uniform live loads. |
| 1607.9.1.1 | Heavy live loads | 1607.9.1.1 | Heavy live loads | Section reformatted for clarity. Exception added that permits additional live load reductions where shown by the registered design professional, and approved by the building official, that a rational approach has been used and such reductions are warranted. |
| 1607.9.2 | Alternate floor live load reduction | 1607.9.2 | Alternate floor live load reduction | Item 2 revised to change "columns" to "members supporting two or more floors."New Item 3 added prohibiting reductions for passenger vehicle parking garages, except that live loads for members supporting two or more floors are permitted to be reduced to a maximum of 20 percent.Item 4 has been reformatted for clarity. |
| 1607.11 | Roof loads | 1607.11 | Roof loads | Live loads for roofs have been mostly relocated from Section 1607.11 to Table 1607.1 for consistency with ASCE 7. |
| 1607.13 | Interior walls and partitions | 1607.13 | Interior walls and partitions | New exception added that exempts fabric partitions complying with Section 1607.13..1 from the minimum 5 psf horizontal load. |
| - | - | 1607.13.1 | Fabric partitions | New section requiring fabric partitions exceeding 6 feet in height to resist a horizontal load of 5 psf and a concentrated load of 40 pounds. Application of the horizontal uniform and concentrated load is also addressed. |
| 1609.1 | Application, wind loads | 1609.1 | Application, wind loads | New language added requiring wall coverings and soffits to be capable of resisting design pressures specified fro walls using component and cladding loads. |
|  |  | Figure 1609 | State of Florida Debris Region and Basic Wind Speed | Add statement “As Amended by Laws CS/HB 1A – 2007” to top of Figure 1609 |
| 1609.1.1 | Determination of wind loads | 1609.1.1 | Determination of wind loads | Section revised to permit opening protection required, basic wind speed, and exposure category to be determined from Section 1609 or ASCE 7. New note added clarifying the applicability of the Figure 6-10 in ASCE 7. The language incorporates the Florida Building Commissions action on DCA05-DEC-220. Exception 1 permitting wind loads to be determined in accordance with Section 1609.6 has been deleted due to Section 1609.6 being deleted. |
|  |  | 1609.1.1 | Determination of wind loads | Change section to read as follows to correct a conflict with Florida Specific Amendments: 1609.1.1 Determination of wind loads. Wind loads on every building or structure shall be determined in accordance with Chapter 6 of ASCE 7. Wind shall be assumed to come from any horizontal direction and wind pressures shall be assumed to act normal to the surface considered Note: Clarification to ASCE 7. Arrows shown on Figure 6-10 of ASCE7 indicate that the pressure coefficients apply specifically to “Direction of MWFRS being designed.” This means that the longitudinal pressure coefficients are not applicable to trusses that span in the transverse direction and, therefore, uplift reactions for trusses that span in the transverse direction would be determined by the pressure coefficients associated with those shown for the transverse direction. Exceptions: 1. – 5. No change. 6. ANSI/TIA/EIA 222 shall be permitted for communication tower and steel antenna support structures . 7. – 9. No change. |
|  |  | 1609.1.1.1 | Applicability | Insert FP&PA Guide as it was omitted from the section at printing. The provisions of IBHS Guideline for Hurricane Resistant Residential Construction, the AF&PA Wood Frame Construction Manual for One- and Two-Family Dwellings, High Wind Areas, the FC & PA Guide to Concrete Masonry Residential Construction in High Wind Areas and the WPPC Guide to Wood Construction in High Wind Areas are applicable only to buildings located within Exposure B or C as defined in Section 1609.4. The provisions of IBHS Guideline for Hurricane Resistant Residential Construction, the AF&PA Wood Frame Construction Manual for One- and Two-Family Dwellings, High Wind Areas, the FC & PA Guide to Concrete Masonry Residential Construction in High Wind Areas and the WPPC Guide to Wood Construction in High Wind Areas shall not apply to buildings sited on the upper half of an isolated hill, ridge or escarpment meeting the following conditions: 1. – 3. No change to text. |
| 1609.1.2 | Minimum wind loads | - | - | Section deleted because requirements are covered in ASCE 7. |
|  |  | 1609.1.2 | Protection of openings. | Clarify testing of products shall be in accordance with approved standards. Glazed openings in buildings located in wind-borne debris regions shall be protected from wind-borne debris. Glazed opening protection for wind-borne debris shall meet the requirements SSTD 12, ASTM E 1886 and ASTM E 1996, ANSI/DASMA 115 (for garage doors and rolling doors) or TAS 201, 202 and 203 or AAMA 506 referenced therein. |
| 1609.1.3 | Anchorage against overturning, uplift, and sliding | 1604.9 | Counteracting structural actions | Section relocated to more appropriate General Design Requirements section. Language addressing the use of dead load as the "minimum dead load likely to be in place for the event being designed, has been deleted since it is already covered in ASCE 7. |
|  |  | 1605.3.2 | Alternate basic load combinations | Provisions regarding the use of 2/3 of the minimum dead load likely to be in place for the event being designed when dead and wind are counteracting loads, has been relocated to Section 1605.3.2. |
| 1609.1.4 | Protection of openings | 1609.1.2 | Protection of openings | Language requiring impact-resistant coverings to be tested to 1.5 times the design pressure has been relocated to Section 1609.1.2.2.1. |
|  |  | 1609.1.2.2.1 | Impact-resistant coverings |  |
| - | - | 1609.1.2.2.2 | Impact-resistant coverings, labeling | New section requiring impact-resistant coverings to be labeled in accordance with Section 1714.8. |
| 1609.2 | Definitions: Buildings and other structures, flexible | 1609.2 | Definitions: Buildings and other structures, flexible | Definition deleted. |
| 1609.2 | Definitions: Building, enclosed | 1609.2 | Definitions: Building, enclosed | Definition deleted. |
| 1609.2 | Definitions: Building, low-rise | 1609.2 | Definitions: Building, low-rise | Definition deleted. |
| 1609.2 | Definitions: Building, open | 1609.2 | Definitions: Building, open | Definition deleted. |
| 1609.2 | Definitions: Building, partially enclosed | 1609.2 | Definitions: Building, partially enclosed | Definition deleted. |
| 1609.2 | Definitions: Building, simple diaphragm | 1609.2 | Definitions: Building, simple diaphragm | Definition deleted. |
| 1609.2 | Definitions: Components and cladding | 1609.2 | Definitions: Components and cladding | Definition deleted. |
| 1609.2 | Definitions: Effective wind area | 1609.2 | Definitions: Effective wind area | Definition deleted. |
| 1609.2 | Definitions: Importance factor, Iw | 1609.2 | Definitions: Importance factor, Iw | Definition deleted. |
| 1609.2 | Definitions: Main windforce-resisting system | 1609.2 | Definitions: Main windforce-resisting system | Definition deleted. |
| 1609.2 | Definitions: Mean roof height | 1609.2 | Definitions: Mean roof height | Definition deleted. |
| 1609.3.1 | Wind speed conversion | 1609.3.1 | Wind speed conversion | Equation added that permits wind speeds to be converted from 3-second gust wind speeds to fastest-mile in accordance with Table 1609.3.1 or new equation. |
| 1609.4 | Exposure category | 1609.4 | Exposure category | New exception permits an the determination of an intermediate exposure in a transition zone when determined by a rational analysis. Definitions of exposure categories is relocated to Section 1609.4.3. |
| 1609.4.2 | Surface roughness categories. | 1609.4.2 | Surface roughness categories. | Clarify the difference between Surface Roughness and Exposure. A ground surface roughness within each 45-degree (0.79 rad) sector shall be determined for a distance upwind of the site as defined in Section 1609.4.3 from the categories defined below, for the purpose of assigning an exposure category as defined in Section 1609.4.3. Surface Roughness B. Urban and suburban areas, wooded areas or other terrain with numerous closely spaced obstructions having the size of single-family dwellings or larger. Surface Roughness C. Open terrain with scattered obstructions having heights generally less than 30 feet (9144 mm). This category includes flat open country, grasslands, and all water surfaces in hurricane-prone regions. This surface roughness shall also apply to any building located within surface roughness B-type terrain where the building is within 100 feet horizontally in any direction of open areas of surface roughness C-type terrain that extends more than 600 feet (182.9 m) and width greater than 150 ft. in the upwind direction. Short-term (less than two year) changes in the pre-existing terrain exposure, for the purposes of development, shall not be considered surface roughness C. Where development buildout will occur within three years and the resultant condition will meet the definition of surface roughness B, surface roughness B shall be regulating for the purpose of permitting. This category includes flat open country, grasslands and ocean or gulf shorelines and shall extend downwind for a distance of 1500 feet. Surface Roughness D. Reserved. |
| 1609.4.3 | Exposure categories | 1609.4.3 | Exposure categories | Exposure C has been revised to clarify the effect of open patches. Requires buildings in Exposure B-type terrain to be categorized as Exposure C where the building is within 100 feet horizontally in any direction of Exposure C-type terrain that extends more than 600 feet and width greater than 150 feet. Exposure C is required to extend downwind for a distance of 1500 feet. For buildings located within 600 feet of inland bodies of water with a fetch of 1 mile or more, roof sheathing uplift and roof-to-wall uplift loads are required to be increased by 20%. Exposure D has been revised to state "This exposure is not applicable in Florida." |
| 1609.4.3 | Exposure categories. | 1609.4.3 | Exposure categories. | Make Exposure Category C the default . An exposure category shall be determined in accordance with the following: Exposure B. Exposure B shall apply where the ground surface roughness condition, as defined by Surface Roughness B, prevails in the upwind direction for a distance of at least 2,600 feet (792 m) or 20 times the height of the building, whichever is greater. Exception: For buildings whose mean roof height is less than or equal to 30 feet (9144 mm), the upwind distance is permitted to be reduced to 1,500 feet (457 m). Exposure C. Exposure C shall apply for all cases where Exposure B does not apply. Buildings located within a distance of 600 feet of inland bodies of water that present a fetch of 1 mile (1.61 km) or more or inland waterways or rivers with a width of 1 mile (1.61 km) or more shall be classified as Exposure C and roof sheathing uplift and roof-to-wall uplift loads shall be increased by 20 percent. Exposure D. This exposure category is not applicable in Florida. |
| - | - | 1609.4.1 | Wind directions and sectors | New section requiring exposure categories to be determined for the two upwind sectors extending 45 degrees from either side of the wind direction. The exposure resulting in the highest wind loads is required to be used for that direction. |
| - | - | 1609.4.2 | Surface roughness categories | New section requiring the ground surface roughness to be determined within each 45 degree sector for the distance upwind as specified for each exposure category. Surface roughness is used to determine the exposure category for the site. Three surface roughnesses are identified: Surface Roughness B Surface Roughness C Surface Roughness D |
| 1609.5 | Importance factor | - | - | Section deleted because requirements are covered in ASCE 7. |
| 1609.6 | Simplified provisions for low-rise buildings | - | - | Simplified wind load method for low-rise buildings has been deleted because the same method is covered in ASCE 7. |
| 1609.7.1 | Roof deck | 1609.5.1 | Roof deck | Requires the roof deck to be designed for wind pressures determined from ASCE 7. |
| 1609.7.2 | Roof coverings | 1609.5.2 | Roof coverings | Section revised to include new language requiring asphalt shingles to be tested to determine the resistance of the sealant to uplift forces using ASTM D 6381. Permits asphalt shingles to be designed using UL 2390 to determine the appropriate uplift and force coefficients. |
|  |  | 1609.5.2 | Roof coverings | Clarify and coordinate asphalt shingle testing with Roofing Chapter. Roof coverings shall comply with Section 1609.5.1. Exception: Rigid tile roof coverings that are air permeable and installed over a roof deck complying with Section 1609.5.1 are permitted to be designed in accordance with Section 1609.5.3. Asphalt shingles installed over a roof deck complying with Section 1609.5.1 shall comply with the wind resistance requirements of Section 1507.2.10. |
| 1611.2 | Ponding instability | 1611.2 | Ponding instability | Section revised to refer to Section 8.4 of ASCE 7 for verification of adequate stiffness to preclude progressive deflection as result of ponding instability. |
| - | - | 1618.4.6.4 | Railing | New section requiring that when posts supporting the top rail of exterior railings are substituted with the glass, the assembly is required to be tested to TAS 201, where the impacted glass continues to support the top rail and all applicable loads after impact. |
|  |  | 1622.1 | Screen enclosures. | Delete reference to Table in ASCE-7 1622.1.1 The wind loads on screen surfaces shall be per ASCE 7 based on the ratio of solid to gross area. 1622.1.2 Design shall be based on such loads applied horizontally inward and outward to the walls with a shape factor of 1.3 and applied vertically upward and downward on the roof with a shape factor of 0.7 |
|  |  | 1622.2 1622.2.1 1622.2.2 | Windbreakers. | Add criteria for windbreakers taken from the “South Florida Building Code” 1622.2.1 Vinyl and acrylic glazed panels shall be removable. Removable panels shall be identified as removable by a decal. The identification decal shall essentially state "Removable panel SHALL be removed when wind speeds exceed 75 mph (34 m/s)." Decals shall be placed such that the decal is visible when the panel is installed. 1622.2.2 Permanent frame shall be designed per section 1620 and 1622.1.2. |
|  |  | 1626.1 | HVHZ – Impact Test for Wind-Bourn Debris | Remove solariums from paragraph h as solariums are covered in definition of sunroom. All parts or systems of a building or structure envelope such as, but not limited, to exterior walls, roof, outside doors, skylights, glazing and glass block shall meet impact test criteria or be protected with an external protection device that meets the impact test criteria. Test procedures to determine resistance to wind-borne debris of wall cladding, outside doors, skylights, glazing, glass block, shutters and any other external protection devices shall be performed in accordance with this section. Exception: The following structures or portion of structures shall not be required to meet the provisions of this section: a. Roof assemblies for screen rooms, porches, canopies, etc., attached to a building that do not breach the exterior wall or building envelope and have no enclosed sides other than screen. b. Soffits, soffit vents and ridge vents. Size and location of such vents shall be detailed by the designer and shall not compromise the integrity of the diaphragm boundary. c. Vents in a garage with four or fewer cars. Size and location of such vents shall be detailed by the designer and shall not exceed the minimum required area by more than 25 percent. d. Exterior wall or roof openings for wall or roof mounted HVAC equipment. e. Openings for roof-mounted personnel access roof hatches. f. Storage sheds that are not designed for human habitation and that have a floor area of 720 square feet (67 m2) or less are not required to comply with the mandatory windborne debris impact standards of this code. g. Louvers as long as they properly considered ASCE 7 in the design of the building. h. Buildings and structures for marinas, cabanas, swimming pools, solariums and greenhouses. |
| Chapter 17: Structural Tests and Special Inspections |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| 1702.1 | Definition: Fabricated Item | 1702.1 | Definition: Fabricated Item | Revised definition by changing "plywood" to "wood structural panel." |
|  | - |  | Definition: Garage door manufacturer | New definition added for garage door manufacturer. |
|  | - |  | Definition: Main Wind-Force Resisting System | New definition added for main wind-force resisting system. Definition is consistent with definition for MWFRS in Section 1609.2 in the 2004 FBCB. |
|  | - |  | Definition: Permanent Label | New definition added for permanent label. |
| 1703.4.1 | Research and investigation | 1703.4.1 | Research and investigation | Replaced "cost offsets" with "costs" since offsets is not universally recognized and could be misunderstood. |
| 1714.5.2.1 | Testing and labeling, exterior window and door assemblies | 1714.5.2.1 | Testing and labeling, exterior window and door assemblies | New language that limits the use of one design pressure rating per reference standard per permanent label.New language requiring exterior windows and glass doors to be labeled with a temporary supplemental label applied by the manufacturer. Specific criteria for information required on the label is provided. Permits the temporary supplemental label to be removed upon final approval by the building official.Requires the permanent label to be the default label in the event the temporary label is missing or no longer legible for final approval by the building official. |
|  |  | 1714.5.2.1 | Testing and labeling | Clarify the label maybe a permanent or supplemental label. Exterior windows and glass doors shall be tested by an approved independent testing laboratory, and shall to indicate compliance with the requirements of one of the following specifications: ANSI/AAMA/NWWDA 101/I.S. 2 or ANSI/AAMA/WDMA/101/I.S. 2/NAFS or AAMA/WDMA/CSA 101/I.S. 2/A440 or TAS202 (HVHZ shall comply with TAS202 utilizing ASTM E 1300-98 or ASTM E 1300-04 or Section 2404). Exterior windows and sliding glass doors shall be labeled with a permanent label, marking, or etching providing traceability to the manufacturer and product. The following shall also be required either on a permanent label or on a temporary supplemental label applied by the manufacturer: information identifying the manufacturer, the product model/series number, positive and negative design pressure rating, product maximum size, glazing thickness, impact-resistance rating if applicable, Florida Product Approval number or Miami-Dade Product Approval number, applicable test standard(s), and approved product certification agency, testing laboratory, evaluation entity or Miami-Dade Product Approval. The labels are limited to one design pressure rating per reference standard. The temporary supplemental label shall remain on the window or door until final approval by the building official. Exceptions: - Door assemblies installed in nonhabitable areas where the door assembly and area are designed to accept water infiltration need not be tested for water infiltration. - Door assemblies installed where the overhang (OH) ratio is equal to or more than 1 need not be tested for water infiltration. The overhang ratio shall be calculated by the following equation: OH ratio = OH Length/OH Height Where: OH length = The horizontal measure of how far an overhang over a door projects out from door surface. OH height = The vertical measure of the distance from the door sill to the bottom of the overhang over a door. - Pass-through windows for serving from a single-family kitchen, where protected by a roof overhang of 5 feet (1.5 m) or more shall be exempted from the requirements of the water infiltration test. Glass Strength: Products tested and labeled as conforming to ANSI/AAMA/NWWDA 101/I.S.2 or ANSI/AAMA/WDMA/101/I.S.2/NAFS or AAMA/WDMA/CSA 101/I.S.2/A440 or TAS 202 shall not be subject to the requirements of Sections 2403.2 or 2403.3 or 2404.1. Determination of load resistance of glass for specific loads of products not tested and certified in accordance with Section 1714.5.2.1 shall be designed to comply with ASTM E 1300 in accordance with Section 2404. The temporary supplemental label shall designate the type and thickness of glass or glazing material. |
| 1714.5.2.1.1 | Testing and labeling of skylights | 1714.5.2.1.1 | Testing and labeling of skylights | Requires skylights to be labeled with a permanent label. Adds the products model/series number as information to be included on the label. New language that limits the use of one design pressure rating per reference standard per permanent label. New language requiring exterior skylights to be labeled with a temporary supplemental label applied by the manufacturer. Specific criteria for information required on the label is provided. Permits the temporary supplemental label to be removed upon final approval by the building official. Requires the permanent label to be the default label in the event the temporary label is missing or no longer legible for final approval by the building official. |
| 1714.5.2.1.1 | Testing and labeling of skylights. | 1714.5.2.1.1 | Testing and labeling of skylights. | Makes the labeling requirement the same for skylights as windows and glass doors. Exterior skylights shall be tested by an approved independent testing laboratory, and shall be labeled to indicate compliance with the requirements of one of the following specifications: ANSI/AAMA/WDMA 101/I.S.2/NAFS or AAMA/WDMA/CSA 101/I.S.2/A440, or TAS 202 (HVHZ shall comply with TAS 202). Exterior skylights shall be labeled with a permanent label, marking, or etching providing traceability to the manufacturer and product. The following shall also be required either on a permanent label or on a temporary supplemental label applied by the manufacturer: information identifying the manufacturer, the product model/series number, positive and negative design pressure rating, product maximum size, type and thickness of glass or glazing material, impact-resistance rating if applicable, Florida Product Approval number or Miami-Dade Product Approval number, applicable test standard(s), and approved product certification agency, testing laboratory, evaluation entity or Miami-Dade Product Approval. Labels are limited to one design pressure rating per reference standard. The temporary supplemental label shall remain on the skylight until final approval by the building official. |
| 1714.5.2.2 | Supplemental label | 1714.5.2.2 | Supplemental label | Adds 101/I.S. 2/NAFS or AAMA/WDMA/CSA 101/I.S.2/A440 reference standard applicable to the use of a temporary supplemental label conforming to AAMA 203. Permits the use of comparative analysis for operable windows and glazed doors and fixed windows with specific criteria provided for performing the analysis. |
| 1714.5.2.2 | Supplemental label | 1714.5.2.2 | Comparative Analysis Label | Clarify the Comparative Analysis Label is not the Supplemental required in 1714.5.2.1. A temporary supplemental label conforming to AAMA 203, Procedural Guide for the Window Inspection and Notification System, shall be acceptable for establishing to communicating the calculated allowable design pressures higher than indicated on the label required by Section R613.3.1 for window or door sizes smaller than that required by the ANSI/AAMA/NWWDA 101/I.S.2 or ANSI/AAMA/WDMA 101/I.S.2/NAFS or AAMA/WDMA/CSA 101/I.S.2/A440 test requirements. This temporary supplemental label shall be applied by the manufacturer and remain on the window or door until final approval by the building official. |
| 1714.5.3 | Exterior door assemblies. | 1714.5.3 | Exterior door assemblies. | Correct reference Exterior door assemblies not covered by Section 1714.5.2 or Section 1714.5.3.1 shall be tested for structural integrity in accordance with ASTM E 330 Procedure A, at a load of 1.5 times the required design pressure load. The load shall be sustained for 10 seconds with no permanent deformation of any main frame or panel member in excess of 0.4 percent of its span after the load is removed. High-velocity hurricane zones shall comply with TAS 202. After each specified loading, there shall be no glass breakage, permanent damage to fasteners, hardware parts, or any other damage which causes the door to be inoperable. The minimum test sizes and minimum design pressures shall be as indicated in Table 1714.5.3. The unit size tested shall qualify all units smaller in width and/or height of the same operation type and be limited to cases where frame, panels and structural members maintain the same profile as tested. |
| - | - | 1714.5.3.4 | Garage door labeling | New section requiring garage doors to be labeled with an approved permanent label provided by the manufacturer.Specific criteria for information required on the label is provided.Requires installation instructions to be provided and available on the job site. |
| 1714.5.5.1 | Mullions | 1714.5.5.1 | Mullions | Provisions in Section 1714.5.1.1, 1714.5.1.2, and 1714.5.1.3 have been relocated to Section 1714.5.5.1. Permits mullions to be tested in accordance with ASTM E 330 or TAS 202 (HVHZ is required to comply with TAS 202) in addition to AAMA 450. |
|  |  | 1714.5.5.1.1 | Engineered mullions |  |
|  |  | 1714.5.5.1.2 | Mullions tested as stand-alone lone units |  |
|  |  | 1714.5.5.1.3 | Mullions tested as assembly |  |
| 1714.5.5.4 | Structural safety factor, mullions | 1714.5.5.4 | Structural safety factor, mullions | Section revised to only apply to mullions that are tested by an approved testing laboratory. Requires mullions to be capable of resisting 1.5 times the design pressure sustained for 10 seconds with the permanent deformation not exceeding 0.2 percent of the mullion span for assemblies requiring deflection limitations, and 0.4 percent of the mullion span for all other assemblies. Additional performance criteria provided. |
| - | - | 1714.8 | Impact-resistant coverings, labeling | New section requiring impact-resistant coverings to be provided with a permanent label supplied by the manufacturer. Criteria for location of label and information required on the label is specified. Specific installation criteria is also provided. |
| 1715.1.1 | Test standard for joist hangers | 1715.1.1 | Test standard for joist hangers | Last sentence is revised to more appropriately refer to "headers" instead of "hangers" where specific gravities are discussed. New exception states that the joist length for the testing is not required to exceed 24 inches so that during the test, the joist doesn't fail before hanger. |
| 1715.1.2 | Vertical load capacity of joist hangers | 1715.1.2 | Vertical load capacity of joist hangers | Added "minimum" to the required number of tests because additional tests may be desirable.Items 1 and 2 were revised to clarify that the load for a single hanger is required to be used.In Item 2, the average ultimate load is revised to be divided by 3 instead of 6.Items 3, 4, and 5 were revised for clarity. |
| 1715.1.3 | Torsional moment capacity for joist hangers | 1715.1.3 | Torsional moment capacity for joist hangers | Section revised to remove "for normal duration of loading" for allowable torsional moment because the torsional moment capacity is not permitted to be increased for duration of load. |
| 1715.1.4 | Design value modifications for joist hangers | 1715.1.4 | Design value modifications for joist hangers | Deleted incorrect reference to Section 2305.1. |
| Chapter 18: Soils and Foundations |  |  |  |  |
| Section | Requirement | Section | Requirement |  |
| 1802.2.1 | Questionable soil | 1802.2.1 | Questionable soil | Revised language to change "safe-sustaining power" to "strength characteristics" regarding the soil condition. |
| 1803.3 | Site grading | 1803.3 | Site grading | Revised section to add alternative for situations where there may be obstructions or when a full 10-feet of distance isn't obtainable, and in this case, a 5% slope shall be provided. Also added that swales used for diversion shall be sloped at min of 2% away from the building when located within 10 feet of foundation. |
| 1804.2 | Presumptive load-bearing values | 1804.2 | Presumptive load-bearing values | Revised language to remove "at or" regarding soil surface. Current language implies that the values in Table 1804.2 may be applied at ground surface. |
| 1805.2.1 | Frost protection | 1805.2.1 | Frost protection | Revised Exception 2 to apply to areas of 600 square feet or less for light-frame construction to and 400 square feet or less for other than light-frame construction. |
| 1805.4.1.1 | Design loads | 1805.4.1.1 | Design loads | Revised language from "shall include" to "is permitted" regarding dead load allowances. |
| 1805.4.5 | Timber footings | 1805.4.5 | Timber footings | Revised section's reference to AWPA C22 to "U1 (Commodity Specification A, Use Category 4B)" - the AWPA new use category system. Also added term "treated" to pile support requirement. |
| 1805.4.6 | Wood foundations | 1805.4.6 | Wood foundations |  |
| 1805.5 | Foundation walls | 1805.5 | Foundation walls | Revised section to add reference to new table 1805.5(5). |
| Table 1805.5(1) | Plain masonry and plain concrete foundation walls | Table 1805.5(1) | Plain masonry and plain concrete foundation walls | Revised for editorial change - replaced column heading "Height of Unbalanced Backfill" with "Unbalanced Backfill Height" to align heading to the definition/meaning provided in this chapter. |
| Table 1805.5(2) | 6-inch concrete and masonry foundation walls with reinforcing | Table 1805.5(2) | 6-inch concrete and masonry foundation walls with reinforcement | Revised for editorial change - replaced column heading "Height of Unbalanced Backfill" with "Unbalanced Backfill Height" to align heading to the definition/meaning provided in this chapter. Also revised title of Table to replace term "reinforcing" with "reinforcement." Wall heights have been modified so that they are on an even module of 8 inches. Reinforcement size and spacings have been updated to reflection changes in ACI 530/ASCE 5/TMS 402. A 10 foot wall height was added as this is becoming common in construction practice. Concrete foundations walls have been removed and provided in Table 1805.5(5). |
| Table 1805.5(3) | 10-inch concrete and masonry foundation walls with reinforcing | Table 1805.5(3) | 10-inch concrete and masonry foundation walls with reinforcement |  |
| Table 1805.5(4) | 12-inch concrete and masonry foundation walls with reinforcing | Table 1805.5(4) | 12-inch concrete and masonry foundation walls with reinforcement |  |
| - | - | Table 1805.5(5) | Concrete foundation walls | Added Table for concrete foundation walls, which allows for a separate table application for both masonry and concrete. With concrete separated into separate table, the appropriate material design standards (ACI) can be used. |
| 1805.5.1.1 | Thickness at foundation walls | 1805.5.1.1 | Thickness at foundation walls | Revised title from "thickness based on wall" to "thickness at foundation walls" for clarity of section intent. Revised section to require a that the top corbel on an 8" wall not extend past the bottom of the floor framing. For structural integrity, the corbel shall be tied to the veneer and the void filled with grout. |
| 1805.5.1.2 | Thickness based on soil loads, unbalanced backfill height and wall height | 1805.5.1.2 | Thickness based on soil loads, unbalanced backfill height and wall height | Majority of revisions to these sections intended to separate the foundation requirements for concrete foundation walls from masonry foundation walls. New Table 1805.5(5) provides prescriptive designs for concrete foundation walls. |
| 1805.5.2 | Foundation wall material | 1805.5.2 | Foundation wall material |  |
| - | - | 1805.5.2.1 | Concrete foundation walls |  |
| - | - | 1805.5.2.2 | Masonry foundation walls |  |
| 1805.5.3 | Alternative Foundation wall reinforcement | 1805.5.3 | Alternative Foundation wall reinforcement |  |
| 1805.7.1 | Lateral bearing limitations | 1805.7.1 | Lateral bearing limitations | Revised section's reference from AWPA C22 to "AWPA U1 (Commodity Specification A, Use Category 4B)" - the AWPA new use category system. |
| 1805.8.2 | Slab on grade foundations | 1805.8.2 | Slab on grade foundations | Revised section to provide consistent requirements for shallow ground-supported foundations on expansive soils. |
| 1807.1.1 | Story above grade | 1807.1.1 | Story above grade plane | Revised section title and section language from "grade" to "grade plane." |
| 1807.3.1 | Waterproofing and dampproofing of floors | 1807.3.1 | Waterproofing and dampproofing of floors | Revised section to add fully adhered/fully bonded HPDE or polyolefin composite membrane as an option for waterproofing floors. |
| 1808.1 | Pier and pile foundations - definition for micropiles | 1808.1 | Pier and pile foundations - definition for micropiles | Added definition for micropiles to allow for requirements to be added to code that not previously provided. |
|  |  |  |  | Added definition for timber piles. |
| 1808.2.6 | Piles and piers structural integrity | 1808.2.6 | Piles and piers structural integrity | Editorial change to eliminate duplication of words. |
| 1808.2.8.3 | Load tests | 1808.2.8.3 | Load tests | Editorial change to add "axial" to reference to load capacity. Also added "driven with the same hammer" to reference of equal supporting capacity. |
| 1808.2.8.3.1 | Load test evaluation | 1808.2.8.3.1 | Load test evaluation | Revised section to replace number 3 "Chin-Konder Extrapolation" with Butler-Hoy Criterion" to discourage extrapolation methods which can overestimate the safe ultimate bearing capacity; however, these methods may be still be allowed through number 4's "other methods" if needed. |
| 1808.2.8.4 | Allowable frictional resistance | 1808.2.8.4 | Allowable frictional resistance | Revised section to include reference to Section 1808.2.8.3, which allows the use of an exception when verified by actual load test. |
| 1808.2.11 | Piles in subsiding areas | 1808.2.11 | Piles in subsiding areas | Revised language from "driven" to "installed" since section applies to all piles. |
| 1809.1.2 | Preservative treatment | 1809.1.2 | Preservative treatment | Revised section's reference to AWPA C22 to "U1 (Commodity Specification A, Use Category 4B)" - the AWPA new use category system. |
| 1809.1.3 | Defective piles | 1809.1.3 | Defective piles | Revised title of section from "End supported" to "Defective piles" to clarify that the piles do not have to be end supported to be defective. Also revised section to include clarification in terms and replace "driving resistance" with "rate of penetration" so that language is more consistent with 1808.2.8.2. |
| - | - | 1809.1.4 | Allowable stresses | Added new section to stress to the designer where the design stresses for timber piles are located. |
| 1809.2.3.3 | Allowable stresses | 1809.2.3.3 | Allowable stresses | Removed the term "maximum" from section. |
| 1809.3.1 | Structural steel pile materials | 1809.3.1 | Structural steel pile materials | Revised section to add references ASTM A 690 and ASTM A 992. |
| 1809.3.4 | Dimensions of steel pipe piles | 1809.3.4 | Dimensions of steel pipe piles | Revised section to add to the rule of thumb of "referenced pile hammer energy" to also include the wave equation as an alternate determination for adequacy of steel pipe piles. Also changed pipe wall thickness from "0.188" to "0.179", which is a thickness of a common pipe size. |
| 1810.3.1 | Allowable stresses for drilled or augured uncased piles | 1810.3.1 | Allowable stresses for drilled or augured uncased piles | Revised language to require that both augured cast-in-place piles be the same as the design value for drilled uncased piles. Also, revised allowable compressive strength for both from "34" to "40" percent of the yield strength of steel. |
| 1810.3.3 | Installation | 1810.3.3 | Installation | Revised section to eliminate "in increments of about 12 inches each" to avoid confusion of possible starting and stopping during withdrawal as opposed to the intent of measurements taken every 12 inches during withdrawal. |
| 1810.3.4 | Reinforcement | 1810.3.4 | Reinforcement | Revised section to state "stem" rather than "ducts" to provide a clearer interpretation as well as to utilize the industry practice. |
| 1810.6.5 | Placing concrete | 1810.6.5 | Placing concrete | Revised section to add statement to allow concrete to be chuted directly into pipe (w/out a hopper), and thus recognizing an accepted industry practice. |
| - | - | 1810.8 | Micropiles | Added section and definition for micropiles. |
| - | - | 1810.8.1 | Construction | Added new requirements to address the installation and construction of micropiles. Micropiles are defined as bored- or grouted-in-place piles no more than 12 inches in diameter and incorporating steel pipe casing and/or steel reinforcement. |
| - | - | 1810.8.2 | Materials |  |
| - | - | 1810.8.3 | Allowable stresses |  |
| - | - | 1810.8.4 | Reinforcement |  |
| - | - | 1810.8.5 | Micropile installations |  |
| 1816.1.8 | Termiticide after changes in framing | 1816.1.8 | Termiticide after changes in framing | Section modified to require changes in framing or additions to framing in areas of the structure requiring treatment that occur after the initial wood treatment must be treated prior to final building approval. |
|  |  | 1816.2 | Penetration. | Combine requirements from 1816.2.1 & 1816.2.2 to make code consistent. Protective sleeves around piping penetrating concrete slab-on-grade floors shall not be of cellulose-containing materials. If soil treatment is used for subterranean termite protection, the sleeve shall have a maximum wall thickness of 0.010 inch, and be sealed within the slab using a non-corrosive clamping device to eliminate the annular space between the pipe and the sleeve. No termiticides shall be applied inside the sleeve. |
| 1816.2.1 | Penetration | 1816.2.1 | Penetration | Added section 1816.2.2 and moved scope from 1816.2 to new section. |
|  |  | 1816.2.1 | Penetration. | Delete section as requirements have been combined in 1816.2. |
| 1816.2.2 | Protective sleeves, requirements | 1816.2.2 | Protective sleeves, requirements | Specific requirements for sleeves have been added which include: 1. The sleeve shall have a nominal thickness of 0.025 inch. 2. The sleeve shall be sized for the pipe. 3. The sleeve shall be sealed within the slab using a noncorrosive mechanical clamping device to eliminate the annular space between the pipe and pipe sleeve. |
|  |  | 1816.2.2 | Penetration. | Delete section as requirements have been combined in 1816.2. |
| Chapter 19: Concrete |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| 1901 through 1908 | Concrete | 1901 through 1908 | Concrete | The majority of the technical provisions contained in Chapter 19 regarding concrete have been deleted and replaced with the applicable references to ACI 318. |
| 1909.1 | Scope for structural plain concrete | 1909.1 | Scope for structural plain concrete | Revised section to add "as modified in Section 1908" to reference document changes to ACI 318. |
| 1909.2 | Limitations of structural plain concrete | 1909.2 | Limitations of structural plain concrete | Revised section to modify reference for additional information on use of structural plain concrete from "1910" to "1908.1.15." |
| 1909.4 | Design of structural plain concrete | 1909.4 | Design of structural plain concrete | Revised section exception to remove reference to Section 101.2, which previously implied that buildings subject to the IRC are not entitled to use the exception. Removal of reference provides clarification of the applicability to any Group R-3 occupancy. |
| 1913.1 | Anchorage to concrete strength design | 1912.1 | Anchorage to concrete strength design | Revised compliance of design to add "ACI 318 as modified by Section 1908.1.16, provided they are within the scope of Appendix D." |
| 1917 | Lightweight Insulation Concrete Fill | 1917 | Lightweight Insulating Concrete Roof Deck | Revised section title. |
| 1917.1 | Lightweight Insulation Concrete Fill | 1917.1 | Lightweight Insulation Concrete | Revised section title to remove the term "fill." |
| 1917.1.1 | Aggregate lightweight insulating concrete | 1917.1.1 | Aggregate lightweight insulating concrete | Editorial changes for clarification and removed the term "fill" and the reference "C 796." |
| 1917.1.2 | Cellular lightweight insulating concrete | 1917.1.2 | Cellular lightweight insulating concrete | Revised section to remove the term "fill" and add "preformed" to clarify the type of foam. |
| 1917.1.3 | Cellular/aggregate lightweight insulating concrete | 1917.1.3 | Cellular/aggregate lightweight insulating concrete | Revised section to remove the term "fill" and add "preformed" to clarify the type of foam. Editorial change to revise term "import" to "impart" and replace the term "fill" with "concrete." |
| 1917.1.4 | Walkability | 1917.1.4 | Walkability | Editorial changes to remove the term "fill" and add "foot" to "foot traffic." |
| 1917.2.1 | Inspection | 1917.2.1 | Inspection | Revised description of requirement for control approval from "lightweight insulation concrete fill systems" to "lightweight insulating concrete systems." |
| 1917.2.4 | Foot traffic | 1917.2.4 | Foot traffic | Revised language to remove "24 hours after placement" and replace with "once the roof deck system can support foot traffic" in regard to when building official shall inspect. |
| 1917.3 | Testing | 1917.3 | Testing | Editorial changes to remove the term "fill." |
| 1917.3.1 | Roof assemblies testing | 1917.3.1 | Roof assemblies testing |  |
| 1917.4 | Materials and limitations | 1917.4 | Materials and limitations |  |
| 1917.4.1 | Materials and limitations | 1917.4.1 | Materials and limitations |  |
| 1917.4.2 | Material thickness | 1917.4.2 | Material thickness | Editorial changes to remove the term "fill" and to specify the thickness receive the "specified" (not specific) base ply fastener "length." |
| 1917.4.3 | Minimum compressive strength | - | - | Section information was removed and section is "reserved." |
| 1917.4.10 | Insulating concrete fastener withdrawal | 1917.4.10 | Insulating concrete fastener withdrawal | Editorial change to remove the term "fill." |
| 1917.4.11 | Expansion joints | 1917.4.11 | Expansion joints | Editorial change to remove the term "fill." Also removed the term "contraction" in regards to expansion joints. |
| 1917.4.12 | Material and limitations - insulation board | 1917.4.12 | Material and limitations - insulation board | Revised section, added item number 1 to add reference information for insulation board delivered to the job site to comply will labeling and identification. |
|  |  |  |  | Renumbered item 1 to Item 2 and revised section to require installation to comply with manufacturer's Product Control Approval, as opposed to providing specific continuous pour information. |
| 1917.4.13 | Reinforcing mesh | 1917.4.13 | Reinforcing mesh | Editorial change to clarify that mesh will be provided "as required" not "when necessary" and removed item number 1 regarding fibers. |
| 1926.5.5 | Exterior Balcony slabs | 1926.5.5 | Exterior Balcony slabs | Revised section to remove specific requirements and items 1 through 5 and add "shall be designed and constructed in accordance with the provisions of ACI 318." |
| Chapter 20: Aluminum |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| 2001.1 | Scope | 2001.1 | Scope | "Light metal alloys" changed to "Aluminum." |
| 2002.2.1 | Definitions | 2002.2.1 | Definitions | Definition of Primary Members revised to include "eave rail, purlins, and roof brace." Definition of Secondary Members revised to include "wall brace." |
|  |  | 2002.4 | Loads. | Replace “either” with “both” to eliminate confusion in calculation. Structural members supporting screened enclosures shall be designed for wind in both of two orthogonal directions using the pressures given in Table 2002.4. Each primary member shall also be designed for a 300 pound (1.33 kN) load applied vertically downward along any 1 foot (305 Mm) of any member, not occurring simultaneously with wind load. |
| Table 2002.4 | Design wind pressures for aluminum screen enclosures | Table 2002.4 | Design wind pressures for aluminum screen enclosures | Note 2 edtiorially revised to remove "or less" clarifying that the pressures in the table apply to enclosures with a mean enclosure height of 30 feet. Factors in Table 2002.4 are to be used for other heights. |
|  |  | Table 2002.4 | Footnote h. | Correct value in table to reflect the most commonly used mesh material in Florida. h. Table pressures apply to 20 x 20 x 0.013" mesh screen. For 18 X 14 X 0.013" mesh screen, pressures on screen surfaces may be multiplied by 0.88. For screen densities greater than 20X20X0.013", use pressures for enclosed buildings. |
| 2002.6 | Sunrooms | 2002.6 | Sunrooms | Section revised to provide sunroom categories from AAMA/NPEA/NSA 2100. |
| 2003.2 HVHZ | Standards | 2003.2 HVHZ | Standards | Section revised to require the design, fabrication, and erection of structural aluminum to conform to the Aluminum Design Manual |
| 2003.4 HVHZ | Definitions | 2003.4 HVHZ | Definitions | Section revised by deleting previous definitions and refer to Section 2002.2.1 for definitions pertinent to structural aluminum. |
| Chapter 21: Masonry |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| 2101.2 | Design methods | 2101.2 | Design methods | Changed "working" stress to "allowable" stress. |
| 2101.2.1 | Working stress design | 2101.2.1 | Allowable stress design |  |
| 2101.2.2 | Strength design | 2101.2.2 | Strength design | New language added requiring AAC masonry to comply with Chapter 1 and Appendix A of ACI 530/ASCE 5/TMS 402. |
| 2101.2.5 | Glass unit masonry | 2101.2.5 | Glass unit masonry | Revised section to add "unit" to "glass unit" and also revised language to remove wordiness. |
| 2101.2.6 | Masonry veneer | 2101.2.6 | Masonry veneer | Added additional reference to Chapter 6 of ACI 530/ASCE 5/TMS 402. |
| - | - | 2101.2.7 | Prescriptive methods | New section added that permits compliance with the applicable prescriptive standards referenced in Section 1609.1.1. |
| 2102.1 | Masonry Definitions | 2102.1 | New definitions | Additional definitions have been added to this section to reflect the revisions to ACI 530/ASCE 5/TMS 402. |
| - | - |  | Foundation pier |  |
| - | - |  | Glass masonry unit |  |
| - | - |  | New definitions - Masonry |  |
| - | - |  | Ashlar masonry |  |
| - | - |  | Coursed ashlar |  |
| - | - |  | Glass unit masonry |  |
| - | - |  | Plain masonry |  |
| - | - |  | Random ashlar |  |
| - | - |  | Reinforced masonry |  |
| - | - |  | Solid masonry |  |
| - | - |  | Unreinforced (plain) masonry |  |
| 2103.2 | Clay or shale masonry units | 2103.2 | Clay or shale masonry units | Revised section to add ASTM C 1405 reference for glazed brick. |
| - | - | 2103.3 | AAC masonry | New section requiring AAC masonry units to conform to ASTM C 1386. |
| 2103.9.2 | Electrically conductive dry-set mortars | - | - | Removed section and renumbered subsequent sections - product is no longer manufactured. |
| - | - | 2103.11 | Mortar for ACC masonry | Added section. Autoclaved aerated concrete (AAC) is being utilized more extensively in the industry and added section(s) provides compliance information and references. |
| - | - | 2103.11.1 | Thin-bed mortar for ACC masonry |  |
| - | - | 2103.11.2 | Mortar for leveling courses of ACC masonry |  |
| 2103.11.4 | Wire fabric | 2103.11.4 | Wire fabric | Reference standard for welded deformed steel wire fabric has been updated to ASTM A 497. |
| 2103.11.5 | Anchors ties and accessories | 2103.13.5 | Anchors ties and accessories | Removed reference to ASTM A 167, Type 304 and added more detailed and specific references for chromium, chromium-nickel stainless steel, anchor bolts and flat rolled stainless for clarify of requirements for each. |
| 2103.11.6 | Prestressed tendons | 2103.13.6 | Prestressed tendons | Revised section exception number 2 to remove reference to ASTM A 616. |
| 2103.11.7 | Corrosion protection | 2103.13.7 | Corrosion protection | Revised section to separate prestressing tendons and the anchors, couplers, and end blocks and provide separate reference requirements for each. |
| 2103.11.7.1 | Hot dipped galvanized | 2103.13.7.2 | Hot dipped galvanized | Mostly editorial revisions for consistency with ACI 530/ASCE 5/TMS 402.. |
| 2103.11.7.2 | Epoxy coatings | 2103.13.7.3 | Epoxy coatings | Mostly editorial revisions for consistency with ACI 530/ASCE 5/TMS 402.. |
| 2103.11.7.3 | Mill galvanized | 2103.13.7.1 | Mill galvanized | Mostly editorial revisions for consistency with ACI 530/ASCE 5/TMS 402.. |
| 2104.1.2 | Placing mortar and units | 2104.1.2 | Placing mortar and units | Section revised to include specific references for placing clay and concrete masonry units. |
| - | - | 2104.1.2.6 | Thin-bed mortar and AAC masonry units | Added section to provide intent and clear application of the test standards for thin-bed mortar used in ACC masonry applications. |
| - | - | 2104.1.2.7 | Grouted masonry | Added section to provide application requirements for grout to prevent cold joints. |
| 2104.2 | Corbelled masonry | 2104.2 | Corbelled masonry | More specific requirements for corbelled masonry have been provided for consistency with ACI 530/ASCE 5/TMS 402. |
| 2104.3.2.2 | Temperature and construction requirements | 2104.3.2.2 | Temperature and construction requirements | Added item number 3 to this section to include minimum temperature requirements for installation of thin-bed mortar. |
| - | - | 2104.3.3.2 | AAC masonry | Added section to provide temperature requirements for ACC masonry applications. Also renumbered subsequent sections. |
| 2104.4.2.1 | Temperature and mortar | 2104.4.2.1 | Temperature and mortar | Revised section to add requirements for AAC masonry by the addition of items 5 (mortar spread no more than 4' ahead) and item number 6 (units placed w/in 1 minute of thin-bed mortar placement). |
| 2105.2.1 | Compressive strength compliance | 2105.2.1 | Compressive strength compliance | Added compliance requirements for compressive strength of AAC masonry. |
| 2105.2.2.1.1 | Clay masonry | 2105.2.2.1.1 | Clay masonry | Editorial change to add "or exceeds" to minimum compressive strength requirement. |
| 2105.2.2.1.2 | Concrete masonry | 2105.2.2.1.2 | Concrete masonry |  |
| - | - | 2105.2.2.1.3 | AAC masonry | Added new section and reference for requirements of AAC masonry. |
| 2105.2.2.2.1 | Prism test method | 2105.2.2.2.1 | Prism test method | Revised section to add "clay and concrete" to the description of masonry. |
| 2107.1 | General, working stress design | 2107.1 | General, allowable stress design | Permits lap splices to be in accordance with ACI 530/ASCE 5/TMS 402 or Section 2107.3 or 2107.5 as specified by the architect or engineer. Permits development of bars in tension to be in accordance with ACI 530/ASCE 5/TMS 402 or Section 2107.4 as specified by the architect or engineer. |
| 2107.2.2 | Masonry columns | 2107.2 | Masonry columns | Relocated section and provided statement to add ACI 2.1.6.6 light frame construction. Requirements remain the same, change is editorial regarding the reference to ACI addition. |
| 2107.2.3 | Lap splices | 2107.3 | Lap splices | Relocated section. Requirements remain the same, change is editorial regarding the reference to ACI addition. |
| 2107.2.4 | Maximum bar size | - | - | Deleted section. |
| 2107.2.5 | Splices for large bars | - | - | Deleted section. |
| 2107.2.6 | Maximum reinforcement percentage | - | - | Deleted section. |
| - | - | 2107.4 | Development of bars in tension | Added new requirements for development of bars in tension. |
| - | - | 2107.5 | Splices of reinforcement | Added section providing additional requirements for splicing. |
| 2108.1 | Scope for strength design of masonry | 2108.1 | Scope for strength design of masonry | Revised section referenced to remove reference to 2106 and to add reference to modifications in section 2108.2 through 2108.3. |
|  |  |  |  | Revised exceptions to move exception 1 information to number 2 and add new number 1 for AAC masonry exception. |
| 2108.2 | Masonry stress | 2108.2 | Development | Deleted section from the 2004 Code and replaced with modification of ACI 530/ASCE 5/TMS 402 for development. |
| 2108.3 | Splices | - | - | Section deleted. |
| 2108.4 | Tensile reinforcement | 2108.3 | Tensile reinforcement | Revisions for consistency with ACI 530/ASCE 5/TMS 402. |
| 2110.2.1 | Standard units | 2110.2.1 | Standard units | Editorial change to add that thickness of units shall be "at least" 3 7/8 inches. |
| 2110.4.1 | Isolation | 2110.4.1 | General requirements for glass unit masonry panels | Revised section title to better reflect intent. |
| - | - | 2110.4.2.1 | Support on wood construction | New section permitting glass unit masonry with an installed weight of 40 psf or less and maximum height of 12 feet to be supported on wood consruction. Revisions for consistency with ACI 530/ASCE 5/TMS 402. |
| - | - | 2110.4.2.2 | Expansion joint | New section requiring an expansion joint for glass masonry supported on wood construction. Revisions for consistency with ACI 530/ASCE 5/TMS 402. |
| 2111.1 | Scope for masonry fireplaces | 2111.1 | Scope for masonry fireplaces | Revised section to remove reference to Table and Figure in this section. Figure and Table were outdated and not necessary and therefore removed. |
| Figure 2111.1 | Fireplace and Chimney Details | - | - |  |
| Table 2111.1 | Summary of Requirements for Masonry Fireplaces and Chimneys | - | - |  |
| 2111.11 | Fireplace clearance | 2111.11 | Fireplace clearance | Revised exception number 4 to allow for flexibility for combustible materials along sides of fireplaces in recognition that radiant heat is a greater problem for materials above the opening. |
| 2111.12 | Mantel and trim | - | - | Deleted section due to redundancy within the code. |
| 2112 | Masonry heaters | 2112 | Masonry heaters | Section entirely rewritten for consistency with the requirements in the FBCR and standards referenced in new language. |
| - | - | 2113.10.1 | Masonry veneer chimneys | Added section to provide requirements for masonry veneer over wood or metal frame chimneys, also subject to same requirements as other veneer applications. |
| 2113.12 | Flue lining installation | 2113.12 | Clay flue lining installation | Revised title and language in section from "flue" lining to "clay flue" lining. |
| Table 2113.16(2) | Net cross-sectional area of square and rectangular flue sizes | Table 2113.16(2) | Net cross-sectional area of square and rectangular flue sizes | Revised table to express flue liners by their nominal exterior dimensions as commonly used In addition, the 8 x 16 size was eliminated since it's no longer manufactured. |
| 2115.1 | Gable end walls | 2115.1 | Gable end walls | Added scope information: Gable endwalls shall be structurally continuous between points of lateral support. |
| 2120.3 | Unreinforced masonry | 2120.3 | Unreinforced masonry | Revised section to add term "axial" regarding the type of tension. New language added permitting fluxural tension in un-reinforced masonry per ACI 530. |
| Chapter 22: Steel |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| 2202 | Definitions | 2202 | Definitions | Definition for "Adjusted Shear Resistance, Type I Shear Wall, Type II Shear Wall, Type II Shear Wall Segment, and Unadjusted Shear Resistance" deleted with deference to the AISI-Lateral standard. Figure 2202.1 and all Nomenclature deleted as well. |
| 2203.2 | Protection | 2203.2 | Protection | Reference standard for painting of structural steel has been updated to AISC 360. |
| 2205.1 | General, structural steel | 2205.1 | General, structural steel | Reference standard for design, fabrication and erection of structural steel has been updated to AISC 360. |
| 2206.1 | General, steel joists | 2206.1 | General, steel joists | Reference standards for design, manufacture and use of open web steel joists and joist girders has been updated to SJI K-1.1, SJI LH/DLH-1.1, and SJI JG-1.1. |
| - | - | 2206.2 | Design, steel joists | New provisions providing criteria for design, calculations, drawings, and certification of steel joists and joist girders. |
| - | - | 2206.3 | Calculations, steel joists |  |
| - | - | 2206.4 | Steel joist drawings |  |
| - | - | 2206.5 | Certification, steel joists |  |
| 2209.1 | General, cold-formed steel | 2209.1 | General, cold-formed steel | Reference standard for design of cold-formed carbon and low-alloy steel structural members has been updated to AISI-NAS. |
| 2210.1 | General, cold-formed steel light-framed construction | 2210.1 | General, cold-formed steel light-framed construction | Reference standard for design, installation and construction of cold-formed carbon or low-alloy steel, structural and nonstructural steel framing has been updated to AISI-NAS. |
| 2210.2 | Headers, cold-formed steel light-framed construction | 2210.2 | Headers, cold-formed steel light-framed construction | Section revised to include single L-headers. Reference standard for design and installation of headers has been updated to AISI-Header. |
| 2210.3 | Trusses, cold-formed steel light-framed construction | 2210.3 | Trusses, cold-formed steel light-framed construction | Reference standard for design, quality assurance, installation and testing of cold-formed steel trusses has been updated to AISI-Truss. |
| - | - | 2210.4 | Wall stud design, cold-formed steel light-framed construction | New section requiring the design and installation of cold-formed steel studs for structural and non-structural walls to be in accordance with AISI-WSD. |
| - | - | 2210.5 | Lateral design, cold-formed steel light-framed construction | New section requiring the design of light-framed cold-formed steel walls and diaphragms to resist wind loads to be in accordance with AISI-Lateral. |
| - | - | 2210.6 | Prescriptive framing, cold-formed steel light-framed construction | New section permitting the use of AISI-PM for detached one- and two-family dwellings and townhouses up to two stories in height. |
| 2211 | Cold-formed steel light-framed shear walls | - | - | Section deleted in deference to AISI-Lateral. |
| 2222.4.7 HVHZ | Allowable stress increase | - | - | Section prohibiting metal building siding and roof decking from being designed with a 1/3 allowable stress increase for wind has been deleted because this limitation is covered elswhere in the code. |
| Chapter 23: Wood |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| 2301.2 | General design requirements | 2301.2 | General design requirements | Revised language from "shall be based on" to "shall be in accordance." Editorial change to remove sections 2302.1, 2302.2 and 2302.3 but relocate information to items numbers in this section to provide clarification of specific methods. |
| 2302.1 | Definitions - Adjusted shear resistance | - | - | Defintion deleted and specifics related to the its use have been relocated within the code sections pertaining to the perforated shear wall method. |
| - | - | 2302.1 | Definitions - Prefabricated wood I-joist | Added definition to align with corresponding AF&PA terms. |
| 2302.1 | Definitions - Shear wall | 2302.1 | Definitions - Shear wall | Revised shear wall definition perforated shearwall and perforated shear wall segment as subdefintitions for correlation with changes to the perforated shear wall method. |
| - | - | 2302.1 | Definitions - Structural composite lumber | Added definition to align with corresponding AF&PA terms. |
| 2302.1 | Definitions - Structural glued-laminated timber | 2302.1 | Definitions - Structural glued-laminated timber | Revised definition to align with corresponding AF&PA terms. |
| 2302.1 | Definitions - Oriented stand board (OSB) | 2302.1 | Definitions - Oriented stand board (OSB) |  |
| 2302.1 | Definitions - Plywood | 2302.1 | Definitions - Plywood |  |
| 2302.1 | Definitions - Unadjusted shear resistance | - | - | Defintion deleted and specifics related to the its use have been relocated within the code sections pertaining to the perforated shear wall method. |
| 2303.1 | Minimum standards and quality | 2303.1 | Minimum standards and quality | Added structural log members, structural composite lumber, round timber poles and piles, nails and staple to list of applicable products covered by this section. |
| 2303.1.5 | Fiberboard | 2303.1.5 | Fiberboard | Replaced reference to ANSI/AHA A194.1 with ASTM C208, the recognized specification for cellulosic fiberboards. |
| 2303.1.5.4 | Insulating roof deck | - | - | Section deleted. Insulating fiberboard roof deck product is no longer manufactured. |
| 2303.1.8 | Preservative treated wood | 2303.1.8 | Preservative treated wood | All referenced standards for perservative-treated would have been deleted and replace with a reference to AWPA U1 and M4 for the species, product, preservative, and end use of preservative-treated wood. |
| - | - | 2303.1.10 | Structural log members | New section added providing reference standard and grading of structural log and timber members. |
| - | - | 2303.1.11 | Round timber poles and piles |  |
| 2303.2.2.2 | Fire-retardant-treated wood | 2303.2.2.2 | Fire-retardant-treated wood | Revised section to replace, "in accordance with approved method of investigation" with new ASTM D 6841 standard developed to evaluate the ASTM D 5664 test data. |
| 2303.4 | Trusses | 2303.4 | Trusses | Revised section to remove information regarding manufacturing and inspecting and replaced with overall truss scope for design. |
| - | - | 2303.4.1.1 | Truss designer | Added section to define truss designer. |
| 2303.4.1 | Truss design drawings | 2303.4.1.2 | Truss design drawings | The requirement that a registered design professional prepare the truss drawings has been deleted. Unnecessary language was removed from Item 17. Item 18 has been revised to provide and exception to providing the required permanent individual truss member bracing on the truss design drawings, wher a bracing plan has been provided by a registered design professional. New requirements for signing and sealing the truss design drawings have been added. |
| - | - | 2303.4.1.3 | Truss placement diagram | New section added to essentially define the truss placement diagram in order to distinguish it from other documents such as installation documents, construction documents, etc. |
| - | - | 2303.4.1.4 | Truss submittal package | New criteria for and definition of truss submittal package added. |
| - | - | 2303.4.1.5 | Truss member permanent bracing | New section added providing specific criteria for bracing trusses. |
| - | - | 2303.4.1.6 | Anchorage | New section added to clarify that transfer of design loads throughout the building is the responsibility of the registered design professional. |
| - | - | 2303.4.1.7 | Alterations to trusses | Section relocated from Section 2308.10.7.3 since these requirements apply to all trusses not just ones installed where the conventional construction provisions of Section 2308 are used. |
| - | - | 2303.4.2 | Metal-plate-connected trusses | Most of information in this section was relocated from Section 2303.4. |
| 2303.6 | Nails and staples | 2303.6 | Nails and staples | Section revised regarding the bending strength of nails to indicate that a 100 ksi yield strength is required for shank diameters of at least 0.099 inches but not larger than 0.142 inches. |
| 2304.8 | Mechanically laminated floors and decks | 2304.8 | Lumber decking | Revised title to indicate that the provisions cover all decking including mechanically laminated and solid sawn decking. |
| - | - | 2304.8.2 | Layup patterns | Sections added as a result of eliminating reference to AITC 112 in Section 2306.1. New sections now address the provisions and requirements of lumber decking that were previously covered in AITC 112. |
| - | - | 2304.8.2.1 | Simple span pattern |  |
| - | - | 2304.8.2.2 | Two-span continuous pattern |  |
| - | - | 2304.8.2.3 | Combination simple and two-span |  |
| - | - | 2304.8.2.4 | Cantilevered pieces intermixed pattern |  |
| - | - | 2304.8.2.5 | Controlled random pattern |  |
| - | - | 2304.8.3 | Mechanically laminated decking |  |
| - | - | 2304.8.3.1 | General |  |
| - | - | 2304.8.3.2 | Nailing |  |
| - | - | 2304.8.3.3 | Controlled random pattern |  |
| - | - | 2304.8.4 | Two-inch sawn tongue-and-groove decking |  |
| - | - | 2304.8.4.1 | General |  |
| - | - | 2304.8.4.2 | Nailing |  |
| - | - | 2304.8.4.3 | Controlled random pattern |  |
| - | - | 2304.8.5 | Three-and4-inch sawn tongue-and-groove decking |  |
| - | - | 2304.8.5.1 | General |  |
| - | - | 2304.8.5.2 | Nailing |  |
| - | - | 2304.8.5.3 | Controlled random pattern |  |
| 2304.9.5 | Fasteners in preservative-treated and fire-retardant-treated wood. | 2304.9.5 | Fasteners in preservative-treated and fire-retardant-treated wood. | Revised section by subdividing fastener requirements for preservative-treated wood, wood foundations, and fire-retardant-treated wood into separate sections. |
| - | - | 2304.9.5.1 | Fasteners for preservative treated wood | Requires fasteners for preservative-treated wood to have coating weights for zinc-coated fasteners to be in accordance with ASTM A 153. Exception permits fasteners, other than nails and timber rivets, of mechanically deposited zinc-coated steel to have coating weights in accordance with ASTM B 695, Class 55 minimum. |
| - | - | 2304.9.5.2 | Fastenings for wood foundations | New section containing the reference to AF&PA TR No. 7 for wood foundations previously contained in Section 2304.9.5. |
| - | - | 2304.9.5.3 | Fasteners for fire-retardant-treated wood used in exterior applications or wet or damp locations | New section specific to fasteners used for fire-retardant-treated wood in exterior applications. Permits fasteners other than nails, timber rivets, lag screws and wood screws to be mechanically deposited zinc-coated steel with coating weights in accordance with ASTM B 695, Class 55 minimum. |
| - | - | 2304.9.5.4 | Fasteners for fire-retardant-treated wood used in interior applications | New section specific to fasteners used for fire-retardant-treated wood in interior applications. Requires fasteners to be in accordance with manufacturer's specifications. |
| Table 2304.9.1 | Fastening Schedule | Table 2304.9.1 | Fastening Schedule | Revised entire table and footnotes to add nail size (shank length and diameter). The addition will assist to ensure proper nail type and size by adding the information to the pennyweight system currently utilized. |
| 2304.11.2 | Protection of decay and termites for wood used above ground | 2304.11.2 | Protection of decay and termites for wood used above ground | Replaced all standard references with AWPA U1. |
| 2304.11.2.2 | Framing | 2304.11.2.2 | Wood supported by exterior foundation | Revised title for both sections to establish distinct sections for requirements of both above grade and below grade. |
| 2304.11.2.3 | Sleepers and sills | 2304.11.2.3 | Exterior walls below grade |  |
| 2304.11.3 | Laminated timbers | 2304.11.3 | Laminated timbers | Revised to add "from moisture" for clarification. |
| 2304.11.4.1 | Posts or columns | 2304.11.4.1 | Posts or columns | Editorial revision to add "that is" to itemize each intent within the section. |
| 2304.11.6 | Termite protection | 2304.11.6 | Termite protection | Added AWPA U1, or user specification standard, for clarification. |
| 2304.11.7 | Wood used in retaining walls and cribs | 2304.11.7 | Wood used in retaining walls and cribs |  |
| 2304.12 | Wood supporting masonry or concrete | 2304.12 | Long-term loading | Section completely revised and now permits wood members to support concrete or masonry provided checks for long-term loading using the AF&PA NDS. |
| 2305.1 | Lateral-force-resisting systems | 2305.1 | Lateral-force-resisting systems | Revised section to permit compliance with AF&PA SDPWS as an alternative to Section 2305. |
| 2305.2.2 | Deflection | 2305.2.2 | Deflection | New table added to provide for use in determining diaphragm deflections. |
| - | - | Table 2305.2.2(1) | Values for use in calculating diaphragm deflection due to fastener slip |  |
| 2305.2.4 | Construction - wood diaphragms | 2305.2.4 | Construction - wood diaphragms | Revised section to move information about shear walls to the appropriate location in Section 2305.3.3. |
| - | - | Table 2305.2.2(2) | Values of Gt | New table added to provide for use in determining diaphragm deflections. |
| 2305.2.5 | Rigid diaphragms | 2305.2.5 | Rigid diaphragms | Revised references from "9.5.2.3" to 12.3.2" and for horizontal shear distribution revised from "9.5.5.5" to "12.8.4." |
| Equation 23-2 2305.3.2 | Deflection | Equation 23-2 2305.3.2 | Deflection | Method for calculation shear wall deflection have been revised for consistency with the AF&PA SDPWS. |
| - | - | 2305.3.3 | Construction - shear walls | Pertinent information about shear wall construction relocated from Section 2305.2.4. |
| 2305.3.3 | Shear wall aspect ratios | 2305.3.4 | Shear wall aspect ratios | Revised section to clarify the inclusion of piers in shear wall dimensions and also added references for the height and width determinations. |
| Table 2305.3.3 | Shear wall aspect ratios | Table 2305.3.4 | Shear wall dimension ratios | Renamed table to Maximum shear wall dimension ratios. Footnote b revised language from "aspect ratio" to height-to-width" ratio. |
| 2305.3.4 | Shear wall height definition | 2305.3.5 | Shear wall height definition | Added "h" to denote wall height for table. |
| - | - | 2305.3.5.1 | Perforated shear wall segment height definition | The determination of the shear wall height has been revised to clarify the differences between the different methods for designing shear walls (perforated, force transfer, etc.) |
| - | - | 2305.3.5.2 | Force transfer shear wall pier height definition |  |
| 2305.3.5 | Shear wall width definition | 2305.3.6 | Shear wall height definition | The determination of the shear wall width has been revised to clarify the differences between the different methods for designing shear walls (perforated, force transfer, etc.) |
| - | - | 2305.3.6.1 | Perforated shear wall segment width definition |  |
| - | - | 2305.3.6.2 | Force transfer shear wall pier width definition |  |
| 2305.3.7.2 | Perforated shear walls | 2305.3.8.2 | Perforated shear walls | Revised section to add references for the height and width determinations. |
| 2305.7.2.2 | Perforated shear wall resistance | 2305.8.2.2 | Perforated shear wall resistance | Added Item 3 to clarify the determination of the unadjusted shear resistance for the upper limits on height-to-width ratios. |
| 2305.3.7.2.5 | Anchorage for in-plane shear | 2305.3.8.2.5 | Anchorage for in-plane shear | Revised section to remove "drag struts" parenthetical notation. |
| 2306.1 | List of applicable standards | 2306.1 | List of applicable standards | Removed AITC 500 since methods to determine design values for structural glued laminated timber are now included and reference in ASTM D3737. |
| 2306.1 | List of applicable standards | 2306.1 | List of applicable standards | Revised "Plywood" design specification to "Panel" design specification under APA. |
| - | - | 2306.1.4 | Lumber decking | Added section and table for lumber decking. Section references new table for allowable loads. This addition incorporates pertinent provisions from AITC no longer referenced in code. |
| - | - | Table 2306.1.4 | Allowable loads for lumber decking |  |
| 2306.2.1 | Wind provisions for wall stud bending stress increase | 2306.2.1 | Wind provisions for wall stud bending stress increase | Revised language to clarify that sheathing is not only attached to studs, but that they must "occur" over studs or blocking. |
| Table 2306.2 | Wall stud bending stress increase factors | Table 2306.2 | Wall stud bending stress increase factors | Revised factors for 2 x 6 and 2 x 8 studs that were incorrect due to rounding errors. |
| - | - | 2306.3.1 | Wood structural panel diaphragms | New section providing scope, references and standards for wood structural panel diaphragms. |
| 2306.3.2 | Shear capacities modifications | 2306.3.2 | Shear capacities modifications | Added reference to Table 2306.3.2 permitting the 40% increase for wind design for High Load Diaphragms. |
| Table 2306.3.1 | Recommended shear for wood structural panel diaphragms | Table 2306.3.1 | Allowable shear for wood structural panel diaphragms | Revised title to replace "recommended" with "allowable" for consistency with other table titles. Added actual nail dimensions in parenthesis next to the penny weight. |
| 2306.4.1 | Wood structural panel shear walls | 2306.4.1 | Wood structural panel shear walls | Revised reference for wood structural panel design from "APA/PDS" to "APA Panel Design Specification." |
| 2306.4.4 | Fiberboard shear walls | 2306.4.4 | Fiberboard shear walls | Revised reference in section from "Table 2308.9.3(4)" to "Table 2306.4.4." |
| 2306.4.5.1.3 | Nailing | 2306.4.5.1.3 | Fastening | Revised language from "nails" to "fastener(s)(ing)." |
| 2306.4.5.1.4 | Fasteners | 2306.4.5.1.4 | Fasteners |  |
| 2307.1 | Load and resistance factor design | 2307.1 | Load and resistance factor design | Revised scope to remove parenthetical (LRFD) and to replaced reference to ASCE 16 with AF&PA NDS. |
|  |  | 2314.4.5 |  | Correct Address for AWPA and updates applicable standards. American Wood Preservers Association P.O. Box 361784, Birmingham, AL 35236-1784 1. AWPA Use Category Systems Standard U1 2. AWPA Standard M4 Care of Pressure Treated Wood Products |
|  |  | 2315.1.9 | Quality | Updates applicable standards. Clarifies section. Pressure-treated poles shall be treated in accordance with AWPA U1 for sawn timber posts (Commodity Specification A, Use Category 4B) and for round timber posts (Commodity Specification B, Use Category 4B) |
|  |  | 2325.3 | Wood Supporting Masonry | Plywood decking and approved wood panels, wood joists and wood studs supporting such wood joists may be used to support reinforced concrete slabs, concrete-base tile and terrazzo floors and lightweight concrete toppings as follows: 1. There shall be an approved moisture vapor barrier between the concrete or other cementitious materials and the wood. 2. Wood members supporting concrete shall be preservative treated in compliance with AWPA Use Category Systems Standard U1, Commodity Specification A Use Category 4B set forth in Sections 2314.4 and 2326. 3. Approved wood-based structural-use panel decking shall be rated for Exposure 1. 4. Wood rafters may support concrete roof tile. |
| 2328.2 HVHZ | Fencing | 2328.2 HVHZ | Fencing | Revised administrative error to correct "8-inch" to "8-feet" and corresponding "203mm" to "2438 mm." |
| Chapter 24: Glass and Glazing |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| 2403.1 | Identification for glass | 2403.1 | Identification for glass | Revised manufacturer's "label" to manufacturer's "mark." Laser etched added as a method for applying the identification mark for tempered glass. |
|  |  | 2403.1 | Identification. | Clarify in laminated glass the laminator, thickness of the glass and the name of the interlayer must be identified. Each pane shall bear the manufacturer’s mark designating the type and thickness of the glass or glazing material. With the exception of tempered glazing materials or laminated materials, the identification shall not be omitted unless approved and an affidavit is furnished by the glazing contractor certifying that each light is glazed in accordance with approved construction documents that comply with the provisions of this chapter. Safety glazing shall be identified in accordance with Section 2406.2. Each pane of tempered glass, except tempered spandrel glass, shall be permanently identified by the manufacturer and each pane of laminated glass shall be permanently identified with the laminator, overall glass thickness and trade name of interlayer. The identification mark shall be acid etched, sand blasted, ceramic fired, laser etched, embossed or of a type that, once applied, cannot be removed without being destroyed. Tempered or laminated spandrel glass shall be provided with a removable paper marking by the manufacturer. |
| 2405.5 | Unit skylights | 2405.5 | Unit skylights | Updated the reference standard throughout this section to AAMA/WDMA/CSA 101/I.S.2/A440. |
| 2406.1.2 | Wired glass | - | - | Section deleted. Wired glass is not permitted to be used as a glazing material in hazardous locations. |
| 2406.2 | Identification of safety glass | 2406.2 | Identification of safety glass | Revised section and exceptions for consistency of utilizing the terms label, mark and manufacturer's designation. Identification for safety glazing was revised from "label" to "manufacturer's designation." Also added clarification that a label as described in Section 1702 will also meet the requirements. |
| 2406.2.1 | Multilight assemblies | 2406.2.1 | Multilight assemblies | Section previously allowed for the assembly to marked with CPSC 16 CFR 1201 or ANSI Z97. Section was revised to remove the ANSI allowance since it doesn't meet full intent of this section. |
| 2407.1 | Glass in handrails and guards | 2407.1 | Glass in handrails and guards | Revised language (no change to technical portion of code) to revise "structural balustrade panels in railings" to "a handrail assembly or a guard section." |
| 2407.1.3 | Parking garages | 2407.1.3 | Parking garages | Revised language from "railings" to "handrails or guards." |
| 2409.1 | Glass in floors and sidewalks | - | - | Removed entire section. Code and references currently do not fully address the design requirements for this section and therefore section is removed and glass in floors applications will be engineered by a registered design professional as opposed to attempting to address specific requirements in this section. |
| - | - | 2409 | Glass in elevator enclosures | New section added requiring glass in elevator enclosures to comply with ANSI Z97.1 or 16 CFR Part 1201.. |
| 2411.3.2.1 HVHZ | Operative window and door assemblies in HVHZ | 2411.3.2.1 HVHZ | Operative window and door assemblies in HVHZ | Added exception number 3 to include pass-through windows for serving from single-family kitchen. |
| 2411.3.2.5HVHZ | Window and door assembly tests | 2411.3.2.5HVHZ | Window and door assembly tests | Revised section item number 7 to move information from this item to exception number 3 of 2411.3.2.1. a more appropriate location for the exception. New item number 7 limits the compared unit to the maximum cyclic pressure when tested to TAS 203. |
| 2411.3.2.6 HVHZ | Fixed glass windows | 2411.3.2.6 HVHZ | Fixed glass windows | New item number 8 limits the compared unit to the maximum cyclic pressure when tested to TAS 203. |
| - | - | 2411.3.3.7 HVHZ | Exterior lite of glass | Requires the exterior lite of glass in an insulated glazing unit to be safety glazing. Exceptions provided for large missile impact resistant glazed assemblies and other assemblies protected by shutters. |
| - | - | 2411.3.4 HVHZ | Gaskets in glazing systems | Added new section to provide list of ASTM standards applicable for gasket use in glazing. |
| Chapter 25: Gypsum Board and Plaster |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| 2509.2 | Base for tile | 2509.2 | Base for tile | Section revised requiring the use of cement, fiber-cement, or glass mat gypsum backer as a base for wall tile in tub and shower areas and wall and ceiling panels in shower areas. Water-resistant gypsum backing board permitted to be used as abase for tile water closet compartment walls. |
| 2510.5.2.1 | Gypsum backing board for stucco | 2510.5.2.1 | Gypsum backing board for stucco | Revised language from "weather-resistant" to "water-resistive." |
| 2510.5.2.2 | Gypsum sheathing for stucco | 2510.5.2.2 | Gypsum sheathing for stucco |  |
| 2510.6 | Water-resistive barriers | 2510.6 | Water-resistive barriers | Revised language in title and in section from "weather-resistant" to "water-resistive." Exception added for commonly used alternative to 2 layers of Grade D paper. |
| 2510.8 | Sealing at plaster and fenestration | 2510.8 | Sealing at plaster and fenestration | New section requiring the juncture of exterior plaster and fenestrations products to be sealed, in accordance with the standards referenced. |
| 2512.1.2 | Plaster and weep screeds | 2512.1.2 | Plaster and weep screeds | Revised language from "weather-resistant" to "water-resistive." |
| Chapter 26: Plastic |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
|  |  | 2601.1 | Scope | Correct reference to section 2603.8 These provisions shall govern the materials, design, application, construction and installation of foam plastic, foam plastic insulation, plastic veneer, interior plastic finish and trim and light-transmitting plastics. See Chapter 14 for requirements for exterior wall finish and trim. Exception: Buildings and structures located within the high-velocity hurricane zone shall comply with the provisions of Sections 2603.8 and 2612. |
| 2603.4.1.12 | Interior Signs | 2603.4.1.12 | Interior Signs | Added additional sentence regarding foam plastic signs not affixed to interior surfaces. This addition provides a cross reference to the FFPC. |
| 2603.8 | Special Approval | 2603.9 | Special Approval | Referenced large-scale tests revised require the use of the acceptance criteria of Section 803.2 when using NFPA 286. |
| 2603.9 | Protection against termite damage | 2603.8 | Protection against termite damage | Relocated section. |
| 2603.9.1 |  | 2603.8.1 |  |  |
| 2603.9.2 |  | 2603.8.2 |  |  |
| 2606.7.5 | Electrical lighting fixtures | 2606.7.5 | Electrical luminaries | Revised language for title and in section from "lighting fixtures" to "luminaries." |
| 2606.10 | Light transmitting plastics for awnings, patio covers and similar structures | 2606.10 | Light transmitting plastics for awnings, patio covers and similar structures | Editorial revision to remove "and appendages" from regarding projections. |
| Chapter 27: Electrical |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
|  |  | 2705.1 | Equipotential Bonding | Add criteria for equipotential bonding of pools. 2705.1 NFPA 70A - 05: National Electric Code, Article 680 (Swimming Pools, Fountains, and Similar Installation), Section 680.26, Equipotential Bonding is amended to read as follows: 680.26 Equipotential Bonding. (A) Performance. The equipotential bonding required by this section shall be installed to reduce voltage gradients in the pool area. (B) Bonded Parts. The parts specified in 680.26(B)(1) through (B)(57) shall be bonded together using solid copper conductors, insulated covered, or bare, not smaller than 8 AWG or with rigid metal conduit of brass or other identified corrosion-resistant metal. Connections to bonded parts shall be made in accordance with 250.8. An 8 AWG or larger solid copper bonding conductor provided to reduce voltage gradients in the pool area shall not be required to be extended or attached to remote panel boards, service equipment, or electrodes. - Conductive Pool Shells. Bonding to conductive pool shells shall be provided as specified in 680.26(B)(1)(a) or (B)(1)(b). Poured concrete, pneumatically applied or sprayed concrete, and concrete block with painted or plastered coatings shall all be considered conductive materials due to water permeability and porosity. Vinyl liners and fiberglass composite shells shall be considered to be non-conductive materials. - Structural Reinforcing Steel. Unencapsulated structural reinforcing steel shall be bonded together by steel tie wires or the equivalent. Where structural reinforcing steel is encapsulated in a nonconductive compound, a copper conductor grid shall be installed in accordance with 680.26(B)(1)(b). - Copper Conductor Grid. A copper conductor grid shall be provided and shall comply with (b)(1) through (b)(4): (1) Be constructed of minimum 8 AWG bare solid copper conductors bonded to each other at all points of crossing. (2) Conform to the contour of the pool and the pool deck. - Be arranged in a 300 mm (12 in.) by 300 mm (12 in.) network of conductors in a uniformly spaced perpendicular grid pattern with a tolerance of 100 mm (4 in.). - Be secured within or under the pool no more than 150 mm (6 in.) from the outer contour of the pool shell. - Perimeter Surfaces. The perimeter surface shall extends for 1 m (3 ft) horizontally beyond the inside walls of the pool and shall includes unpaved surfaces as well as poured concrete and other types of paving. Bonding to perimeter surfaces shall be provided as specified in 680.26(B)(2)(a) or (2)(b), and shall be attached to the pool reinforcing steel or copper conductor grid at a minimum of four (4) points uniformly spaced around the perimeter of the pool. For non-conductive pool shells, bonding at four points shall not be required. - Structural Reinforcing Steel. Structural reinforcing steel shall be bonded In accordance with 680.26 (B)(1)(a). - Alternate Means. Where structural reinforcing steel is not available or is encapsulated in a nonconductive compound, a copper conductor(s) shall be utilized where the following requirements are met: - At least one minimum 8 AWG bare solid copper conductor shall be provided. - The conductor(s) shall follow the contour of the perimeter surface. - Only listed splices shall be permitted. - The required conductor shall be 450 to 600 mm (18 to 24 in.) from the inside walls of the pool. - The required conductor shall be secured within or under the perimeter surface 100 to 150 mm (4 to 6 in.) below the subgrade. - Metallic Components. All metallic parts of the pool structure, including reinforcing metal not addressed in 680.26(B)(1)(a), shall be bonded. Where reinforcing steel is encapsulated with a nonconductive compound, the reinforcing steel shall not be required to be bonded. - Underwater Lighting. All metal forming shells and mounting brackets of no-niche luminaries shall be bonded. Exception: Listed low-voltage lighting systems with nonmetallic forming shells shall not require bonding. - Metal Fittings. All metal fittings within or attached to the pool structure shall be bonded. Isolated parts that are not over 100 mm (4 in.) in any dimension and do not penetrate into the pool structure more than 25 mm (1 in.) shall not require bonding. - Electrical Equipment. Metal parts of electrical equipment associated with the pool water circulating system, including pump motors and metal parts of equipment associated with pool covers, including electric motors, shall be bonded. Exception: Metal parts of listed equipment incorporating an approved system of double insulation shall not be bonded. - Double-Insulated Water Pump Motors. Where a double-insulated water-pump motor is installed under the provisions of this rule, a solid 8 AWG copper conductor of sufficient length to make a bonding connection to a replacement motor shall be extended from the bonding grid to an accessible point in the vicinity of the pool pump motor. Where there is no connection between the swimming pool bonding grid and the equipment grounding system for the premises, this bonding conductor shall be connected to the equipment grounding conductor of the motor circuit. - Pool Water Heaters. For pool water heaters rated at more than 50 amperes and having specific instructions regarding bonding and grounding, only those parts designated to be bonded shall be bonded and only those parts designated to be grounded shall be grounded. (7) Metal Wiring Methods and Equipment. Metal-sheathed cables and raceways, metal piping, and all fixed metal parts shall be bonded. Exception No. 1: Those separated from the pool by a permanent barrier shall not be required to be bonded. Exception No. 2: Those greater than 1.5 m (5 ft) horizontally of the inside walls of the pool shall not be required to be bonded. Exception No. 3: Those greater than 3.7 m (12 ft) measured vertically above the maximum water level of the pool, or as measured vertically above any observation stands, towers, or platforms, or any diving structures shall not be required to be bonded. (C) Pool Water. An intentional bond of a minimum conductive surface area of 5806 mm 2 (9 in 2 ) shall be installed in contact with the pool water. This bond shall be permitted to consist of parts that are required to be bonded in 680.26(B). |
|  |  | 2706.1 | Connection of Grounding and Bonding Equipment. | Add criteria for Grounding and Bonding of equipment. (Revised in accordance with SB2836 2007) NFPA 70A-05 National Electric Code, Article 250 (Grounding and Bonding), Section 250.8 Connection of Grounding and Bonding Equipment is amended to read as follows: 250.8 Connection of Grounding and Bonding Equipment. A. Permitted Methods. Grounding conductors and bonding jumpers shall be connected by one of the following means: - Listed pressure connectors - Terminal bars - Pressure connectors listed as grounding and bonding equipment - Exothermic welding process - Machine screw-type fasteners that engage not less than two threads or are secured with a nut - Thread-forming machine screws that engage not less than two threads in the enclosure - Connections that are part of a listed assembly - Other listed means B. Methods not permitted. Connection devices or fittings that depend solely on solder shall not be used. |
| Chapter 30: Elevators and Conveying Systems |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| 3001.2 | Hoistway enclosure protection | 3001.2 | Hoistway enclosure protection | Revised references in section from a broad reference to chapter 6 to a more specific reference of Section 707 (shaft enclosures) and 715 (Opening Protectives). |
| 3002.1.1 | Hoistway enclosure opening protectives | 3002.1.1 | Hoistway enclosure opening protectives | Added exception to section to clarify coordination with ASME A17.1. |
| 3002.4 | Elevator accommodation for ambulance stretcher | 3002.4 | Elevator accommodation for ambulance stretcher | Revised language from "four stories in height" to "four or more stories above grade plane or four or more stories below grade plane" for clarification. |
|  |  | 3002.4 | Elevator car to accommodate an ambulance stretcher. | Change to make FBC consistent with Florida Statutes 399.035(2) Where elevators are provided in buildings four or more stories above grade plane or four or more stories below grade plane, or where the rise exceeds 25 feet, at least one elevator shall be provided for fire department emergency access to all floors. The elevator car shall be of such a size and arrangement to accommodate an ambulance stretcher 24-inch by 76-inch (610 mm by 1950 mm) ambulance stretcher in the horizontal, open position and shall be identified by the international symbol for emergency medical services (star of life). The symbol shall not be less than 3 inches (76 mm) high and shall be placed inside on both sides of the hoistway door frame. |
| - | - | 3002.8 | Glass in elevator enclosure | Added section for coordination of ASME requirements. |
| 3002.8 | Hoistway enclosure automatic fire alarm locations | 3002.9 | Hoistway enclosure automatic fire alarm locations | Relocated section and revised to remove specific language regarding locations but to add referenced compliance standards. |
| - | - | 3002.9 | Hoistway enclosure automatic fire alarm locations | Added section to include, "Automatic fire alarm initiating devices shall be located and installed in accordance with ASME A 17.1 and NFPA 72." |
| 3004.2 | Location of vents | 3004.2 | Location of vents | Revised section to remove "below the floor or floors" from allowable vent locations, which coordinates with requirements of ASME A17. and to eliminate confusion of the term floor since it doesn't specify "floor of penthouse." |
| 3004.3 | Area of vents | 3004.3 | Area of vents | Revised section to include requirement regarding closed portions of the required vent area. Also added exception to allow vents to be closed except when needed to vent hot gasses. |
| 3004.4 | Closed vents | - | - | Removed section. Relocated information to 3004.3 to editorially clarify intent stated above. |
| 3005.2.1 | Escalator enclosure | 3005.2.1 | Escalator enclosure | Revision is editorial to clarify that shaft enclosures are what enclose escalator openings. |
| 3005.3.1 | Conveyor enclosure | 3005.3.1 | Conveyor enclosure | Revised references in section from a broad reference to chapter 6 to a more specific reference of Section 707 (shaft enclosures) and 715 (Opening Protectives). |
| 3006.4 | Machine rooms and machinery spaces | 3006.4 | Machine rooms and machinery spaces | Section revised language from specifying that rooms must be enclosed with construction that has a fire-resistance rating, to a more specific requirement of "fire barrier complying with Section 706 or 711." |
| Chapter 31: Special Construction |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| 3102.3.1 | Membrane structures and interior liner material | 3102.3.1 | Membrane structures and interior liner material | Revised language in exception from "flame resistant" to, "in accordance with NFPA 701" to clarify that the term flame-resistant is not an equivalent requirement to NFPA fire propagation performance. |
| 3102.6.1.1 | Membrane | 3102.6.1.1 | Membrane | Revised title from "Flame-resistant membrane" to "Membrane." Also removed the term flame-resistant from the section and added the standard for the criteria of NFPA 701. |
| 3102.8.3 | Support provisions for inflation systems | 3102.8.3 | Support provisions for inflation systems | Revised language from "more than 50" to "50 or more" for consistency throughout the code. |
| 3104.3 | Pedestrian walkways and tunnels | 3104.3 | Pedestrian walkways and tunnels | Revised section to add exception 2 to clarify the allowance of fire-retardant-treaded wood for walkways. |
| 3104.5 | Fire barriers between pedestrian walkways and buildings | 3104.5 | Fire barriers between pedestrian walkways and buildings | Revised exception 1 to add "except for open parking garages" due to their limited fire hazard. |
| 3104.11 | Ventilation for pedestrian walkways and tunnels | - | - | Removed section. Requirement isn't necessary and was based on older code requirements. |
|  |  | 3105.3.1 | Fabric awnings and fabric covered frames. | Change to be consistent with ICC 301.2.3 and 3102.6.1.1 Fabric used for awnings or fabric-covered frames shall meet the flame propagation performance criteria of NFPA 701. Exception: Awnings or fabric-covered frames used in conjunction with Group R-3 occupancies. |
| 3105.4 | Awning and canopy designs | 3105.4 | Awning and canopy designs | Revised language in exception from "flame resistant" to, "in accordance with NFPA 701" to clarify that the term flame-resistant is not an equivalent requirement to NFPA fire propagation performance. |
| Chapter 32: Encroachments into the Public Right-of-Way |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| 3201.2 | Encroachment measurement | 3201.2 | Encroachment measurement | Revised section to remove the term "appendage" and add "or portion thereof" in reference to projections of the structure. |
| Chapter 33: Safeguards During Construction |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| 3310.1 | Stairways required | 3310.1 | Stairways required | Revised section to require temporary lighted stairway for height greater than "one story," and remove height allowance of "four stories." Added requirement, "During construction, the stairway shall be enclosed where the building exterior walls are in place." |
| 3310.3 | Stairway floor number signs | 3310.3 | Stairway floor number signs | Added section to require floor number signs in accordance with Section 1020.1.6 for temporary stairways. |
| Chapter 35 Reference Standards |  |  |  |  |
| Section | Requirement | Section | Analysis |  |
|  |  | Chapter 35 | Revise address and update Standard AAF Aluminum Association of Florida, Inc. 3165 McCrory Place, Suite 185 Orlando, FL 32803 AAF 07-1 Guide to Aluminum Construction in High Wind Areas 2007-1--- ---- 2202.41 |  |
|  |  | Chapter 35 | Delete Standards as they are no longer referenced in code. ASME A112.18.19.8M—1987 Suction Fittings for Use in Swimming Pools, Wading Pools, Spas, Hot Tubs and Whirlpool Bathing Appliances………….3109.5.1 A112.19.17—2002 Manufactured Safety Vacuum Release Systems (SVRS) for Residential and Commercial Swimming Pool, Spa, Hot Tub and Wading Pool |  |
|  |  | Chapter 35 | Change Organization name from NSPI to APSP and update Standards APSP - Association of Pool and Spa Professionals ANSI/NSPI 6 -99 American National Standard for Portable Spas……....424.2.6.1 ANSI/APSP 7 – 06 American National Standard for Suction Entrapment Avoidance in Swimming Pools, Wading Pools, Spas, Hot Tubs, and Catch Basins…….424.2.66 |  |
|  |  | Chapter 35 | Standards Update ASTM A 924 /A924M—04 Standard Specification for General Requirements for Steel Sheet, Metallic-coated by the Hot-dip Process . . . . . . . . . . . Table 1507.4.3(1) . 2319.17.2.2.7. ASTM D 2824 Standard Specification for Aluminum-Pigmented Asphalt Roof Coatings, Nonfibered Asbestos Fibered, and Fibered without Asbestos. Table 1507.10.2 ASTM D 6509-00 Specification for Atactic Polypropylene (APP) Modified Bituminous Base Sheet Materials Using Glass Fiber Reinforcements 1507.11.2 ASTM E 283-04 Test Method for Determining Rate of Leakage Through Exterior Windows, Curtain Walls and Doors Under Specified Pressure Differences Across the Specimen 13-606.ABC.1.1, 13-606.ABC.1.2.4 |  |
|  |  | Chapter 35 | Standards Update DASMA ANSI/DASMA 107-98 (03) Room Fire Test Standard (remainder unchanged) ANSI/DASMA 108-05 Standard Method for Testing Sectional Garage Doors and Rolling Doors: Determination of Structural Performance Under Uniform Static Air Pressure Difference 1714.5.3.1 ANSI/DASMA 115-05 Standard Method for Testing Garage Doors (remainder unchanged) |  |
|  |  | Chapter 35 | Standards Update FM 4470 (1992) Approval Standard for Class 1 Roof Covers …...1504.3.1, 1504.7, 1515.1.1 |  |
|  |  | Chapter 35 | Standards Update NFPA 32 - 04 Dry Cleaning Plants ……………………………………………...415.6.4 96 - 04 Standard for Ventilation Control and Fire Protection of Commercial Cooking Operations………………………………………………………..436.6.2 99- 05 Standard for Health Care Facilities………………………….4203.18.1, 420.3.20.2, 420.3.25.1, 419.3.18, 419.3.18.8 101-06 Life Safety Code . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 420.3.3.6, 423.6.1, 423.14.2.1, 423.27.9.1, 423.27.10.1, 427.2.2.1.1.1, 427.1.4.13.2, 427.1.4.2.13, 427.1.4.1.1.2, 427.1.3.1.1.2, 903.6.2, 120 - 04 Coal Preparation Plants . . . . . . . . . . . . . . . . . . . . . . . . . . . .415.6.1 259 - 03 Test Method for Potential Heat of Building Materials. 2603.4.1.10, 2603.5.3, 2612.3.2.4.4 286 - 06 Standard Method of Fire Test for Evaluating Contribution of Wall and Ceiling Interior Finish to Room Fire Growth . . . . . .402.15.4, 803.2, 803.2.1, 803.5, 803.6.3, 2603.4, 2603.9 409- 04 Aircraft Hangars . . . . . . . . . . . . . . . . . . . . . . . . . . .412.2.6, 412.4.5 484 - 06 Combustible Metals, Metal Powders and Metal Dust . . . .415.6.1 780 - 04 Installation of Lighting Systems . . .419.3.19, 420.3.26.1, 423.17.7 |  |
|  |  | Chapter 35 | Add new reference standards UL ANSI/UL 2034 - 96, Standard for Single and Multiple Station CO Alarms…………….……202 UL 2075 - 04, Gas and Vapor Detector Sensor………………………….202 |  |

END OF TABLE

ATTACHMENT

Table 602 Revised

TABLE 602 
FIRE-RESISTANCE RATING REQUIREMENTS FOR EXTERIOR 
WALLS BASED ON FIRE SEPARATION DISTANCE a, e

| FIRE SEPARATION DISTANCE = x (feet) | TYPE OF CONSTRUCTION | GROUP H | GROUP F-1, M, S-1 | GROUP A, B, E, F-2, I, R b , S-2, Ub |
| --- | --- | --- | --- | --- |
| xc | I-A, I-B, III-A, III-B, IV Others | 3 3 | 3 2 | 3 1 |
| 5  x < 10 | I-A, I-B, III-A, III-B, IV Others | 3 2 | 2 1 | 2 1 |
| 10  x < 20 | I-A, I-B, III-A, III-B, IV IIB, VB Others | 2 1 1 | 2 0 1 | 2 d 0 1 d |
| 20  x < 30 | I-A, I-B, III-A, III-B, IV Others | 1 1 | 1 0 | 1 d 0 d |
| x30 | All | 0 | 0 | 0 |

For SI:     1 foot = 304.8 mm.

- Load-bearing exterior walls shall also comply with the fire-resistance rating requirements of Table 601.

- For special requirements for Group U occupancies see Section 406.1.2

- See Section 705.1.1 for party walls.

- Open parking garages complying with Section 406 shall not be required to have a fire-resistance rating.

- The fire-resistance rating of an exterior wall is determined based upon the fire separation distance of the exterior wall and the story in which the wall is located.

TABLE 503

ALLOWABLE HEIGHT AND BUILDING AREASa

Height limitations shown as stories and feet above grade plane.

Area limitations as determined by the definition of “Area, building,” per story.

| GROUP |  | TYPE OF CONSTRUCTION |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | TYPE I |  | TYPE II |  | TYPE III |  | TYPE IV | TYPE V |  |
|  |  | A | B | A | B | A | B | HT | A | B |
|  | Hgt(feet) Hgt(S) | UL | 160 | 65 | 55 | 65 | 55 | 65 | 50 | 40 |
| A-1 | S A | UL UL | 5 UL | 3 15,500 | 2 8,500 | 3 14,000 | 2 8,500 | 3 15,000 | 2 11,500 | 1 5,500 |
| A-2 | S A | UL UL | 11 UL | 3 15,500 | 2 9,500 | 3 14,000 | 2 9,500 | 3 15,000 | 2 11,500 | 1 6,000 |
| A-3 | S A | UL UL | 11 UL | 3 15,500 | 2 9,500 | 3 14,000 | 2 9,500 | 3 15,000 | 2 11,500 | 1 6,000 |
| A-4 | S A | UL UL | 11 UL | 3 15,500 | 2 9,500 | 3 14,000 | 2 9,500 | 3 15,000 | 2 11,500 | 1 6,000 |
| A-5 | S A | UL UL | UL UL | UL UL | UL UL | UL UL | UL UL | UL UL | UL UL | UL UL |
| B | S A | UL UL | 11 UL | 5 37,500 | 4 23,000 | 5 28,500 | 4 19,000 | 5 36,000 | 3 18,000 | 2 9,000 |
| E/D | S A | UL UL | 5 UL | 3 26,500 | 2 14,500 | 3 23,500 | 2 14,500 | 3 25,500 | 1 18,500 | 1 9,500 |
| F-1 | S A | UL UL | 11 UL | 4 25,000 | 2 15,500 | 3 19,000 | 2 12,000 | 4 33,500 | 2 14,000 | 1 8,500 |
| F-2/F-3 | S A | UL UL | 11 UL | 5 37,500 | 3 23,000 | 4 28,500 | 3 18,000 | 5 50,500 | 3 21,000 | 2 13,000 |
| H-1 | S A | 1 21,000 | 1 16,500 | 1 11,000 | 1 7,000 | 1 9,500 | 1 7,000 | 1 10,500 | 1 7,500 | NP NP |
| H-2 d | S A | UL 21,000 | 3 16,500 | 2 11,000 | 1 7,000 | 2 9,500 | 1 7,000 | 2 10,500 | 1 7,500 | 1 3,000 |
| H-3 d | S A | UL UL | 6 60,000 | 4 26,500 | 2 14,000 | 4 17,500 | 2 13,000 | 4 25,500 | 2 10,000 | 1 5,000 |
| H-4 | S A | UL UL | 7 UL | 5 37,500 | 3 17,500 | 5 28,500 | 3 17,500 | 5 36,000 | 3 18,000 | 2 6,500 |
| H-5 | S A | 4 UL | 4 UL | 3 37,500 | 3 23,000 | 3 28,500 | 3 19,000 | 3 36,000 | 3 18,000 | 2 9,000 |
| I-1 | S A | UL UL | 9 55,000 | 4 19,000 | 3 10,000 | 4 16,500 | 3 10,000 | 4 18,000 | 3 10,500 | 2 4,500 |
| I-2 | S A | UL UL | 4 UL | 2 15,000 | 1 11,000 | 1 12,000 | NP NP | 1 12,000 | 1 9,500 | NP NP |
| I-3 | S A | UL UL | 4 UL | 2 15,000 | 1 10,000 | 2 10,500 | 1 7,500 | 2 12,000 | 2 7,500 | 1 5,000 |
| M | S A | UL UL | 11 UL | 4 21,500 | 4 12,500 | 4 18,500 | 4 12,500 | 4 20,500 | 3 14,000 | 1 9,000 |
| R-1 | S A | UL UL | 11 UL | 4 24,000 | 4 16,000 | 4 24,000 | 4 16,000 | 4 20,500 | 3 12,000 | 2 7,000 |
| R-2 | S A | UL UL | 11 UL | 4 24,000 | 4 16,000 | 4 24,000 | 4 16,000 | 4 20,500 | 3 12,000 | 2 7,000 |
| R-3 | S A | UL UL | 11 UL | 4 UL | 4 UL | 4 UL | 4 UL | 4 UL | 3 UL | 3 UL |
| R-4 | S A | UL UL | 11 UL | 4 24,000 | 4 16,000 | 4 24,000 | 4 16,000 | 4 20,500 | 3 12,000 | 2 7,000 |
| S-1 | S A | UL UL | 11 48,000 | 4 26,000 | 3 17,500 | 3 26,000 | 3 17,500 | 4 25,500 | 3 14,000 | 1 9,000 |
| S-2 b, c | S A | UL UL | 11 79,000 | 5 39,000 | 4 26,000 | 4 39,000 | 4 26,000 | 5 38,500 | 4 21,000 | 2 13,500 |
| U c | S A | UL UL | 5 35,500 | 4 19,000 | 2 8,500 | 3 14,000 | 2 8,500 | 4 18,000 | 2 9,000 | 1 5,500 |

Staff Comment:

708.1 General. The following wall assemblies shall comply with this section:

1. Walls separating dwelling units in the same building.

2. Walls separating sleeping units in occupancies in Group R-1 hotel, R-2 and I-1 occupancies.

3. Walls separating tenant spaces in covered mall buildings as required by Section 402.7.2.

4. Corridor walls as required by Section 1017.1 1016.1.

5. Elevator lobby separation as required by Section 707.14.1.

6. Residential aircraft hangars.

7. Wall separating individual tenant spaces.

Exceptions:  No change.

END OF DOCUMENT