| Mechanical Code with “2009 Supplement” |  |  |  |  |
| --- | --- | --- | --- | --- |
| 2004 FBCM |  | 2007 FBCM |  | Analysis |
| Section | Requirement | Section | Requirement |  |
| Preface |  |  |  |  |
|  |  | Preface | Adds missing language to the preface from the 2006 International Codes which explains the letters in brackets at the beginning of the paragraphs. Add text after the section, Adoption and Maintenance, to read as follows: Letter Designations in Front of Section Numbers In each code development cycle, proposed changes to the code are considered at the Code Development Hearings by the ICC Fire Code Development Committee, whose action constitutes a recommendation to the voting membership for final action on the proposed change. Proposed changes to a code section that has a number beginning with a letter in brackets are considered by a different code development committee. For example, proposed changes to code sections that have [F] in front of them (e.g. [F] 903.1.1.1) are considered by the ICC Fire Code Development Committee at the code development hearings. The content of sections in this code that begin with a letter designation are maintained by another code development committee in accordance with the following: [E] = International Energy Conservation Code Development Committee; [EB] = International Existing Building Code Development Committee; [EL] = ICC Electrical Code Development Committee; [F] = International Fire Code Development Committee; [FG] = International Fuel Gas Code Development Committee; [M] = International Mechanical Code Development Committee; and [P] = International Plumbing Code Development Committee. |  |
| Chapter 2: Definitions |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| 202 | Approved | 202 | Approved | Revised definition to change the term "approved" to "acceptable" to avoid using the defining term in the definition itself. |
| 202 | Boiler, Hot Water Supply | 202 | Boiler, Hot Water Supply | Revise capacity and temperature to be consistent with Gas Code. Any vessel used for generating hot water to be used external to the vessel, which exceeds any of the following limitations: 1. A heat input capacity of 400,000 Btuh (58.6 kW). 2. A water temperature of 210 ºF (93ºC). 3. A nominal water capacity of 120 gal (454 L). |
| 202 | Conditioned Space | 202 | Conditioned Space | Add residential energy purposes see “SPACE” in FBC-R Chapter 11. That volume of a structure which is either mechanically heated, cooled or both heated and cooled by direct means. Spaces within the thermal envelope that are not directly conditioned shall be considered buffered unconditioned space. Such spaces may include, but are not limited to, mechanical rooms, stairwells and unducted spaces beneath roofs and between floors. Air leakage into dropped ceiling cavities does not constitute conditioned space. For residential energy purposes; see “SPACE (a) conditioned space, Chapter 11 Section N1100.7.3 of the Florida Building Code, Residential. |
| 202 | - | 202 | Environmental Air | Added new definition to describe a term utilized in Chapter 5 . |
| 202 | Extra-Heavy-Duty Cooking Appliance | 202 | Extra-Heavy-Duty Cooking Appliance | Revised definition for clarification by changing "as the primary" to "all or part of the heat source." This change also provides consistency with ASHRAE standards. |
| 202 | Design Flood Elevation | 202 | - | Deleted definition. |
| 202 | - |  | Sleeping Unit | New definition of sleeping unit added |
| Chapter 3: General Regulations |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| 301.13 | Wind resistance | 301.12 | Wind resistance | Revised section to remove reference to use of design or application of Section 301.13.1 for determination of wind pressures. |
| 301.13.1 | Ground mounted units | - | - | Prescriptive requirements for attaching ground mounted units to supports for resistance to wind have been delete. |
| 302.3.4 | Engineered wood products | 302.3.4 | Engineered wood products | New language permitting cuts, notches and bored holes in engineered products where permitted by the manufacturer's recommendations. |
| 304.4 | Hydrogen-generating and refueling operations | 304.4 | Hydrogen-generating and refueling operations | Revised section to avoid limitation of the number of hydrogen-fueled vehicles to a certain number but to have the limitation based on structure size in combination with the number of vehicles being refueled. |
| 304.4.1 | Natural ventilation | 304.4.1 | Natural ventilation | Revised section to require a limit of 850 square feet for indoor refueling and a limit of output capacity of hydrogen generating appliances. |
| 304.4.1.1 | Two openings | 304.4.1.1 | Two openings | Revised section to clarify size and location of required openings to improve interpretation and enforcement. |
| 304.4.2 | Mechanical ventilation | 304.4.2 | Mechanical ventilation | Revised section to add information for equipment and appliances with ignition source to have the location of the ignition below the mechanical ventilation outlet. |
| 304.5 | Public garages | 304.5 | Public garages | Revised exception in this section to update the NFPA reference standard from 88B-97 to 30A. |
| 304.5 | Public garages | 304.5 | Public garages | Delete reference to 304.3 as the section was removed from the code. Appliances located in public garages, motor fueling dispensing facilities, repair garages or other areas frequented by motor vehicles, shall be installed a minimum of 8 feet (2438 mm) above the floor. Where motor vehicles exceed 6 feet (1829 mm) in height and are capable of passing under an appliance, appliances shall be installed a minimum of 2 feet (610 mm) higher above the floor than the height of the tallest vehicle. Exception: The requirements of this section shall not apply where the appliances are protected from motor vehicle impact and installed in accordance with NFPA 30A |
| 304.10 | Guards | 304.10 | Guards | Section revised to include roof hatch openings within the scope of when guards are required. |
| 306.4 | Appliances under floors | 306.4 | Appliances under floors | Added Exception 2 which permits the passageway to be unlimited in length where the passageway is unobstructed and not less than 6 feet high and 22 inches wide for it's entire length. |
| 306.4.1 | Electrical requirements | 306.4.1 | Electrical requirements | "Light fixture" changed to "luminaire." |
| 306.5 | Equipment and appliances on roofs or elevated structures | 306.5 | Equipment and appliances on roofs or elevated structures | Added reference to 1522.3 for minimum clearances below roof-mounted mechanical units. |
| 306.6 | Sloped roofs | 306.5.1 | Sloped roofs | Relocated section and revised requirements to include equipment, fans, or other components requiring service within the scope of this section. Also added requirements for guards, regarding extension allowance and construction requirements. |
| - | - | 306.5.2 | Electrical requirements | Added new section to provide electrical requirements under sloped roofs, similar to other sections for clarification. |
| 307.2.3 | Auxiliary and secondary drain systems | 307.2.3 | Auxiliary and secondary drain systems | Revised section to add "or fuel-fired appliance" to this section's requirements. Revised Item 2 to permit the use of water-level detection device as an alternative to a separate drain line. Revised Item 3 to require the water-level detection device to conform to UL 508. |
| - | - | 307.2.3.1 | Water-level monitoring devices | Permits the use of a water-level monitoring device on down-flow units and all other coils that do not have a secondary drain and do not have a means to install an auxiliary drain pan. |
| Chapter 4: Ventilation |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| 401.4 | Exits | 601.3 | Exits | Section relocated to Section 601.3. |
| 401.5 | Opening location | 401.4 | Opening location | Revised section to add Exception 2, which removes exhaust outlet information from 511.2 (because it falls outside of scope for that section) and adds it to this section for more appropriate location. |
| 401.5.1 | Intake openings | 401.4.1 | Intake openings | Editorial revisions for clarity. New language added stating that the exhaust from a bathroom or kitchen in a residential dwelling is not considered to be hazardous or noxious. |
| 403.1 | Ventilation Systems | 403.1 | Ventilation of uninhabited spaces | Change is result of action on the Florida Energy code. Delete reference to compliance by method “C”. |
| 403.2 | Outdoor air required | 403.2 | Outdoor air required | New exception permits a reduction in the required rate of outdoor air in accordance with an engineered systems. Additional limitations apply. |
| 403.2.1 | Recirculation of air | 403.2.1 | Recirculation of air | New language in Item 2 puts limits on the permitted amount of recirculated air. Item 3 clarified that scope of this Item is applicable to Note h in Table 403.3. |
| Table 403.3 | Required outdoor ventilation air | Table 403.3 | Required outdoor ventilation air | Note d revised to remove the exception for a mechanical ventilation system in garages having a floor area not exceeding 850 square feet. Revised table to add footnote h to accommodate the use of energy recovery ventilation. Also added footnote reference within table where applicable. |
| - | - | 406.1 | Reserved | Delete text in Section 406.1 as it is covered in 403.1 and mark section as “Reserved”. |
| Chapter 5: Exhaust Systems |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| 501.2 | Outdoor exhaust discharge | 501.2 | Exhaust discharge | New language requiring the discharge of air from mechanical exhaust systems to be discharged at point not less than the distance specified in new Section 501.2.1. |
| - | - | 501.2.1 | Location of exhaust outlets | New section requiring specific termination points for exhaust outlet based upon the type of exhaust. |
| 502.4 | Stationary lead-acid battery systems | 502.4 | Stationary storage battery systems | Scope of section revised to refer to the FFPC for regulation of stationary storage battery system. |
|  |  |  |  | Added exception: Lithium-ion batteries do not require ventilation. |
| 502.4.1 | Hydrogen limit in rooms | 502.4.1 | Hydrogen limit in rooms | Scope of section revised to include flooded lead acid, flooded nickel cadmium and VRLA batteries. |
| 502.5 | Valve-regulated lead-acid batteries in cabinets | 502.5 | Valve-regulated lead-acid batteries in cabinets | Scope of section revised to apply to VRLA batteries installed in cabinets. |
| 502.5.1 | Hydrogen limit in rooms | - | - | Section deleted. Provisions covered in Section 502.4. |
| 502.5.2 | Ventilation rate in rooms | - | - | Section deleted. Provisions covered in Section 502.4. |
| 502.5.3 | Hydrogen limit in cabinets | 502.5.1 | Hydrogen limit in cabinets | Relocated section - no change in content. |
| 502.5.4 | Ventilation rate in cabinets | 502.5.2 | Ventilation rate in cabinets | Relocated section - no change in content. |
| 502.7.3.2 | Recirculation | 502.7.3.2 | Recirculation | Item 1.5 has been reworded for clarity and apply to 100 percent of the air volume specified in Section 510. |
| 502.7.3.6 | Termination point | - | - | Deleted section. Information no longer applicable to this section. |
| 502.8.1.1 | System requirements | 502.8.1.1 | System requirements | Item 4 revised to include "other approved type" in addition to the break-glass switch. Item 5 revised to require that for fumes or vapors lighter than air, the exhaust is required to be taken from a point within 12 inches of the highest point in the room. Item 7 revised to clarify exhaust ventilation can not be recirculated to occupied areas. Air contaminated with explosive or flammable vapors, fumes or dusts; flammable, highly toxic or toxic gases; or radioactive materials are not permitted to be recirculated. |
| 502.8.4 | Indoor dispensing and use - point sources | 502.8.4 | Indoor dispensing and use - point sources | Revised section language to add "gasses" for inclusion with vapors and fumes regarding flammability. |
| 502.10.1 | Hazardous production materials (HPM) | 502.10.1 | Hazardous production materials (HPM) |  |
| 502.16.1 | Design | 502.16.1 | Design | Section revised to add wider range of gases being used in addition to natural gas. |
| - | - | 502.19 | Indoor firing ranges | Added section to address firing ranges and provide design guidance with ventilation reference for OSHA 29 CFR 1910.1025 where applicable. |
|  |  | 504.6 | Domestic clothes dryer ducts. | Delete existing duplicative text in section and substitute the following: Exhaust ducts for domestic clothes dryers shall be constructed of metal and shall have a smooth interior finish. The exhaust duct shall be a minimum nominal size of 4 inches (102 mm) in diameter. The entire exhaust system shall be supported and secured in place. The male end of the duct at overlapped duct joints shall extend in the direction of airflow. Clothes dryer transition ducts used to connect the appliance to the exhaust duct system shall be limited to single lengths not to exceed 8 feet (2438 mm) and shall be listed and labeled for the application. Transition ducts shall not be concealed within construction. |
|  |  | 504.6.1 | Maximum length. | Add Exception 2 to correct requirement for dyer booster fans. The maximum length of a clothes dryer exhaust duct shall not exceed 25 feet (7620 mm) from the dryer location to the outlet terminal. The maximum length of the duct shall be reduced 21/2 feet (762 mm) for each 45 degree (0.79 rad) bend and 5 feet (1524 mm) for each 90 degree (1.6 rad) bend. The maximum length of the exhaust duct does not include the transition duct. Exception: - No change. - Where a clothes dryer booster fan is installed and listed and labeled for the application, the maximum length of the exhaust duct, including any transition duct, shall be permitted to be in accordance with the booster fan manufacturer’s installation instructions. Where a clothes dryer booster fan is installed and not readily accessible from the room in which the dryer is located, a permanent identifying label shall be placed adjacent to where the exhaust duct enters the wall. The label shall bear the words: “This dryer exhaust system is equipped with a remotely located booster fan.” |
| 505.1 | Domestic systems | 505.1 | Domestic systems | Revised section to specifically refer to sheet metal ducts to avoid confusion regarding possible use of flex duct. |
| 506.3.2 | Joints, seams and penetrations of grease ducts | 506.3.2 | Joints, seams and penetrations of grease ducts | Exception 3 revised to require factory-built commercial kitchen grease ducts to be listed and labeled in accordance with UL 1978 |
| - | - | 506.3.2.5 | Grease duct test | New section requiring a leakage test of the grease duct prior to use or concealment. |
|  |  | 506.2.5 | Grease duct test | Move to Section 506.3.3.1 |
| 506.3.4 | Air velocity | 506.3.4 | Air velocity | Revised section to provide a minimum (1,500) and a maximum (2,500) feet per minute for air velocity. |
| 506.3.10 | Duct enclosure | 506.3.10 | Duct enclosure | Exception 1 revised to require evaluation in accordance with ASTM E 236 for the specified conditions. Requires exposed ductwrap systems to be protected where subject to physical damage. New Exception 2 added providing an additional exception to the shaft enclosure provisions in accordance with the requirements specified. |
| 506.3.12.3 | Termination location | 506.3.12.3 | Termination location | Revised section to add "adjacent buildings" to description of locations. Also revised exception to add "parts of the same or contiguous building" - for added clarity to the location description. |
| 506.5.5 | Termination location of exhaust equipment | 506.5.5 | Termination location of exhaust equipment | Revised reference standard from "506.3.12.3" to "506.3.12." |
| 507.1 | General | 507.1 | General | Revised section to provide requirement of commercial hood system to operate during cooking. |
| - | - | 507.2.1.1 | Operation | Added new section requiring that Type I hoods be designed to automatically activate the exhaust fan during cooking operation. |
| 507.2.2 | Type II hoods | 507.2.2 | Type II hoods | Revised section to add products of combustion to scope of where Type II hoods are required. New Exception 3 provided for a single light-duty electric convection, bread, retherm or microwave oven. New Exception 4 provides a list of specific appliances (toasters, popcorn poppers, etc.) that do not require a Type II hood. |
| 507.2.4 | Solid fuel | 507.2.4 | Extra-heavy-duty | Revised title from "solid fuel" to "extra-heavy-duty" which utilizes the correct term for this section. Also added information regarding type I hoods for other appliances. |
| 507.12 | Canopy size and location | 507.12 | Canopy size and location | Section revised to specifically include canopy-type Type I and II commercial hoods within scope of section. Revision eliminates reference to "cooking surface" to avoid confusion of applications such as surfaces over dishwashers which are not used for cooking. |
| 507.13 | Capacity of hoods | 507.13 | Capacity of hoods | Revised section to remove "extra-heavy-duty" from combinations of appliances listed since it isn't applicable to the requirements of this section. |
| - | - | 507.13.5 | Dishwashing appliances | Added new section to accommodate air flow information currently missing on dishwasher appliance installations. |
| 507.16.1 | Capture and containment test | 507.16.1 | Capture and containment test | Revised section to add requirements such that the test is performed under actual conditions. |
|  |  | 508.1.1 | Makeup air temperature | Florida Specific Amendment text removed in 2004. Delete text in Section 508.1.1 and mark section as “Reserved”. |
| 510.1 | General | 510.1 | General | Revised section to add definition of laboratory for the purpose of laboratory ventilation systems to clarify scope for this section. |
| 510.2 | Where required | 510.2 | Where required | Exception to this section added for laboratories with further restrictions specified. |
| 510.4 | Independent system | 510.4 | Independent system | Exception provided for laboratories meeting the 7 listed criteria. |
| - | - | 510.6.1 | Fire dampers | Added new section reinstating language previously removed but still referred to and is still pertinent. |
| 510.7 | Suppression required | 510.7 | Suppression required | Revised section to add new Exception 3 that states in laboratory hoods and exhaust systems, automatic fire protection systems are not required. |
| 511.1.1 | Collectors and separators | 511.1.1 | Collectors and separators | Revised section to remove the term "cyclone" as a description of separator. Revision also adds types of systems for clarification. New Exception 2 added permitting collectors in independent exhaust systems handling combustible ducts to be installed indoors. |
| 511.1.1 | Collectors and separators | 511.1.1 | Collectors and separators | Editorial correction change “with” to “within” in last line. |
| 511.1.3 | Conveying systems exhaust discharge | 511.1.3 | Conveying systems exhaust discharge | Revised section to add statement for exhaust system that discharge can be recirculated if compliance with section is met. |
| 511.2 | Exhaust outlets | 511.2 | Exhaust outlets | Relocated Item 3 to Section 401.4 |
| 513 | Smoke Control Systems | 513 | Smoke Control Systems | Revise Title to read: “Smoke and Carbon Monoxide Control Systems” |
| 513.1 | Scope and purpose | 513.1 | Scope and purpose | Scope of section revised to specifically apply to high-rise buildings. |
| 513.3 | Special Inspection and test Requirements | 513.3 | Special Inspection and test Requirements | Change reference in section from FBC-B 1704 to FBC-B 909.18. |
| 513.4.6 | Duration of operation | 513.4.6 | Duration of operation | Section revised to require continued operation of smoke control of smoke control system not less than 1.5 times the calculated egress time, in addition to the existing time of 20 minutes. |
| 513.8 | Exhaust method | 513.8 | Exhaust method | Revised section to add reference to NFPA 92B. |
| 513.8.1 | Exhaust rate | 513.8.1 | Exhaust rate | Revised height of accumulated smoke layer from 10 feet to 6 feet. |
| 513.8.2 | Axisymmetric plumes | - | - | Sections deleted. |
| 513.8.3 | Balcony spill plumes | - | - |  |
| 513.8.4 | Window plumes | - | - |  |
| 513.9 | Design fire | 513.9 | Design fire | Section revised to require the design fire to be based on a rational analysis. |
| 513.9.2 | Design fire fuel | 513.9.2 | Design fire fuel | Section revised to simply require that the determination of the design fire to include consideration of the type of fuel, fuel spacing and configuration. |
| 513.12 | Detection and Control Systems | 513.12 | Detection and Control Systems | Renumber 513.12 to create 2 parts: 513.12.1 Fire Detection Systems 513.12.2 Carbon Monoxide Control Systems and add reference to FBC-B 913. 513.12.1 Fire detection systems. Fire detection systems providing control input or output signals to mechanical smoke control systems or elements thereof shall comply with the requirements of Chapter 9 of the Florida Building Code, Building and NFPA 72. Such systems shall be equipped with a control unit complying with UL 864 and listed as smoke control equipment. Control systems for mechanical smoke control systems shall include provisions for verification. Verification shall include positive confirmation of actuation, testing, manual override, the presence of power downstream of all disconnects and, through a preprogrammed weekly test sequence report, abnormal conditions audibly, visually and by printed report. [F] 513.12.1.1 Wiring. In addition to meeting the requirements of Chapter 27 of the Florida Building Code, Building, all wiring, regardless of voltage, shall be fully enclosed within continuous raceways. [F] 513.12.1.2 Activation. Smoke control systems shall be activated in accordance with the Florida Building Code, Building. [F] 513.12.1.3 Automatic control. Where completely automatic control is required or used, the automatic control sequences shall be initiated from an appropriately zoned automatic sprinkler system complying with the Florida Fire Prevention Code or from manual controls that are readily accessible to the fire department, and any smoke detectors required by engineering analysis. 513.12.2 Carbon monoxide control systems. See Section 913 of the Florida Building Code, Building. |
| 513.20 | Underground building smoke exhaust system | - | - | Sections deleted. |
| 513.20.1 | Exhaust capability | - | - |  |
| 513.20.2 | Operation |  |  |  |
| 513.20.3 | Alarm required | - | - |  |
| Table 515.2B | Crypt Pressure relief pipe | Table 515.2B | Crypt pressure relief fittings | Revised title from "Crypt Pressure Relief Pipe" to "Crypt Pressure Relief Fittings." |
| 515.3 | Pressure relief vent | 515.3 | Pressure relief vent | For family mausoleum units, where all crypts are bordering an exterior wall, pressure relief ventilation is to be provided from the crypt to the outside of the mausoleum through the exterior wall or roof. |
| 515.4 | Termination | 515.4 | Termination | For family mausoleum units, where all crypts are bordering an exterior wall, pressure relief ventilation is to be provided from the crypt to the outside of the mausoleum through the exterior wall or roof. |
| Chapter 6: Duct Systems |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| 601.2 | Air movement in egress elements | 601.2 | Air movement in egress elements | Revised language in section to remove term "exit access" for consistency. |
| - | - | 602.2.1.6 | Semiconductor fabrication areas | New section essentially providing an exception for Group H, Division 5 fabrication areas within limitations specified. |
|  |  | 603.8 | Cavities of the building structure. | Remove the reference to method C in the Energy code as it no longer applicable Cavities in framed spaces, such as dropped soffits and walls, shall not be used to deliver air from or return air to the conditioning system unless they contain an air duct insert which is insulated in accordance with Table 13-410.1.ABC.2.2 or Table 13-610.1.ABC.2.1 of Chapter 13 of the Florida Building Code, Building and constructed and sealed in accordance with the requirements of Section 603.1 appropriate for the duct materials used. Exception: Return air plenums. Cavities designed for air transport such as mechanical closets, chases, air shafts, etc. shall be lined with an air barrier and sealed in accordance with Section 603.9 and shall be insulated in accordance with Table 13-410.1.ABC.2.2 or Table 13-610.1.ABC.2.1 of Chapter 13 of the Florida Building Code, Building. Building cavities which will be used as return air plenums shall be lined with a continuous air barrier made of durable non-porous materials. All penetrations of the air barrier shall be sealed with a suitable long-life mastic material. Exception: Surfaces between the plenum and conditioned spaces from which the return/mixed air is drawn. Building cavities beneath a roof deck that will be used as return air plenums shall have an insulated roof with the insulation having an R-value of at least R-19. |
|  |  | 603.10 | Enclosed support platforms. | Remove the reference to method C in the Energy code as it no longer applicable. Enclosed support platforms located between the return air inlet(s) from conditioned space and the inlet of the air handling unit or furnace, shall contain a duct section constructed entirely of rigid metal, rigid fibrous glass duct board, or flexible duct which is constructed and sealed according to the respective requirements of Section 603.1 and insulated according to the requirements of Section 13-410.1.ABC.2.2 and 13-610.1.ABC.2.1 of Chapter 13 of the Florida Building Code, Building. ● The duct section shall be designed and constructed so that no portion of the building structure, including adjoining walls, floors and ceilings, shall be in contact with the return air stream or function as a component of this duct section. ● The duct section shall not be penetrated by a refrigerant line chase, refrigerant line, wiring, pipe or any object other than a component of the air distribution system. ● Through-wall, through-floor and through-ceiling penetrations into the duct section shall contain a branch duct which is fabricated of rigid fibrous glass duct board or rigid metal and which extends to and is sealed to both the duct section and the grille side wall surface. The branch duct shall be fabricated and attached to the duct insert in accordance with Section 603.3 or Section 603.4.2, respective to the duct type used. |
| 603.14 | Weather protection | 603.16 | Weather protection | Revised section to remove ambiguous term "adequately." |
| 603.17 | Registers, grilles and diffusers | 603.17 | Registers, grilles and diffusers | "Branch" dampers changed to "Volume" dampers. New language requiring volume dampers or other means of supply air to be provided with access. |
| - | - | 603.17.2 | Prohibited locations | New section limiting the location of diffusers, registers, and grilles in toilet and bathing room floors. |
| 604.3 | Coverings and linings | 604.3 | Coverings and linings | Requires the use of the preparation and mounting procedures of ASTM 2231 when conducting the ASTM E 84 test for flame spread index and smoke development. |
| 606.1 | Controls required | 606.1 | Controls required | New language requiring duct smoke detectors to comply with UL 268A and other smoke detectors to comply with UL 268. |
| 607.1 | General | 607.1 | General | Revised section to remove "fire-resistance-rated" since scope of section addresses assemblies beyond this type. |
| 607.1.1 | Ducts and air transfer openings without dampers | 607.1.1 | Ducts without dampers | Revised title and section to remove "air transfer openings" due to incongruity in the provisions for the penetration of fire-resistance-rated walls and horizontal assemblies by ducts and air transfer openings. |
| 607.2 | Installation | 607.2 | Installation | Editorial revision to remove term "radiation" for continuity of word usage throughout this chapter. |
| 607.3.2.1 | Smoke damper actuation methods | 607.3.2.1 | Smoke damper actuation methods | Revised Item 4 to add wall "or ceiling" since on occasion, smoke dampers may be installed in ceiling area. |
| 607.4 | Access and identification | 607.4 | Access and identification | Revised required labeling in this section to add, "Fire/smoke damper" to ensure proper labeling of access doors. |
| 607.5 | Where required | 607.5 | Where required | Revised reference sections from "this section" to "Sections 607.5.1 through 607.5.5." |
| 607.5.1 | Fire walls | 607.5.1 | Fire walls | Revised term "approved" to state "listed" regarding fire dampers. |
| 607.5.2 | Fire barriers | 607.5.2 | Fire barriers | Revised term "approved" to state "listed" regarding fire dampers. New language clarifies that ducts and air transfer openings are not permitted to penetrate exit enclosures or exit passageways except as permitted in the FBCB. |
| 607.5.3 | Fire partitions | 607.5.3 | Fire partitions | Revised title and section scope to add "air transfer openings." New Exception 2 added permitting penetrations of fire partitions without a fire damper provided the partitions are tenant partitions in covered mall buildings where the walls are not required to extend to the underside of the floor or roof deck above. |
| 607.5.5 | Shaft enclosures | - | - | Provisions moved to more appropriate location in Section 607.5.2 since shaft enclosure walls are required to be fire barriers. |
| 607.5.5.1 | Penetrations of shaft enclosures | 607.5.5 | Shaft enclosures | Relocated section and revised title. Changed "approved" fire and smoke dampers to "listed" fire and smoke dampers. Revisions provide clarity and consistency with other changes regarding shaft enclosures as fire barriers. |
| 607.6 | Horizontal assemblies | 607.6 | Horizontal assemblies | Language revised to permit compliance with Sections 716.6.1 through 716.6.3 FBCB or with Section 607.6.1 through 607.6.3 in the FBCM. |
| 607.6.1 | Through penetrations | 607.6.1 | Through penetrations | Revised scope to include individual specific requirements for ducts and specific requirements for air transfer openings. New language that permits the duct to be protected in accordance with Section 712.4 of the FBCB in lieu of a shaft enclosure, within the scope of this section. New language refers to Exception 7 of Section 702.2 in the FBCB for air transfer openings. |
| 607.6.2 | Membrane penetrations | 607.6.2 | Membrane penetrations | Revised entire section to totally reorganize existing requirements from a paragraph format to an itemized (adds items 1-3) list of protection methods. Reorganization also added new section 607.6.2.1 to accommodate information regarding ceiling radiation dampers. |
| - | - | 607.6.2.1 | Ceiling radiation dampers |  |
| 607.6.3 | Nonfire-resistance-rated assemblies | 607.6.3 | Nonfire-resistance-rated assemblies | Revised title to add "floor" to better provide intent of section. Revised entire section to totally reorganize existing requirements from a paragraph format to an itemized (adds items 1-3) list of protection methods. |
| Chapter 7: Combustion Air |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| 702.3 | Air from adjacent spaces | 702.3 | Air from adjacent spaces | Revised section to make editorial change in effort to replace "inside" with "indoor" (and outside with outdoor) throughout the code. Similar changes made elsewhere in Chapter 7. |
| Chapter 8: Chimneys and Vents |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| 804.3.5 | Vertical terminations | 804.3.5 | Vertical terminations | Revised section to clarify method of measurement by adding the term "horizontally" to Item 2. |
| 805.2 | Solid fuel appliances | 805.2 | Solid fuel appliances | Revised section to add requirement for marking of factory-built chimneys to be marked appropriately for distinction between Type HT and non-Type HT chimneys. Existing exception deleted. New Exception 1 requires chimneys for use with open combustion chamber fireplaces to comply with UL 103 and to be marked "Residential Type and Building Heating Appliance Chimney." Exception 2 addresses chimneys for use with open combustion chamber appliances installed in buildings other than dwelling units. |
| Chapter 9: Specific Appliances, Fireplaces and Solid Fuel Burning Equipment |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| 904.1 | General | 904.1 | General | Revised section to add reference to ASTM E 1509. |
| 912.1 | Support | 912.1 | Support | Revised section to remove vague and unenforceable terms "safely and adequately" from this section. |
| 924 | Stationary fuel cell power plants | 924 | Stationary fuel cell power systems | Editorial revision in title to replace "plants" with "systems" to maintain consistency with ANSI standards. |
| 924.1 | General | 924.1 | General | Revised section to replace "plants" with "systems" and include reference to ANSI CSA America FC 1 standard. Revised output designation of "1,000 kW" to "10 MW." |
| - | - | 931 | Gaseous hydrogen systems | New section requiring the installation of gaseous hydrogen systems to be in accordance with applicable requirements of the FBCM, FFPC, FBCFG, and FBCB. |
| Chapter 10: Boilers, Water Heaters and Pressure Vessels |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| 1002.2.2 | Scald protection | 1002.2.2 | Temperature limitation | Revised title of section for better description of scope. Also revised term "tempering valve" to match ASSE reference standard to "temperature actuated mixing valve." |
|  |  | 1003.1 | General | Date of the referenced documents belongs in Chapter 15 All pressure vessels shall bear the label of an approved agency and shall be installed in accordance with the manufacturer’s installation instructions. Pressure vessels shall be designed and stamped per ASME Boiler and Pressure Vessel Code, Section VIII-Division 1, Division 2, or Division 3. |
| 1004.1 | Standards | 1004.1 | Standards | Revised section to remove reference to Sections II V and IX due to error as they do not pertain to the design and construction of boilers. |
| Chapter 11: Refrigeration |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| 1105.5 | Fuel-burning appliances | 1105.5 | Fuel-burning appliances | Revised to add, "fuel-burning appliances and equipment" to the scope for clarity. Deleted exception for matches, lighters, halide leak detectors and similar devices. |
| - | - | 1105.9 | Emergency pressure control system | New section requiring an emergency pressure control system for refrigeration systems containing more than 6.6 pounds of flammable, toxic or highly toxic refrigerant or ammonia. |
| 1106.3 | Ammonia room ventilation | 1106.3 | Ammonia room ventilation | Revised section to add reference to 1105.6.4 and the emergency ventilation rate. |
| 1106.5.1 | Refrigeration system | 1106.5.1 | Refrigeration system | Added exception stating that the cutoff switch is not required for machinery rooms where only nonflammable refrigerants are used, electrical equipment and appliances, other than compressors. |
| Chapter 12: Hydronic Piping |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| 1203.3.7 | Grooved and shouldered joints | 1203.3.7 | Grooved and shouldered joints | Revised title and section content to add the term "mechanical" for proper piping term. Revised to add reference to ASTM F 1476 standard. Removed the term approval since it implies that the mechanical joints require an approval above the section requirements. |
| 1204.1 | Insulation characteristics | 1204.1 | Insulation characteristics | Revised section to add additional ASTM E 2231 standard to address specimen preparation procedures. |
| 1206.9.1 | Flood hazard | 1206.9.1 | Flood hazard | New section requiring piping located in a flood hazard area to be capable of resisting hydrostatic and hydrodynamic loads and stresses during flooding. |
|  |  | 1206.9.1 | Flood hazard | Refer all flood requirement back to Chapter 3 See Section 301.13. |
| Chapter 13: Fuel Oil Piping and Storage |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| - | - | 1301.5 | Tanks abandoned or removed | Added new section to address possible dangers that occur with abandoned tanks, such as accidentally delivery. Section requires compliance of removal per the Florida Fire Prevention Code. |
|  |  |  |  | Refer all flood requirement back to Chapter 3 Section 1305.2.1 Flood hazard. See Section 301.13. |
| Chapter 15: Referenced Standards |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
|  |  |  |  | NFPA 30A—03 Code for Motor Fuel-dispensing Facilities and Repair Garages . . . . . . . . ………………….. . . . . . .304.5 86-03 Standard for Ovens and Furnaces. . . . . .924.1 90B-06 Standard for the Installation of Warm Air Heating and Air Conditioning Systems ………... 301.15 91—04 Exhaust Systems for Air Conveying of Vapors, Gases, Mists and Noncombustible Particulate Solids .. . …………………………………….…….502.9.5.1, 502.17 96-04 Ventilation Control and Fire Protection of Commercial Cooking Operations . . …………...... .506.1 214-05 Standard on Water Cooling Towers . . .908.1 |

End of Document