| Plumbing Code with “2009 Supplement” |  |  |  |  |
| --- | --- | --- | --- | --- |
| 2004 FBCP |  | 2007 FBCP |  | Analysis |
| Section | Requirement | Section | Requirement |  |
| Preface |  |  |  |  |
|  |  | Preface | Adds missing language to the preface from the 2006 International Codes which explains the letters in brackets at the beginning of the paragraphs. Add text after the section, Adoption and Maintenance, to read as follows: Letter Designations in Front of Section Numbers In each code development cycle, proposed changes to the code are considered at the Code Development Hearings by the ICC Fire Code Development Committee, whose action constitutes a recommendation to the voting membership for final action on the proposed change. Proposed changes to a code section that has a number beginning with a letter in brackets are considered by a different code development committee. For example, proposed changes to code sections that have [F] in front of them (e.g. [F] 903.1.1.1) are considered by the ICC Fire Code Development Committee at the code development hearings. The content of sections in this code that begin with a letter designation are maintained by another code development committee in accordance with the following: [E] = International Energy Conservation Code Development Committee; [EB] = International Existing Building Code Development Committee; [EL] = ICC Electrical Code Development Committee; [F] = International Fire Code Development Committee; [FG] = International Fuel Gas Code Development Committee; [M] = International Mechanical Code Development Committee; and [P] = International Plumbing Code Development Committee. |  |
| Chapter 2: Definitions |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| 202 | Approved | 202 | Approved | Revised definition to change the term "approved" to "acceptable" to avoid using the defined term in the definition itself. |
| 202 | Branch interval | 202 | Branch interval | Definition was revised to a more current explanation based on industry standards and to provide a more specific definition. |
| 202 | - | 202 | Flow Control | Added new definition needed to define terms referenced through ASME and throughout the code. |
| 202 | - | 202 | Automatic grease removal device (GRD) | Added new definition needed to define terms referenced through ASME and throughout the code. |
| 202 | - | 202 | Gridded water distribution system | Added new definition for consistency with additions throughout code to provide an alternative design methods for water distribution. |
| Chapter 3: General Regulations |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
|  |  | 305.1 | Corrosion | Change to make Plumbing Code consistent with Sec. 1816.2 of FBC-B. Correct thickness of sleeving material. Pipes passing through concrete or cinder walls and floors or other corrosive material shall be protected against external corrosion by a protective sheathing or wrapping or other means that will withstand any reaction from lime and acid of concrete, cinder or other corrosive material. Sheathing or wrapping shall allow for expansion and contraction of piping to prevent any rubbing action. Minimum wall thickness of material shall be 0.010 inch (0.64 mm). Exception: Sleeving is not required for installation of CPVC into concrete or similar material |
| - | - | 305.1.2 | Penetration. | Change to make Plumbing Code consistent with Sec. 1816.2 of FBC-B Add new section to prohibit application of termiticides inside of sleeve. Protective sleeves around piping penetrating concrete slab-on-grade floors shall not be of cellulose-containing materials. If soil treatment is used for subterranean termite protection, the sleeve shall have a maximum wall thickness of 0.010 inch, and be sealed within the slab using a non-corrosive clamping device to eliminate the annular space between the pipe and the sleeve. No termiticides shall be applied inside the sleeve. |
| Table 308.5 | Hanger spacing | Table 308.5 | Hanger spacing | Revised table to add polypropylene piping materials to allowance in hot and cold water distribution piping systems. |
| 308.9 | Stacks | - | - | Deleted section to remove duplicate provision, since stacks are covered in other sections of this chapter. |
| - | - | 310.5 | Urinal partitions | Added new section to update requirements for privacy partitions used at urinal stations to possibly save water when users would utilize a water closet at times when there's not a space available at urinals. |
| 312.9.2 | Backflow testing | 312.9.2 | Backflow testing | Revised section to add reference to CSA B64.10.1, an alternative and specific reference for backflow preventers. |
| 314.2.3 | Auxiliary and secondary drain systems | 314.2.3 | Auxiliary and secondary drain systems | Scope of Section revised clarify when auxiliary drain is required. Revised section to include requirement of compliance to UL 508, which adds a reference standard for water level detection devices. |
|  |  | 314.2.3 | Auxiliary and secondary drain systems. | Make FBC-P consistent with FBC-M. These are Florida Specific Amendments. Delete paragraph 4 with the exception. |
| - | - | 314.2.3.1 | Water level monitoring devices | New section permitting the use of a water level monitoring device within the limitations prescribed. |
| Chapter 4: Fixtures, Faucets and Fixture Fittings |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| Table 403.1 | Minimum number of required plumbing fixtures | Table 403.1 | Minimum number of required plumbing fixtures | Revised No. 2 Business - number of lavatories changed to 1 per 40 for the first 80 and 1 per 80 for the remainder exceeding 80. Revised table to remove footnote e. This footnote is duplicated in the R-2 and R-3 occupancy portion of the table and therefore not required as a footnote. |
|  |  | Table 403.1 | Minimum number of required plumbing fixtures | Remove from table in Assembly occupancies the column requiring bathtubs/showers. Editorial change to be consistent with base code. |
| 403.1.1.2 | Occupancy content calculation | 403.1.1.2 | Occupancy content calculation | Revised section to modify "building code in effect in a jurisdiction" to now state, "Florida Building Code, Building." |
| 403.4 | Location of employee toilet facilities in occupancies other than assembly or mercantile | 403.4 | Required public toilet facilities | Provisions of Sections 403.4 through 403.6.1 have been reformatted and combined for clarity and simplicity. |
| - | - | 403.4.1 | Location of toilet facilities in occupancies other than covered malls | Added new information for this section to address locations and travel distances. |
| 403.6.1 | Covered malls | 403.4.2 | Location of toilet facilities in covered malls | Relocated section and added new information for this section to address locations and travel distances. |
| 403.5 | Location of employee toilet facilities in mercantile and assembly occupancies | - | - | Deleted section - information is addressed in new section 403.4.1. |
| 405.3.1 | Water closets, urinals, lavatories and bidets | 405.3.1 | Water closets, urinals, lavatories and bidets | Revised language to a better format for clarity. |
| 405.4 | Floor and wall drainage connections | 405.4 | Floor and wall drainage connections | Removed reference to the discontinued standard: FS TT P 1536a. |
| 406.3 | Waste connection | 406.3 | Waste connection | Revised section to address washers that discharge by gravity to allow use of this appliance. Previous wording would not permit the use of gravity discharge washers. |
| - | - | 408.3 | Bidet water temperature | Added new section for bidet installations and provisions for water temperature safety. |
| 412.2 | Floor drains trap and strainer | 412.2 | Floor drain | Revised section to remove area requirement of floor drains since ASME provides specifications. |
| - | - | 416.5 | Tempered water for public hand-washing facilities | Added new section for provisions of public hand-washing installations and water temperature safety. |
| 417.4 | Shower compartments | 417.4 | Shower compartments | Revised section to add exception in this section regarding size requirements for shower replacements. Change is needed to accommodate the increasing trend by owners to convert bathtubs with shower receptors. |
| - | - | 417.4.2 | Access | Added new section to address the need to provide a specific provision for shower compartment opening sizes for consistency with enforcement. |
| 419.1 | Urinals - approval | 419.1 | Urinals - approval | Revised section to add ANSI Z124.9 to provide conformance standard for waterless urinals. |
| 419.2 | Substitution for water closets | 419.2 | Substitution for water closets | Revised section to reword intent pertaining to urinals and water closets in assembly and educational occupancies versus other occupancies. This change allows 2/3 substitution of the water closets in assembly and educational occupancies. |
| 421.2 | Whirlpool bathtub installations | 421.2 | Whirlpool bathtub installations | Revised section to remove requirement to have access to the pump; information is now detailed and included in 421.5. |
| - | - | 421.5 | Access to pump | Added section to provide size and location provisions for access panels for access to pumps in whirlpool tubs. |
| 424.1.2 | Waste fittings | 424.1.2 | Waste fittings | Removed duplicate wording to standards and added reference to the new ASME A112.18.2 standard for fittings as well as the comparative CSA standard B125. |
| 424.2 | Hand showers | 424.2 | Hand showers | Section revised to require backflow prevention for hand-held showers. |
| 424.3 | Individual shower valves | 424.3 | Individual shower valves | Revised section to remove (and relocate) information regarding multiple (gang) showers. |
|  |  |  |  | Added statement regarding non-compliance of in-line thermostatic valves for this application. |
| - | - | 424.4 | Multiple (gang) showers | Added new section to include information from 424.3 and additional provisions and reference standards for gang showers. |
| - | - | 424.5 | Bathtub and whirlpool bathtub valves | Added new section for provisions of bathtub and whirlpool bathtub installations and water temperature safety. |
| 424.4 | Hose-connected outlets | 424.6 | Hose-connected outlets | Relocated section and revised to add reference to CSA B125 as alternative compliance standard. |
| Chapter 5: Water Heaters |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| 502.4 | Seismic supports. Reserved | 502.4 | Water heaters installed in attics. | Prescribes the space requirements for water heaters located in attics. Sufficient space must be provided for servicing appliance and removal. Revise text to read as follows: Attics containing a water heater shall be provided with an opening and unobstructed passageway large enough to allow removal of the water heater. The passageway shall not be less than 30 inches high and 22 inches wide and not more than 20 feet in length when measured along the centerline of the passageway from the opening to the water heater. The passageway shall have continuous solid flooring not less than 24 inches wide. A level service space at least 30 inches deep and 30 inches wide shall be present at the front or service side of the water heater. The clear access opening dimensions shall be a minimum of 20 inches by 30 inches where such dimensions are large enough to allow removal of the water heater. |
| 504.6 through 504.6.2 | Relief outlet waste | 504.6 | Requirements for discharge piping | Deleted section to reorganize into a new section 504.6. Reorganization of the information provides a breakdown of 13 requirements in a more user friendly format. Additional requirements include: -Requires the discharge piping to terminate not more than 6 inches above the floor or waste receptor. -Prohibits the discharge piping from having a threaded connection -Discharge piping cannot be directly connected to the drainage system -Prohibits the use of valves or tee fittings |
| 504.7.1 | Pan size and drain | 504.7.1 | Pan size and drain | Revised section to add reference to Table 605.4 for list of applicable materials. |
| Chapter 6: Water Supply and Distribution |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| Table 603.1 | Minimum Water Service Size | Table 603.1 | Minimum Water Service Size | Editorial Change. Correct typo in table where in the third row it reads 56-58 it should read 56-85. |
| 604.4 | Maximum flow and water consumption | 604.4 | Maximum flow and water consumption | Revised section exceptions 1 and 3 editorially to clarify maximum consumptions. |
| 604.5 | Size and fixture supply | 604.5 | Size and fixture supply | Revised section(s) to add the term "gridded" water distribution for application to this section and for continuity with additions to the code. |
| 604.10 | Parallel water distribution system | 604.10 | Gridded and parallel water distribution system |  |
| 605.3 | Water service pipe | 605.3 | Water service pipe | Revised section to clarify termination point by eliminating the reference to 5 feet and adding "before the full open valve" for a more specific location. |
| Table 605.3 | Water service pipe | Table 605.3 | Water service pipe | Revised table to include polypropylene and cross-linked polyethylene materials and referenced appropriate reference standards. |
| Table 605.4 | Water distribution pipe | Table 605.4 | Water distribution pipe |  |
| Table 605.5 | Pipe fittings | Table 605.5 | Pipe fittings |  |
| 605.3.1 | Dual check-valve-type backflow preventer | 605.3.1 | Dual check-valve-type backflow preventer | Revised section to provide additional reference to CAN/CSA-B64.6 as an additional compliance for backflow preventers. |
| 605.7 | Valves | 605.7 | Valves | Revised section to extend the NSF 61 standard (currently required for water distribution pipe and fittings) to valves. |
| 605.17.2 | Mechanical joints | 605.17.2 | Mechanical joints | Revised section to add ASTM F 877 to provided references to address added polyethylene materials. |
| - | - | 605.21 | Polypropylene (PP) plastic | Added new sections providing information for allowance of polypropylene (PP) joints. |
| - | - | 605.21.1 | Heat-fusion joints |  |
| - | - | 605.21.2 | Mechanical and compression sleeve joints |  |
| 606.2 | Location of shutoff valves | 606.2 | Location of shutoff valves | Revised exception to replace the term "construction" with "occupancies" for an appropriate description of residential use. |
| 606.3 | Access to valves | 606.3 | Access to valves | Revised section to remove the word "required" due to the term being misleading for this particular section by presenting a situation where a valve may be installed by choice instead of being required and then not providing access. |
| 606.5.4 | Overflows for water supply tanks | 606.5.4 | Overflows for water supply tanks | Editorial change to replace confusing language regarding discharge location. |
| 607.1 | Where required | 607.1 | Where hot or tempered water is required | New language requires tempered water to be supplied through a water temperature limiting device that conforms to ASSE 10170 limiting the tempered water to a maximum of 110° F. |
| Table 607.1 | Minimum Pipe Insulation Domestic and Service hot water Circulating Systems | Table 607.1 | Minimum Pipe Insulation Domestic and Service hot water Circulating Systems | Delete Table 607.1 This table reflects an old version of energy code requirements. It should either be updated to reflect Table 13-411.ABC.2 of the FBC-B or reference the appropriate table and sections in the FBC-B for code consistency. |
| 607.2.1 | Circulating Systems | 607.2.1 | Minimum pipe insulation | Revise title, Insert New Table 607.2.1 and change text to read:: Circulating hot water piping and domestic and service hot water systems with fluid design operating temperatures greater than 105oF shall be insulated in accordance with the requirements of Table 607.2.1. (See Table in Attachment) |
| 607.4 | Flow of hot water to fixtures | 607.4 | Flow of hot water to fixtures | Also revised exception to include approved reference standard for shower and tub/shower mixing valves - CSA B125. |
| Table 608.1 | Application for Backflow preventers | Table 608.1 | Application for Backflow preventers | Revised column "applicable standards" within the table to include applicable CSA standards. |
| 608.2 | Plumbing fixtures | 608.2 | Plumbing fixtures | Revised to require backflow protection in accordance with ASME A112.18.1. |
| 608.13.2 | Reduced pressure principle backflow preventers | 608.13.2 | Reduced pressure principle backflow preventers | Section revised to delete reference to CAN/CSA-B643 and replace with CSA B64.4 and CSA B64.4.1 for reduced pressure principal backflow preventers. |
| 608.13.5 | Pressure-type vacuum breakers | 608.13.5 | Pressure-type vacuum breakers | Revised section to provide additional reference to CAN/CSA-B64.1.2 as an additional compliance for pressure-type vacuum breakers.. |
| 608.13.6 | Atmospheric-type vacuum breakers | 608.13.6 | Atmospheric-type vacuum breakers | Revised section to provide additional reference to CAN/CSA-B64.2.1 and B64.2.1.1 as an additional compliance for hose-connection vacuum breakers. |
| 608.13.7 | Double check-valve assemblies | 608.13.7 | Double check-valve assemblies | Revised section to provide additional reference to CAN/CSA-B64.5 and B64.5.1 as an additional compliance for double check-valve assemblies. |
| 608.16.1 | Beverage dispensers | 608.16.1 | Beverage dispensers | Revised section to provide additional reference to CAN/CSA-B64.3.1 as an additional compliance for backflow preventers. |
| - | - | 608.16.10 | Coffee machines and noncarbonated beverage dispensers | Added new section to provide compliance provisions for this type of equipment where protection is needed for potential backflow siphonage. |
| Chapter 7: Sanitary Drainage |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| 701.2 | Sewer required. | 701.2 | Sewer required. | Direct user to the appropriate FAC Rule. Every building in which plumbing fixtures are installed and all premises having drainage piping shall be connected to a public sewer, where available, or an approved private sewage disposal system in accordance with Chapter 64E-6, Florida Administrative Code, Standards for Onsite Sewage Treatment and Disposal Systems , |
| Table 702.2 | Underground building drainage and vent pipe | Table 702.2 | Underground building drainage and vent pipe | Revised table to update referenced standard for polyolefin pipe material to add ASTM F1412. Table 702.4 also adds CSA reference standard to provide an option for compliance. |
| Table 702.4 | Pipe fittings | Table 702.4 | Pipe fittings |  |
| 703.1 | Building sewer pipe near the water service | 703.1 | Building sewer pipe near the water service | Revised section to remove provisions and reference to Table 702.3 to provide a single reference to Section 603.2 which contains a single reference for complete coverage. |
| 705.5.2 | Compression gasket joints | 705.5.2 | Compression gasket joints | Revised section to add newly established hydrostatic testing criteria for the finished gaskets. |
| 705.5.3 | Mechanical joint coupling | 705.5.3 | Mechanical joint coupling | Revised section to add reference to ASTM C1540 to correlate with requirements in residential and building codes. |
| - | - | 705.16 | Polyethylene plastic pipe | Added new section(s) to provide joining methods for newly added polyethylene piping materials. |
| - | - | 705.16.1 | Heat-fusion joints |  |
| - | - | 705.16.2 | Mechanical joints |  |
| 705.16.4 | Plastic pipe or tubing to other piping material | 705.18.4 | Plastic pipe or tubing to other piping material | Relocated section and revised the term "grades" to "types" to avoid misinterpretation that section is only applicable for materials with grades. |
| - | - | 705.17 | Polyolefin plastic | Added new section(s) to provide joining methods for newly added polyolefin piping materials. |
| - | - | 705.17.1 | Heat-fusion joints |  |
| - | - | 705.17.2 | Mechanical and compression sleeve joints |  |
| - | - | 706.4 | Heel-or-side-inlet quarter bends | Added new section to clarify use and applications of heel- or side-inlet quarter bends. |
| 708.3.3 | Changes of direction | 708.3.3 | Changes of direction | Revised section to clarify that cleanouts are required where there is a change of direction greater than 45 degrees for the building sewer. |
| Table 709.1 | Drainage fixture units for fixtures and groups | Table 709.1 | Drainage fixture units for fixtures and groups | Revised table to add provisions for "service sink" to the list of fixture types provided. |
|  |  |  |  | Revised table to add "Urinal, nonwater supplied" to the list of fixture types provided. |
| 712.2 | Valves required | 712.2 | Valves required | Exception deleted. |
| Chapter 9: Vents |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| 903.1 | Stack required | - | - | Deleted section to account for buildings not requiring a stack. See replaced content in entries below. |
| 903.1.1 | Connection to drainage system | - | - |  |
| 903.1 | Stack required | 903.1 | Required vent extension | Revised section to add scope, installation, and size. This re-organization of content will assist to eliminate confusion and provide clarity of requirements. New section also eliminates ambiguous language and provides specific installation and size requirements. |
| 903.1.1 | Connection to drainage system | 903.1.1 | Installation |  |
|  |  | 903.1.2 | Size |  |
| 903.3 | Vent termination | 903.3 | Vent termination | Revised section to expand the use of an air admittance valve to stack applications. Also added reference to Section 917. |
| 906.1 | Distance of trap from vent | 906.1 | Distance of trap from vent | Exception added permitting the developed length of the fixture drain from the trap weir to the vent fitting for self-siphoning fixtures to not be limited. |
| Table 906.1 | Maximum distance of fixture trap from vent | Table 906.1 | Maximum distance of fixture trap from vent | Revised table with removal of "size of fixture drain" which isn't required. The intent of the table is better provided by use of what has been provided within sections. This modified table also utilized concept to provide distances that prevent trap seal loss. |
| 906.2 | Venting of fixture drains | 906.2 | Venting of fixture drains | Revised to also require that the total fall in a fixture drain due to pipe slope is not permitted to exceed the diameter of the fixture drain. |
| 909.1 | Wet vent permitted | 909.1 | Horizontal wet vent permitted | Revised title and section to add "horizontal" to make it clear that this section regulates only horizontal wet venting. |
| 909.1.1 | Vertical wet vent | 909.1.1 | Vertical wet vent permitted | Revised section to add the term "permitted" in the title. Also revised language to provide consistency with horizontal vent requirements and to clarify requirements of wet vents and fixture drains. |
| 909.2 | Vent Connection | 909.2 | Vent Connection | Revised section to remove information regarding sizing (relocated to subsequent section) and added clarifying information regarding vertical and horizontal wet vents relative to the requirements for the dry-vented fixture drain connection. |
| 909.3 | Size | 909.3 | Size | Revised section to add relocated information from 909.2, which is applicable to sizing and more appropriate for this section. |
| 910.2 | Stack installation | 910.2 | Stack installation | Revised section to modify previous offset prohibition to limit where vertical offset can occur rather than eliminate it altogether. This change will provide more flexibility but maintain the original intent. |
| 910.3 | Stack vent | 910.3 | Stack vent | Revised to require that the size of the stack vent to be not less than the size of the wasted stack, instead of equal to the size. Permits connection of the stack vent with other stack vents and vent stacks in accordance with Section 903.5 |
| 912.2 | Fixture branch or drain | 912.2 | Fixture branch or drain | Revised section to remove applicable list of fixtures since the types are provided in another section. |
| 917.1 | General | 917.1 | General | Revised section to expand the use of an air admittance valve to stack applications and add reference to ASSE 1050. |
| 917.3 | Where permitted | 917.3 | Where permitted | Revised section to expand the use of an air admittance valve to stack applications and add reference to Section 917.3.3. |
| 917.3.2 | Relief vent | 917.3.2 | Relief vent | Revised section to provide horizontal branch location and requirements. |
| - | - | 917.3.3 | Stack | Added new section providing information for stack type air admittance valves. |
| 917.4 | Location | 917.4 | Location | Revised section to expand the use of an air admittance valve to stack applications and provide specific location information. |
| Chapter 10: Traps, Interceptors and Separators |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| 1002.1 | Fixture traps | 1002.1 | Fixture traps | Revised section to remove ambiguous language, "as close as possible" and replace with "a horizontal distance of 30 inches," which provides specific location information and corresponds with exception within this section. |
| 1003.1 | Interceptors and separators - where required | 1003.1 | Interceptors and separators - where required | Revised section to add "private sewage disposal systems" not previously addressed. |
| 1003.3 | Great traps and grease interceptors | 1003.3 | Grease interceptors | Deleted "trap" from title and scope of section. |
| 1003.3 | Great traps and grease interceptors | 1003.3 | Grease traps and Grease interceptors for public sewer. | Add “Grease Traps” to title and clarify section is for public sewers. 1003.3 Grease traps and Grease interceptors for public sewer. Grease interceptors shall comply with the requirements of Sections 1003.3.1 through 1003.3.4.2. |
| 1003.3.1 | Grease traps, grease interceptors required | 1003.3.1 | Grease interceptors and automatic grease removal devices required | Revised title and section to add "automatic grease removal device." Also provided additional language including the listing of fixtures for clarification and further clarification indicates that grease removal devices must only receive the discharge from fixtures requiring treatment or separation. |
| 1003.3.2 | Food waste grinders | 1003.3.2 | Food waste grinders | Revised title and section to replace the term "traps" with "interceptors" to correlate with referenced standards. Also added recommended information from the Plumbing and Drainage Institute regarding emulsifiers, chemical, enzyme and bacteria organisms to not be utilized. |
| 1003.3.3 | Grease interceptors and automatic grease removal devices not required | 1003.3.3 | Grease interceptors and automatic grease removal devices not required | Revised title and section to replace the term "traps" with "interceptors" to correlate with referenced standards. |
| 1003.3.4 | Grease interceptors and automatic grease removal devices | 1003.3.4 | Grease interceptors and automatic grease removal devices |  |
| 1003.3.4.1 | Grease trap capacity | 1003.3.4.1 | Grease interceptor capacity. | Revised title and section to replace the term "traps" with "interceptors" to correlate with referenced standards. |
| 1003.3.4.1 | Grease trap capacity. | 1003.3.4.1 | Grease interceptor capacity. | Add “grease trap” back into text. 1003.3.4.1 Grease interceptor capacity. Grease interceptors and grease traps shall have the grease retention capacity indicated in Table 1003.3.4.1 for the flow-through rates indicated. |
| Table 1003.3.4.1 | Capacity of grease interceptors | Table 1003.3.4.1 | Capacity of grease interceptors | Revised title to replace the term "traps" with "interceptors" and added flow-through ratings "75" and "100" to the table content. Also added footnote "a." to provide information regarding flow-through rates greater than 100 gpm. |
| 1003.3.4.2 | Rate of flow controls | 1003.3.4.2 | Rate of flow controls | Add “grease traps” to be included with inceptors. Grease interceptors and grease traps shall be equipped with devices to control the rate of water flow so that the water flow does not exceed the rated flow. The flow-control device shall be vented and terminate not less than 6 inches (152 mm) above the flood rim level or be installed in accordance with the manufacturer’s instructions. |
| - | - | 1003.3.5 | Automatic grease removal devices | Added new section to provide specifics regarding when and where automatic grease recovery devices are utilized per ASME A112.14.4. |
| 1003.4 | Oil separators required | 1003.4 | Oil separators required | Revised section to require oil separators for hydraulic elevator pits; an exception allows warning device per ANSI. New exception added to Section stating that an oil separator is not required in hydraulic elevator pits where an approved alarm system is installed. |
| 1003.4.2 | Oil separator design | 1003.4.2 | Oil separator design | Revised title and section to replace the term "traps" with "interceptors" to correlate with referenced standards. |
|  |  | 1003.5 | Grease interceptors for onsite sewage treatment and disposal systems. | Add text in title to include reference to onsite sewage treatment systems. Clarify size of tank for both grease interceptors and grease traps. 1003.5 Grease interceptors for onsite sewage treatment and disposal systems. Grease interceptors shall be water and gas tight. Each interceptor shall be engineered to withstand the load, such as from vehicular traffic, to be placed on the interceptor. Sizing of grease interceptors shall be based on the equations of Table 1003.5.1. The minimum tank volume of grease interceptors shall be 750 gallons (2839 L), and the maximum volume of an individual grease interceptor chamber shall be 1,250 gallons (4731 L). Interceptors shall be permitted to be installed in series or as multi-chambered tanks |
| 1003.5.2 | Construction of interceptor. | 1003.5.2 | Construction of interceptor. | Makes code consistent with Florida Administrative Code 64E-6. Each interceptor shall be constructed in accordance with Rule 64E-6, Florida Administrative Code. Minimum depth of the liquid shall be 40 inches (1016 mm). Each compartment shall be accessible with a minimum clearance of 18 inches (457 mm) square or in diameter. |
| 1003.6 | Laundries | 1003.6 | Laundries | Section revised to change "commercial laundries" to "laundries not installed within an individual dwelling unit or intended for individual family use." |
| Chapter 11: Storm Drainage |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| Table 1102.4 | Building storm sewer pipe | Table 1102.4 | Building storm sewer pipe | Revised table to add reference standard CSA B181.1, CSA B181.2, and B182.1. |
| Table 1102.5 | Subsoil drain pipe | Table 1102.5 | Subsoil drain pipe | Revised table to add reference standards CSA B182.1, CSA B182.6, and CSA B182.8. |
| Table 1102.7 | Pipe fittings | Table 1102.7 | Pipe fittings | Revised table to remove ASTM standards no longer appropriate for this section. |
|  |  |  |  | Added reference to ASTM F1866, ASTM D3311 and CSAB181.1. |
|  |  |  |  | Added coextruded composite pipe fitting materials. |
|  |  |  |  | Deleted CPVC plastic and polyethylene plastic from materials. |
| Chapter 13. Referenced Standards |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| - | - | 13 | Reference Standards | Standards update NFPA NFPA 99C-05 Gas and Vacuum Systems 1202.1 |
| APPENDIX C. Section C103 Subsurface Landscape Irrigation Systems |  |  |  |  |
| Section | Requirement | Section | Requirement | Analysis |
| 301.3 | Connection to drainage system. | 301.3 | Connections to drainage system. | Change exception to require sanitary drainage systems to be connected to a public sewer, onsite sewage treatment system in accordance with State Department of Health regulations All plumbing fixtures, drains, appurtenances and appliances used to receive or discharge liquid wastes or sewage shall be directly connected to the sanitary drainage system of the building or premises, in accordance with the requirements of this code. This section shall not be construed to prevent indirect waste systems required by Chapter 8. Exception: Bathtubs, showers, lavatories, clothes washers and laundry trays shall not be required to discharge to the sanitary drainage system where such fixtures discharge to an approved gray water system for flushing of water closets and urinals. Any sewage that discharges from the building must be connected to a sanitary drainage system of the building or premises. The sanitary drainage system shall discharge either to public sewer or to an onsite sewage treatment and disposal system in accordance with the State of Florida Standards for Onsite Sewage Treatment and Disposal Systems. |
| C101.1 | General | C101.1 | Scope | Delete subsurface landscape irrigation from the scoping of Appendix C. The provisions of this appendix shall govern the materials, design, construction and installation of gray water systems for flushing of water closets and urinals. (see Figures 1). |
| C101.2 | Definition | C101.2 | Definition | Add definition for “greywater” and clarify what constitutes “Blackwater” GRAYWATER. As defined by 381.0065(2)(b) and (d) Florida Statutes, “Graywater” means that part of domestic sewage that is not blackwater, including waste from the bath, lavatory, laundry, and sink, except kitchen sink waste. “Blackwater” means that part of domestic sewage carried off by toilets, urinals, and kitchen drains |
| C101.4 | Resorvior | C101.4 | Installation | Delete subsurface landscape irrigation from the section. In addition to the provisions of Section C101, systems for flushing of water closets and urinals shall comply with Section C102. Except as provided for in Appendix C, all systems shall comply with the provisions of the Florida Building Code, Plumbing. |
| - | - | C103 | Subsurface Landscape Irrigation Systems | Delete Section 103 in its entirety. |

ATTACHMENT

Modifications to Table 607.2.1 from page 10

# TABLE 607.2.1

MINIMUM PIPE INSULATION (in.)a,b

Domestic and Service Hot Water Circulating Systemsa

| Fluid Design Operating Temperature Range (oF) | Insulation Conductivity |  | Nominal Pipe or Tube Size (inches) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Conductivity Range Btu in/(h ft2 .oF) | Mean Temperature Rating | <1 | 1-1 ½ | 1 ½ to 4 | 4 to <8 | ≥8 |  |
| >105 | 0.22-0.28 | 100 | 0.5 | 0.5 | 1.0 | 1.0 |  | 1.0 |

a Section 13-412.ABC.4 of Chapter 13 of the Florida Building Code, Building  requires piping insulation for

- recirculating system piping, including the supply and return piping of a circulating tank type water heater,

- the first 8’ of outlet piping for a constant temperature nonrecirculating storage system,

- The inlet pipe between the storage tank and a heat trap in a nonrecirculating storage system and

4)   pipes that are externally heated for commercial non-circulating systems. For residential greater than two-family and less than 4 stories, Section 13-612.AB.5 of Chapter 13 of the Florida Building Code, Building requires at least ½ inch insulation for circulating hot water system pipes.

bFor insulation outside the stated conductivity range, the minimum thickness (T) shall be determined as follows:

T=r(1+t/r)K/k - 1

Where T= minimum insulation thickness (in.), r=actual outside radius of pipe (in.), t=insulation thickness listed in this table for applicable fluid temperature and pipe size, K=conductivity of alternate material at mean rating temperature indicated for the applicable fluid temperature (Btu.in.[h.ft2.oF]); and k=upper value of the conductivity range listed in this table for applicable fluid temperature.

cPiping insulation is not required between the control valve and coil on run-outs when the control valve is located within 4 feet of the coil and the pipe size is 1 inch or less.