TABLE 1005.1
EGRESS WIDTH PER OCCUPANT SERVED

OCCUPANCY	WITHOUT SPRINKLER SYSTEM	WITH SPRINKLER SYSTEM	
	
Stairways
(inches per occupant)	Other egress components
(inches per occupant)	
Stairways
(inches per occupant)	Other egress components
(inches per occupant)	
Occupancies
Other than those listed below	
0.3	
0.2	
0.3
.2	
0.2
.15	
Hazardous: H-1, H-2, H-3 and H-4	
0.7	
0.4	.3
0.7	.2
0.4	
Institutional: I-2	NA	NA	0.4	0.2	

Table 7.3.3.1 Capacity Factors
								Level Components						      Stairways		                   and Ramps 
				(width Per person)                      (width Per person)
Area			    mm            in.                               mm            in.
Board and care			    10              0.4		       5              0.2
Health care, 			    7.6	         0.3		       5	          0.2
     sprinklered	
Health care			    15	         0.6		       13	          0.5
     nonsprinklered
High hazard contents		     18	         0.7		        10	           0.4
All others			     7.6	         0.3		         5             0.2
______________________________________________________________________________