Florida Supplement to the 2012 IPC

Note 1:  Throughout the document, change International Building Code to Florida Building Code, Building; change the ICC Electrical Code to Chapter 27 of the Florida Building Code, Building; change the International Energy Conservation Code to the Florida Building Code, Energy Conservation; change the International Existing Building Code to Florida Building Code, Existing Building; change the International Fire code to Florida Fire Prevention Code; change International Fuel Gas Code to Florida Building Code, Fuel Gas; change the International Mechanical Code to Florida Building Code, Mechanical; change the International Plumbing Code to Florida Building Code, Plumbing; change the International Residential Code to Florida Building Code, Residential.

Note 2:  Criteria blocked in yellow indicate Florida specific language from the 2010 FBC.

Chapter 2, Definitions

Add to read as follows:

GREASE INTERCEPTOR.  An interceptor whose rated flow exceeds 50 gpm or has a minimum storage capacity of 750 gallons or more and is located outside the building.

GREASE TRAP. An interceptor whose rated flow is 50 gpm or less and is located inside the building.

RECLAIMED WATER. Water that has received treatment and is reused after flowing out of a domestic wastewater treatment facility.

REUSE. The deliberate application of reclaimed water for beneficial purpose.

Chapter 3, General Regulations

305.1 Corrosion.  Change to read as shown:

305.1 Corrosion. Pipes passing through concrete or cinder walls and floors or other corrosive material shall be protected against external corrosion by a protective sheathing or wrapping or other means that will withstand any reaction from the lime and acid of concrete, cinder or other corrosive material. Sheathing or wrapping shall allow for movement including expansion and contraction of piping. Minimum wall thickness of material shall be 0.010 inch (0.25 mm).

Exception: Sleeving is not required for installation of CPVC into concrete or similar material.

Section 305.1.1 Penetration, add text to read as follows:

305.1.1 Penetration. Protective sleeves around piping penetrating concrete slab-on-grade floors shall not be of cellulose-containing materials. If soil treatment is used for subterranean termite protection, the sleeve shall have a maximum wall thickness of 0.010 inch, and be sealed within the slab using a non-corrosive clamping device to eliminate the annular space between the pipe and the sleeve. No termiticides shall be applied inside the sleeve.

317 Public Food Service Establishments and Food Establishments.  Add to read as shown.

317 Public Food Service Establishments and Food Establishments.

317.1 Requirements.  Add to read as shown.

317.1 Requirements. Public food service establishments and food establishments, as defined in Chapter 381 Florida Statutes, Chapter 500 Florida Statutes and Chapter 509 Florida Statutes, shall comply with the applicable code requirements found in the Florida Building Code, Building, Chapter 4, Special Occupancy.

403.2 Separate facilities.     Change to read as shown.

403.2 Separate facilities.   Where plumbing fixtures are required, separate facilities shall be provided for each sex.

Exceptions:

1 .Separate facilities shall not be required for dwelling units and sleeping units.

2. Separate facilities shall not be required for food service establishments which seat 10 persons or less.

3. No change

403.6 Sanitary Facilities for Public Swimming Pools.   Add to read as shown.

403.6 Sanitary facilities for public swimming pools.  Swimming pools with a bathing load of 20 persons or less may utilize a unisex restroom. Pools with bathing loads of 40 persons or less may utilize two unisex restrooms or meet the requirement of Table 403.6. Unisex restrooms shall meet all the requirements for materials, drainage and signage as indicated in sections 424.1.6.1.1 through 424.1.6.1.4 of the FBC, Building.  Each shall include a water closet, a diaper change table, a urinal, and a lavatory. Pools with a bathing load larger than 40 persons shall provide separate sanitary facilities labeled for each sex. The entry doors of all restrooms shall be located within a 200-foot (60 960 mm) walking distance of the nearest water’s edge of each pool served by the facilities.

Exception: Where a swimming pool serves only a designated group of residential dwelling units and not the general public, poolside sanitary facilities are not required if all living units are within a 200 foot horizontal radius of the nearest water's edge, are not over three stories in height and are each equipped with private sanitary facilities.

403.6.1 Required fixtures. Fixtures shall be provided as indicated on Table 403.8. The fixture count of Table 403.8 is deemed to be adequate for the pool and pool deck area that is up to three times the area of the pool surface provided.   An additional set of fixtures shall be provided in the men's restroom for every 7,500 square feet or major fraction thereof for pools greater than 10,000 square feet. Women's restrooms shall have a ratio of three to two water closets provided for women as the combined total of water closets and urinals provided for men.  Lavatory counts shall be equal.

403.6.2 Outside access. Outside access to facilities shall be provided for bathers at outdoor pools.  Where the restrooms are located within an adjacent building and the restroom doors do not open to the outside, the restroom doors shall be within 50 feet of the buildings exterior door. If the restrooms are not visible from any portion of the pool deck, signs shall be posed showing directions to the facilities. Directions shall be legible from any portion of the pool deck; letters shall be a minimum of 1-inch high.

403.6.3 Sanitary facility floors. Floors of sanitary facilities shall be constructed of concrete or other nonabsorbent materials, shall have a smooth, slip-resistant finish, and shall slope to floor drains. Carpets, duckboards and footbaths are prohibited. The intersection between the floor and walls shall be coved where either floor or wall is not made of waterproof materials such as tile or vinyl.

.

TABLE 403.6

PUBLIC SWIMMING POOL - REQUIRED FIXTURES COUNT

SIZE 	            MEN'S RESTROOMS       WOMEN'S RESTROOMS

Urinals  WC  Lavatory 	WC 	Lavatory

0 - 2500 sq ft              1 	     1 	      1 	            1 	     1

2501 - 5000 sq ft       	2 	     1 	      1 	            5 	     1

5001 - 7500 sq ft 	2 	     2 	      2 	            6 	     2

7501 - 10,000 sq ft    	3 	     2           3 	            8	     3

For SI:   1 square foot = 0.0929 m2.

423.3 Reclaimed water.  Add to read as shown.

423.3 Reclaimed water. Reclaimed water shall be permitted to be used for aesthetic uses such as decorative pools or fountains in accordance with Florida Department of Environmental Protection (DEP). Reuse of reclaimed water activities shall comply with the requirements of DEP rules.

Chapter 5, Water Heaters

Chapter 6, Water Supply and Distribution

602.3 Individual water supply.  Change to read as shown.

602.3 Individual water supply. Where a potable public water supply is not available, individual sources of potable water supply meeting the requirements of Florida Statute 373 shall be utilized.

No change to the remaining text.

602.4 Reclaimed water.  Add to read as shown.

602.4 Reclaimed water.  Reclaimed water shall be permitted to be used for flushing water closets and urinals and other fixtures which do not require potable water in accordance with Florida Department of Environmental Protection (DEP) Chapter 62-610, F.A.C. Reuse of reclaimed water activities shall comply with the requirements of DEP Chapter 62-610, FAC.

Chapter 7, Sanitary Drainage

701.2  Sewer required.  Change to read as shown.

701.2 Sewer required. Every building in which plumbing fixtures are installed and all premises having drainage piping shall be connected to a publicly owned or investor-owned sewerage system sewer , where available, or an approved onsite sewage treatment and private sewage disposal system in accordance with Chapter 64E-6, Florida Administrative Code, Standards for Onsite Sewage Treatment and Disposal Systems.

Chapter 10, Traps, Interceptors and Separators

1003.2 Approval.  Change to read as shown.

1003.2 Approval. The size, type and location of each interceptor and of each separator shall be approved by the plumbing official. Where the interceptor or separator is located within an onsite sewage treatment and private sewage disposal system, such interceptor or separator shall be approved by the health official. The interceptor or separator shall be designed and installed in accordance with the manufacturer’s instructions and the requirements of this section. Wastes that do not require treatment or separation shall not be discharged into any interceptor or separator.

Revise 1003.3 Grease interceptors, to read as follows:

1003.3 Grease traps and grease interceptors for public publicly owned or investor-owned sewerage systems sewer.  Grease interceptors shall comply with the requirements of Sections 1003.3.1 through 1003.3.4.2.

(No change to remaining text)

1003.3.4 Grease interceptors and automatic grease removal devices.  Add Exception to read as follows:

Exception: Grease iInterceptors that are sized, constructed and approved in accordance with Rule 64E-6, Florida Administrative Code have a volume of not less than 500 gallons (1893 L) and that are located outside the building outdoors shall not be required to meet the requirements of this section.

1003.3.4.1 Grease interceptor capacity.  Change to read as shown.

1003.3.4.1 Grease interceptor capacity. Grease interceptors and grease traps shall have the grease retention capacity indicated in Table 1003.3.4.1 for the flow-through rates indicated.

1003.3.4.2 Rate of flow controls. Change to read as shown.

1003.3.4.2 Rate of flow controls. Grease interceptors and grease traps shall be equipped with devices to control the rate of water flow so that the water flow does not exceed the rated flow. The flow-control device shall be vented and terminate not less than 6 inches (152 mm) above the flood rim level or be installed in accordance with the manufacturer’s instructions.

1003.5 Grease interceptors.   Change to read as shown.

1003.5 Grease interceptors for onsite sewage treatment and disposal systems. Grease interceptors are not required for a residence.  However, one ore more grease interceptors are required where grease waste is produced in quantities that could otherwise cause line stoppage or hinder sewage disposal.  Where a grease interceptor is required or used, only kitchen wastewater shall first pass through the interceptor and then be discharged into the first compartment of a septic tank or other approved system. Grease interceptors shall be water and gas tight. Each interceptor shall be engineered to withstand the load, such as from vehicular traffic, to be placed on the interceptor. Sizing of grease interceptors shall be based on the equations of Table 1003.5.1.  The minimum tank volume of grease interceptors shall be 750 gallons (2839 L), and the maximum volume of an individual grease interceptor chamber shall be 1,250 gallons (4731 L). Interceptors shall be permitted to be installed in series or as multi-chambered tanks.

1003.5.1 Grease interceptor capacity.  Add to read as shown.

1003.5.1 Grease interceptor capacity.   Sizing of grease interceptors shall be based on the equations of Table 1003.5.1.  The minimum tank volume of grease interceptors shall be 750 gallons (2839 L), and the maximum volume of an individual grease interceptor chamber shall be 1,250 gallons (4731 L). When the required effective capacity of the grease interceptor is greater than 1250 gallons, installation of multi-chambered grease interceptors or grease interceptors in series is required. The minimum grease retention capacity for interceptors shall be at least two times the flow-through rate.

1003.5.2 Construction of interceptor.  Add to read as shown.

1003.5.2 Construction of interceptor. Each interceptor shall be constructed and approved in accordance with Rule 64E-6, Florida Administrative Code. Minimum depth of the liquid shall be 40 inches (1016 mm). Each compartment shall be accessible with a manhole having a minimum area of 225 square inches. clearance of 18 inches (457 mm) square or in diameter. Interceptors must be located so as to provide easy access for routine inspection, cleaning and maintenance.  Manholes shall be provided over the inlet and outlet of each interceptor and be brought to finished grade.

1003.5.3 Inlet and outlet piping.  Add to read as shown.

1003.5.3 Inlet and outlet piping.   The inlet invert shall discharge a minimum 2 1/2 inches above the liquid level line and the outlet pipe shall have a tee with a minimum diameter of 4 inches that extends to within 8 inches of the bottom of the tank.The inlet and outlet piping shall have a two-way cleanout tee installed. Inlet piping shall enter at 2½ inches (64 mm) above the liquid level. Inlet piping shall connect to a tee, sweep or baffle, which shall extend to 24 inches (610 mm) below the water level.  The outlet pipe shall start at 8 inches (203 mm) above the bottom of the interceptor and extend vertically to a tee. The tee and pipe shall be no less than 4 inches (102 mm) in diameter. The tee shall be installed with the run in the vertical direction.

Table 1003.5.1: Sizing Formulas for Grease Interceptors Private Sewage Disposal System.  Add to read as shown.

Table 1003.5.1: Sizing Formulas for Grease Interceptors, Private Sewage Disposal System

| SIZING FORMULA FOR RESTAURANTS: | OTHER ESTABLISHMENTS WITH COMMERCIAL KITCHENS: |
| --- | --- |
| (S)x(GS)x(HR/12)x(LF)=Effective cCapacity of grease iInterceptor in gallons Where: S = Number of seats in dining area GS = Gallons of waste water per seat (Use 25 gallons for ordinary restaurants with china dishes and/or automatic dishwasher) (Use 10 gallons for single service article restaurants with paper or baskets and no dishwashers) HR = Number of hours establishment restaurant is open LF = Loading Factor (Use 2.00 interstate highway; 1.50 other freeways; 1.25 recreational area; 1.00 main highway; 0.75 other roadshighway) | (M)x(GM)x(LF) = Effective capacity of Grease interceptor in gallons Where: M = Meals prepared per day GM = Gallons of waste water per meal (Use 5 gallons) LF = Loading Factor (Use 1.00 with dishwashing machine and 0.75 without dishwashing machine) |

Note:  For other than private sewage disposal systems, reduce gallon values by 25%.

Section 1003.511 Sand interceptors in commercial establishments.  Add to read as shown.

1003.11 Sand interceptors in commercial establishments.  Sand and similar interceptors for heavy solids shall be designed and located so as to be provided with ready access for cleaning, and shall have a water seal of not less than 6 inches (152 mm).

Chapter 13, Referenced Standards

Referenced Standards.  Change to read as shown.

Ch. 62-610 Florida Administrative Code-Reuse of Reclaimed Water

and Land Application                                                                                602.4

Ch. 64E-6 Florida Administrative Code-Standards for Onsite Sewage

and Disposal Systems                                                                             701.2, 1003.5.2

Ch. 373 Florida Statute, Water Resources						602.3

Ch. 381 Florida Statute, Food Products						317.1

Ch. 500 Florida Statute, Lodging and Food Service Establishments		317.1

Ch. 509 Florida Statute, Public Lodging and Food Service Establishments	317.1