| ROOFING Local Technical Amendments to the 2014 5th Edition Florida Building Code |  |  |  |
| --- | --- | --- | --- |
| JURISDICTION | DOCUMENT with TECHNICAL AMENDMENT | TEXT OF TECHNICAL AMENDMENT | TAC REVEW |
| Pinellas County Construction Licensing Board |  | 1509.6.5 Mechanical Units. Roof mounted mechanical units shall be mounted on curbs raised a minimum of 8 inches (203 mm) above the roof surface, or where roofing materials extend beneath the unit, on raised equipment supports providing a minimum clearance height in accordance with Table 1509.6.5. Exception: In buildings where the existing rooftop equipment, in the opinion of the building official, provides sufficient clearance to repair, recover, replace and/or maintain the roofing system or any of its components, such existing equipment need not comply with Table 1509.6.5. TABLE 1509.6.5. CLEARANCE BELOW RAISED ROOF. MOUNTED MECHANICAL UNITS. WIDTH OF MECHNAICAL UNIT (inches); MINIMUM CLEARANCE ABOVE SURFACES (inches). <24; 14. 24 < 36; 18 14. 36 < 48; 24 14. 48 < 60; 30 14. >60; 48. Exception: When removing or replacing roof mounted mechanical units for individual units and/or spaces within multi-unit buildings the individual units mav be reinstalled utilizing the existing system of attachment. At such time of reroofing of the building all mechanical units must be brought into compliance with this code section. | Mechanical and Roofing TAC’s. (0Yes-9No NAR) |