Comments on the 2013 Update to the Florida Building Code to be considered by the Commission

Fire TAC

Meeting Date: August 22, 2013

| Tracking ID | Florida Building Code, Residential Proposed Changes | Comments | TAC Action August 1, 2013 | Commission Action |
| --- | --- | --- | --- | --- |
| F1 | Proponent: Staff Section 553.73(10), Florida Statutes 553.73 Florida Building codes— (17) A provision The provisions of section R313 of the most current version of the International Residential Code relating to mandated fire sprinklers may not be incorporated into the Florida Building Code as adopted by the Florida Building Commission and may not be adopted as a local amendment to the Florida Building Code. This subsection does not prohibit the application of cost-saving incentives for residential fire sprinklers that are authorized in the International Residential Code upon a mutual agreement between the builder and the code official. This subsection does not apply to a local government that has a lawfully adopted ordinance relating to fire sprinklers which has been in effect since January 1, 2010. Revise R101.2 to read as follows: R101.2 Scope. The provisions of the International Residential Code for One- and Two-family Dwellings shall apply to the construction, alteration, movement, enlargement, replacement, repair, equipment, use and occupancy, location, removal and demolition of detached one- and two-family dwellings and townhouses not more than three stories above grade plane in height with a separate means of egress and their accessory structures. Exceptions: 1. Live/work units complying with the requirements of Section 419 of the International Building Code shall be permitted to be built as one- and two-family dwellings or townhouses. Fire suppression required by Section 419.5 of the International Building Code when constructed under the International Residential Code for One- and Two-family Dwellings shall conform to Section P2904 Section 903.3.1.3 of the Florida Building Code, Building. 2. Owner-occupied lodging houses with five or fewer guestrooms shall be permitted to be constructed in accordance with the International Residential Code for One- and Two-family Dwellings when equipped with a fire sprinkler system in accordance with Section P2904 903.3.1.3 of the Florida Building Code, Building. | Glitch – (e) Changes to or inconsistencies with federal or state law. HB 269. | Withdrawn by Staff | No Action Taken |
| F2 | Proponent: Staff Revise R302 to read as follows: SECTION R302 FIRE-RESISTANT CONSTRUCTION R302.1 Exterior walls. Construction, projections, openings and penetrations of exterior walls of dwellings and accessory buildings shall comply with Table R302.1(1); or dwellings equipped throughout with an automatic sprinkler system installed in accordance with Section P2904 shall comply with Table R302.1(2). Exceptions: 1. Walls, projections, openings or penetrations in walls perpendicular to the line used to determine the fire separation distance. 2. Walls of dwellings and accessory structures located on the same lot. 3. Detached tool sheds and storage sheds, playhouses and similar structures exempted from permits are not required to provide wall protection based on location on the lot. Projections beyond the exterior wall shall not extend over the lot line. 4. Detached garages accessory to a dwelling located within 2 feet (610 mm) of a lot line are permitted to have roof eave projections not exceeding 4 inches (102 mm). 5. Foundation vents installed in compliance with this code are permitted. | Glitch – (e) Changes to or inconsistencies with federal or state law. HB 269. | Withdrawn by Staff | No Action Taken |
| F3 | Proponent: Staff Delete Table R302.1(2) TABLE R302.1(2) EXTERIOR WALLS—DWELLINGS WITH FIRE SPRINKLERS | Glitch – (e) Changes to or inconsistencies with federal or state law. HB 269. | Withdrawn by Staff | No Action Taken |
|  | TABLE R302.1(2) EXTERIOR WALLS—DWELLINGS WITH FIRE SPRINKLERS EXTERIOR WALL ELEMENT; MINIMUM FIRE-RESISTANCE RATING; MINIMUM FIRE SEPARATION DISTANCE. Walls; Fire-resistance rated; 1 hour—tested in accordance with ASTM E 119 or UL 263 with exposure from the outside; 0 feet. Not fire-resistance rated; 0 hours; 3 feeta. Projections; Fire-resistance rated; 1 hour on the underside; 2 feeta. Not fire-resistance rated; 0 hours; 3 feet. Openings in walls; Not allowed; N/A; < 3 feet. Unlimited; 0 hours; 3 feeta. Penetrations; All; Comply with Section R302.4; < 3 feet. None required; 3 feeta. For SI: 1 foot = 304.8 mm.. N/A = Not Applicable. a. For residential subdivisions where all dwellings are equipped throughout with an automatic sprinkler systems installed in accordance with Section P2904, the fire separation distance for nonrated exterior walls and rated projections shall be permitted to be reduced to 0 feet, and unlimited unprotected openings and penetrations shall be permitted, where the adjoining lot provides an open setback yard that is 6 feet or more in width on the opposite side of the property line.. |  |
| F4 | Proponent: Staff Delete Section P2904 in its entirety SECTION P2904 DWELLING UNIT FIRE SPRINKLER SYSTEMS (See Attachment) | Glitch – (e) Changes to or inconsistencies with federal or state law. HB 269. | Withdrawn by Staff | No Action Taken |
| F5 | Proponent: Staff Additional Residential Fire Sprinkler language revisions to be considered for modification (See Note): Revise R302.3 to read as follows: R302.3 Two-family dwellings. Dwelling units in two-family dwellings shall be separated from each other by wall and/or floor assemblies having not less than a 1-hour fire-resistance rating when tested in accordance with ASTM E 119 or UL 263. Fire-resistance-rated floor/ceiling and wall assemblies shall extend to and be tight against the exterior wall, and wall assemblies shall extend from the foundation to the underside of the roof sheathing. Exceptions: 1. A fire-resistance rating of 1/2 hour shall be permitted in buildings equipped throughout with an automatic sprinkler system installed in accordance with NFPA 13. Reserved. Revise R309.5 to read as follows: R309.5 Fire sprinklers. Private garages shall be protected by fire sprinklers where the garage wall has been designed based on Table R302.1(2), Footnote a. Sprinklers in garages shall be connected to an automatic sprinkler system that complies with Section P2904. Garage sprinklers shall be residential sprinklers or quick-response sprinklers, designed to provide a density of 0.05 gpm/ft2. Garage doors shall not be considered obstructions with respect to sprinkler placement. Reserved. Revise R501.3 to read as follows: R501.3 Fire protection of floors. Floor assemblies, not required elsewhere in this code to be fire-resistance rated, shall be provided with a 1/2-inch (12.7 mm) gypsum wallboard membrane, 5/8-inch (16 mm) wood structural panel membrane, or equivalent on the underside of the floor framing member. Exceptions: 1. Floor assemblies located directly over a space protected by an automatic sprinkler system in accordance with Section P2904, NFPA13D, or other approved equivalent sprinkler system. Reserved. 2. – 4. (No Change) Revise P2803.6.1 to read as follows: P2803.6.1 Requirements for discharge pipe. The discharge piping serving a pressure-relief valve, temperature relief valve or combination valve shall: 1. – 12. (No Change) 13. Be constructed of those materials listed in Section P2904.5 or materials tested, rated and approved for such use in accordance with ASME A112.4.1. Reserved. | Glitch – (e) Changes to or inconsistencies with federal or state law. HB 269. Note: Items should be modified as indicated if TAC recommends approval for modifications listed in F1-F4 | Withdrawn by Staff | No Action Taken |

Revise P2803.6.1 to read as follows:

TABLE P2902.3

APPLICATION FOR BACKFLOW PREVENTERS

| DEVICE | DEGREE OF HAZARDa | APPLICATIONb | APPLICABLE STANDARDS |
| --- | --- | --- | --- |
| Air gap | High or low hazard | Backsiphonage or backpressure | ASME A112.1.2 |
| Air gap fittings for use with plumbing fixtures, appliances and appurtenances | High or low hazard | Backsiphonage or backpressure | ASME A112.1.3 |
| Antisiphon-type fill valves for gravity water closet flush tanks | High hazard | Backsiphonage only | ASSE 1002, CSA B125.3 |
| Backflow preventer with intermediate atmospheric vents | Low hazard | Backpressure or backsiphonage Sizes 1/4″ - 3/4″ | ASSE 1012, CSA B64.3 |
| Double check backflow prevention assembly and double check fire protection backflow prevention assembly | Low hazard | Backpressure or backsiphonage Sizes 3/8″ - 16″ | ASSE 1015, AWWA C510, CSA B64.5, CSA B64.5.1 |
| Double check detector fire protection backflow prevention assemblies | Low hazard | Backpressure or backsiphonage (Fire sprinkler systems) Sizes 2″ - 16″ | ASSE 1048 |
| Dual-check-valve-type backflow preventer | Low hazard | Backpressure or backsiphonage Sizes 1/4″ - 1″ | ASSE 1024, CSA B64.6 |
| Hose-connection backflow preventer | High or low hazard | Low head backpressure, rated working pressure backpressure or backsiphonage Sizes 1/2″ - 1″ | ASSE 1052, CSA B64.2.1.1 |
| Hose-connection vacuum breaker | High or low hazard | Low head backpressure or backsiphonage Sizes 1/2″, 3/4″, 1″ | ASSE 1011, CSA B64.2, CSA B64.2.1 |
| Laboratory faucet backflow preventer | High or low hazard | Low head backpressure and backsiphonage | ASSE 1035, CSA B64.7 |
| Pipe-applied atmospheric-type vacuum breaker | High or low hazard | Backsiphonage only Sizes 1/4″ - 4″ | ASSE 1001, CSA B64.1.1 |
| Pressure vacuum breaker assembly | High or low hazard | Backsiphonage only Sizes 1/2″ - 2″ | ASSE 1020, CSA B64.1.2 |
| Reduced pressure detector fire protection backflow prevention assemblies | High or low hazard | Backsiphonage or backpressure (Fire sprinkler systems) | ASSE 1047 |
| Reduced pressure principle backflow prevention assembly and reduced pressure principle fire protection backflow prevention assembly | High or low hazard | Backpressure or backsiphonage Sizes 3/8″ - 16″ | ASSE 1013, AWWA C511, CSA B64.4, CSA B64.4.1 |
| Spill-resistant pressure vacuum breaker | High or low hazard | Backsiphonage only Sizes 1/4″ - 2″ | ASSE 1056, CSA B64.1.3 |
| Vacuum breaker wall hydrants, frost-resistant, automatic-draining type | High or low hazard | Low head backpressure or backsiphonage Sizes 3/4″ - 1″ | ASSE 1019, CSA B64.2.2 |

For SI: 1 inch = 25.4 mm.

a. Low hazard—See Pollution (Section R202). High hazard—See Contamination (Section R202).

b. See Backpressure (Section R202). See Backpressure, Low Head (Section R202). See Backsiphonage (Section R202).