NORMATIVE APPENDIX B

CRITERIA FOR COMPUTER MODELING

FOR PERFORMANCE-BASED CODE COMPLIANCE

B-1.0	Residential

B-1.1 405.5 Calculation procedure.

B-1.1.1 405.5.1 General. Except as specified by this section, the Standard Reference Design and Proposed Design shall be configured and analyzed using identical methods and techniques. The Standard Reference Design totals for the Simulated Performance Alternative compliance method developed in accordance with the criteria compliance based on simulated energy performance requires that a proposed residence (Proposed Design) be shown to have an annual normalized, modified energy load that is less than or equal to 80% of the annual energy load of the Standard Reference Design as specified in Sections B 1.1.2 405.5.2 and 405.3 shall be adjusted by a factor of 0.80 to make the code 20 percent more stringent than the “2007” (Effective October 31, 2007) Florida energy code’s Standard Reference Design (Baseline) features.

[3945]

B-1.1.2 405.5.2 Residence specifications. The Standard Reference Design and Proposed Design shall be configured and analyzed as specified by Table B-1.1.2 405.5.2(1). Table 405.5.2(1) shall include by reference all notes contained in Table 402.1.1.

B-1.2 405.6 Calculation software tools. Only The EnergyGauge USA Fla/Res compliance software tools approved by the Florida Building Commission shall be utilized to conform to the provisions of Section 405.  [4457]

B-1.2.1 405.6.1 Minimum capabilities. Calculation procedures used to comply with this section shall be software tools capable of calculating the annual energy consumption of all building elements that differ between the standard reference design and the proposed design and shall include the following capabilities:

1. Computer generation of the standard reference design using only the input for the proposed design. The calculation procedure shall not allow the user to directly modify the building component characteristics of the standard reference design.

2. Calculation of whole-building (as a single zone) sizing for the heating and cooling equipment in the standard reference design residence in accordance with Section 403.6 M1401.3 of the International Residential Code.

3. Calculations that account for the effects of indoor and outdoor temperatures and part-load ratios on the performance of heating, ventilating and air-conditioning equipment based on climate and equipment sizing.

4. Printed code official inspection checklist listing each of the proposed design component characteristics from Table 405.5.2(1) determined by the analysis to provide compliance, along with their respective performance ratings (e.g., R-value, U-factor, SHGC, HSPF, AFUE, SEER, EF, etc.)

TABLE B-1.1.2(1) 405.5.2(1)

SPECIFICATIONS FOR THE STANDARD REFERENCE AND PROPOSED DESIGNS

| Building Component | Standard Reference Design | Proposed Design |
| --- | --- | --- |
| Above-grade walls | Type: mass wall if proposed wall is mass; otherwise wWood frame Gross area: same as proposed U-Factor: 0.082 Solar absorptance = 0.75 Emittance = 0.90 | As proposed As proposed As proposed As proposed As proposed |
| Conditioned basement and crawl space walls | Type: same as proposed Gross area: same as proposed U-Factor: 0.36 with the insulation layer on the interior side of walls | As proposed As proposed As proposed |
| Above-grade Floors over unconditioned spaces | Type: wood frame Gross area: same as proposed U-Factor: 0.064 | As proposed As proposed As proposed |
| Ceilings | Type: Wood frame Gross area: same as proposed U-Factor: 0.035 | As proposed As proposed As proposed |
| Roofs | Type: composition shingle on wood sheathing Gross area: same as proposed Solar absorptance = 0.75 Emittance = 0.90 | As proposed As proposed As proposed, except that proposed solar absorptances less than 0.96 require test report in accordance with Section 405.6.2. As proposed |
| Attics | Type: vented with aperture = 1 ft2 per 300 ft2 ceiling area | As proposed |
| Foundations | Type: same as proposed Foundation wall area above and below grade and soil characteristics: same as proposed Gross Area: same as proposed R-value: 0 | As proposed As proposed As proposed |
| Crawlspaces | Type: vented with net free vent aperture = 1 ft2 per 150 ft2 of crawlspace foor area. | Same as proposed, but not less net free ventilation area than the Standard Reference Design unless an approved ground cover in accordance with Section 408.1 of the Florida Building Code, Residential, is used, in which case, the same net free ventilation area as the Proposed Design home down to a minimum net free vent area of 1 ft2 per 1,500 ft2 of crawlspace floor area. |
| Doors | Area: 40 ft2 Orientation: North U-factor: 0.75 | As proposed As proposed As proposed |
| Glazing a | Total areab - The proposed glazing area; where proposed glazing area is less than 15% of the conditioned floor area. - 15% 18% of the conditioned floor area; where the proposed glazing area is 15% or more of the conditioned floor area. Orientation: equally distributed to four (4) cardinal compass orientations (N,E,S&W) U-factor: 0.75 SHGC:0.40 Interior shade coefficient except that for climates with no requirement (NR) SHGC = 0.40 shall be used Interior shade fraction Summer (all hours when cooling is required) = 0.70 Winter (all hours when heating is required) = 0.85c External shading: none | As proposed As proposed As proposed As proposed Same as standard reference design As proposed As proposed As proposed |
| Skylights | None | As proposed |
| Thermally isolated sunrooms | None | As proposed |
| Air exchange rate | Specific Leakage Area (SLA)d = 0.00036 (assuming no energy recovery) | For residences that are not tested, the same as the Baseline Home. For residences with mechanical ventilation systems and with envelope leakage tested in accordance with ASHRAE Standard 119, Section 5.1, the measured air exchange ratee combined with the proposed mechanical ventilation ratef which where such mechanical ventilation rate shall not be less than 0.01 x CFA + 7.5 x (Nbr+1) Where: CFA = conditioned floor area Nbr = number of bedrooms |
| Mechanical ventilation | None, except where a mechanical ventilation system is specified by the proposed design, in which case: Annual vent fan energy use: kWh/yr = 0.03942*CFA + 29.565 * (Nbr+1) (per dwelling unit) where: CFA = conditioned floor area Nbr = number of bedrooms | As proposed As proposed |
| Internal gains | IGain = 17,900 + 23.8*CFA + 4104*Nbr IGain = 22,196 + 15.13*CFA + 8,562*Nbr (Btu/day per dwelling unit) [3643] | Same as reference design |
| Internal mass: | An internal mass for furniture and contents of 8 pounds per square foot of floor area | Same as reference design plus any additional mass specifically designed as a Thermal Storage Element (g,f) but not integral to the building envelope or structure |
| Structural mass | For masonry floor slabs, 80% of floor area covered by R-2 carpet and pad, and 20% of floor directly exposed to room air. For masonry basement walls, as proposed, but with insulation required by Table 402.1.3 located on the interior side of the walls For other walls, for ceilings, floors, and interior walls, wood frame construction. | As proposed As proposed . |
| Heating systemsg,h,i | As proposed Fuel type: same as Proposed Design efficiencies: Electric: air source heat pump with prevailing federal minimum efficiency Non-electric furnaces: natural gas furnace with prevailing federal minimum efficiency Non-electric boilers: natural gas boiler with prevailing federal minimum efficiency Capacity: sized in accordance with M1401.3 of the International Residential Code Section 403.6.1. | As proposed As proposed As proposed As proposed As proposed |
| Cooling systemsgh,j | As proposed Fuel type: Electric Efficiency: in accordance with prevailing federal minimum standards Capacity: sized in accordance with Section 403.6.1 M1401.3 of the International Residential Code | As proposed As proposed As proposed |
| Service water heating systems g,h,i,j,k | As proposed Fuel type:same as Proposed Design Efficiency: in accordance with prevailing federal minimum standards Use: same as proposed design (gal/day): 30*Ndu + 10*Nbr where Ndu = number of dwelling units Tank temperature: 120 F | As proposed Gal/day=30 + (10 x Nbr) As proposed As proposed As proposed As proposed |
| Thermal distribution systems | A thermal distribution system efficiency (DSE) of 0.80 0.88 shall be applied to both the heating and cooling system efficiencies for all systems other than tested duct systems. Duct insulation: From Section 403.2.1. For tested duct systems, the leakage shall be the applicable maximum rate from Section 403.2.2. | As tested or as specified in Table 405.5.2(2) if not tested. Using Proposed Design duct locations and a DSE of 0.88, except when tested in accordance with ASHRAE Standard 152l , in which case measured duct air leakage values shall be used. |
| Thermostat | Type: manual Temperature setpoints: cooling temperature set point = 75 78 F; heating temperature set point = 72 68 F | Type: Same As proposed Same as standard reference Temperature setpoints: same as the Standard Reference Design, except when programmable thermostats are used. |

Notes:

(a) 	Glazing shall be defined as sunlight-transmitting fenestration, including the area of sash, curbing or other framing elements, that enclose conditioned space. Glazing includes the area of sunlight-transmitting fenestration assemblies in walls bounding conditioned basements.  For doors where the sunlight-transmitting opening is less than one-third of the door area, the glazing area of the sunlight transmitting opening shall be used.  For all other doors, the glazing area shall be the rough frame opening area for the door, including the door and the frame.

(b)	For residences with conditioned basements and for multiple family attached homes the following formula shall be used to determine total window area:

AF = 0.18 x AFL x FA x F

where:

AF = Total fenestration area

AFL = Total floor area of directly conditioned space

FA = (Above-grade thermal boundary gross wall area) / (above-grade boundary gross wall area + 0.5 x below-grade boundary gross wall area)

F = 	(Above-grade thermal boundary gross wall area) / (above-grade thermal boundary gross wall area + common gross wall area) or 0.56 whichever is greater

and where:

Thermal boundary wall is any wall that separates conditioned space from unconditioned space or ambient conditions

Above-grade thermal boundary wall is any portion of a thermal boundary wall not in contact with soil

Below-grade boundary wall is any portion of a thermal boundary wall in soil contact

Common wall is the total wall area of walls adjacent to another conditioned living unit, not including common foundation and attic walls.

(c) 	For fenestrations facing within 15 degrees of due south that are directly coupled to thermal storage mass, the winter interior shade coefficient shall be permitted to increase to 0.95 in the proposed design.

(d) 	Where Leakage Area (L) is defined in accordance with Section 5.1 of ASHRAE Standard 119 and where:

SLA = L / CFA (where L and CFA are in the same units).

(e) 	Tested envelope leakage shall be determined in accordance with Section 5.1 of ASHRAE Standard 119 and documented by a Certified Class 1 Florida Rater. Hourly calculations using the procedures given in the 2005 ASHRAE Handbook of Fundamentals, Chapter 27, page 27.21, equation 40 (Sherman-Grimsrud model) using Shelter Class 4 shall be used to determine the air exchange rates resulting from infiltration.

(f) 	The combined air exchange rate for infiltration and mechanical ventilation shall be determined in accordance with Equation 43 of ASHRAE Handbook of Fundamentals page 27.23.

(g)	 Thermal storage element shall mean a component not normally part of the floors, walls, or ceilings that is part of a passive solar system, and that provides thermal storage such as enclosed water columns, rock beds, or phase change containers. A thermal storage element must be in the same room as fenestration that faces within 15 degrees of due south, or must be connected to such a room with pipes or ducts that allow the element to be actively charged.

(h) 	For a Proposed Design with multiple heating, or cooling, or water heating systems using different fuel types, each system shall be included in the performance calculations. the applicable system capacities and fuel types shall be weighted in accordance with the loads distribution (as calculated by accepted engineering practice for that equipment and fuel type) of the subject multiple systems.For the Standard Reference Design, the prevailing federal minimum efficiency shall be assumed except that the efficiencies given in Table-B 1.1.2(2) 405.5.2(2) below will be assumed when:

1) 	A type of device not covered by NAECA is found in the As-Built Home;

2) 	The Proposed Design is heated by electricity using a device other than an air source heat pump; or

3) 	The Proposed Design does not contain one or more of the required HVAC equipment systems.

[4181]

TABLE B-1.1.2(2) 405.5.2(2)
DEFAULT STANDARD REFERENCE DESIGN HOME

Heating and Cooling Equipment Efficiencies(i) (k) (m) (n)

| As-Built Home Fuel | Function | Baseline Home Device |
| --- | --- | --- |
| Electric | Heating | 7.7 HSPF air source heat pump |
| Non-electric warm air furnace or space heater | Heating | 78% AFUE gas furnace |
| Non-electric boiler | Heating | 80% AFUE gas boiler |
| Any type | Cooling | 13 SEER electric air conditioner |

(i) 	For a Proposed Design without a proposed heating system, a heating system with the prevailing federal minimum efficiency shall be assumed for both the Standard Reference Design home and Proposed Design. For electric heating systems, the prevailing federal minimum efficiency air-source heat pump shall be selected.

(j) 	For a Proposed Design home without a proposed cooling system, an electric air conditioner with the prevailing federal minimum efficiency shall be assumed for both the Standard Reference Design and the Proposed Design.

(k)	For a Proposed Design home with a non-storage type water heater, a 40-gallon storage-type water heater with the prevailing federal minimum energy factor for the same fuel as the predominant fuel type. For the case of a Proposed Design home without a proposed water heater, a 40-gallon storage-type water heater with the prevailing federal minimum efficiency for the same fuel as the predominant heating fuel type shall be assumed for both the Proposed Design and Standard Reference Design.

(l) 	Tested duct leakage shall be determined and documented by a Certified Class 1 Florida Rater.

B-1.1.3 Equipment calculation of End Use Energy Loads for Code Compliance Determination. The energy loads for heating, cooling and hot water in the Proposed Design home shall be normalized to account for the differences in improvement potential that exist across equipment types using the following formula in accordance with the paper "The HERS Rating Method and the Derivation of the Normalized Modified Loads Method," Research Report No. FSEC-RR-54-00, Florida Solar Energy Center.

nMEUL = REUL * (nEC_x /EC_r)

where:

nMEUL = normalized Modified End Use Loads (for heating, cooling or hot water) as computed using Commission approved software EnergyGauge USA Fla/Res.

REUL = Standard Reference Design Home End Use Loads (for heating, cooling or hot water) as computed using Commission approved software EnergyGauge USA Fla/Res.

EC_r = 	estimated Energy Consumption for the Standard Reference Design Home’s end uses (for heating, including auxiliary electric consumption, cooling or hot water) as computed using Commission approved software EnergyGauge USA Fla/Res.

and where: 	nEC_x = (a* EEC_x – b)*(EC_x * EC_r * DSE_r) / ( EEC_x * REUL)

where:

nEC_x = normalized Energy Consumption for Proposed Design’s end uses (for heating, including auxiliary electric consumption, cooling or hot water) as computed using Commission approved software EnergyGauge USA Fla/Res.

EC_r = estimated Energy Consumption for Standard Reference Design home’s end uses (for heating, including auxiliary electric consumption, cooling or hot water) as computed using Commission approved software EnergyGauge USA Fla/Res.

EC_x = estimated Energy Consumption for the Proposed Design home’s end uses (for heating, including auxiliary electric consumption, cooling or hot water) as computed using Commission approved software EnergyGauge USA Fla/Res.

EEC_x = Equipment Efficiency Coefficient for the Standard Reference Design home’s equipment, such that

EEC_x equals the energy consumption per unit load in like units as the load, and as derived from the Manufacturer’s Equipment Performance Rating (MEPR) such that

EEC_x equals 1.0 / MEPR for AFUE, COP or EF ratings, or such that EEC_x equals 3.413 / MEPR for HSPF, EER or SEER ratings.

DSE_r = REUL/EC_r * EEC_r

For simplified system performance methods, DSE_r equals 0.80 for heating and cooling systems. However, for detailed modeling of heating and cooling systems, DSE_r may be less than 0.80 as a result of part load performance degradation, coil air flow degradation, improper system charge and auxiliary resistance heating for heat pumps. Except as otherwise provided by these Standards, where detailed systems modeling is employed, it must be applied equally to both the Standard Reference Design and the Proposed Design homes.

EEC_r = Equipment Efficiency Coefficient for the Standard Reference Design home’s equipment, such that EEC_r equals the energy consumption per unit load in like units as the load, and as derived from the Manufacturer’s Equipment Performance Rating (MEPR) such that EEC_r equals 1.0 / MEPR for AFUE, COP or EF ratings, or such that EEC_r equals 3.413 / MEPR for HSPF, EER or SEER ratings.

REUL = Standard Reference Design home End Use Loads (for heating or cooling) as 
computed using Commission approved software EnergyGauge USA Fla/Res.

[Mod 4752]

and where the coefficients ‘a’ and ‘b’ are as defined by Table B 1.1.3.

TABLE B-1.1.3

COEFFICIENTS ‘a’ AND ‘b’

| Fuel type and End Use | a | b |
| --- | --- | --- |
| Electric space heating Fossil fuel* space heating Biomass space heating Electric air conditioning Electric water heating Fossil fuel* water heating | 2.2561 1.0943 0.8850 3.8090 0.9200 1.1877 | 0 0.4043 0.4047 0 0 1.0130 |

*Such as natural gas, LP, fuel oil

B-1.1.3.1 Following normalization of the heating, cooling and hot water energy consumptions for the Proposed Design home as specified in Section B-1.1.2 above, the Standard Reference Design home’s total reference end use loads for heating, cooling and hot water (REULtot) shall be compared with the Proposed Design home’s total normalized modified end use loads for heating, cooling and hot water (nMEULtot).  If the total normalized modified loads of the Proposed Design home (nMEULtot) are equal to or less than the total reference loads of the Standard Reference Design home (REULtot), the Proposed Design complies with this code.

B-2.0 Commercial and Residential ≥ 3 stories

B-2.1 506.5 Calculation procedure. Except as specified by this section, the standard reference design and proposed design shall be configured and analyzed using identical methods and techniques. The Standard Reference Design totals for the Total Building Performance compliance method shall be adjusted by a factor of 0.80 to make the code 20 percent more stringent than the “2007” Florida energy code’s Standard Reference Design (Baseline) features.

B-2.2 506.5.1 Building specifications. The standard reference design and proposed design shall be configured and analyzed as specified by Table B-2.2   506.5.1(1) shall include by reference all notes contained in Table 502.2(1) developed in accordance with the criteria in Table 506.5.1(1).

B-2.3 506.6 Calculation software tools. Calculation procedures used to comply with this section shall be only those included in the EnergyGauge Summit Fla/Com or other compliance software tools approved by the Florida Building Commission to be capable of calculating the annual energy consumption of all building elements that differ between the standard reference design and the proposed design and shall include the following capabilities. [4467]

1. Computer generation of the standard reference design using only the input for the proposed design. The calculation procedure shall not allow the user to directly modify the building component characteristics of the standard reference design.

2. Building operation for a full calendar year (8760 hours).

3. Climate data for a full calendar year (8760 hours) and shall reflect approved coincident hourly data for temperature, solar radiation, humidity and wind speed for the building location.

4. Ten or more thermal zones.

5. Thermal mass effects.

6. Hourly variations in occupancy, illumination, receptacle loads, thermostat settings, mechanical ventilation, HVAC equipment availability, service hot water usage and any process loads.

7. Part-load performance curves for mechanical equipment.

8. Capacity and efficiency correction curves for mechanical heating and cooling equipment.

9. Printed code official inspection checklist listing each of the proposed design component characteristics from Table 506.5.1(1) determined by the analysis to provide compliance, along with their respective performance ratings (e.g., R-value, U-factor, SHGC, HSPF, AFUE, SEER, EF, etc.).

TABLE B-2.2 506.5.1(1)

SPECIFICATIONS FOR THE STANDARD REFERENCE AND PROPOSED DESIGNS

| BUILDING COMPONENT/ CHARACTERISTICS | STANDARD REFERENCE DESIGN | PROPOSED DESIGN |
| --- | --- | --- |
| Design model | The standard reference design shall be developed by modifying the proposed design as described in this table. Except as specifically instructed in this table, all building systems and equipment shall be modeled identically in the standard reference design and proposed design. | (a) The simulation model of the proposed design shall be consistent with the design documents, including proper accounting of fenestration and opaque envelope types and area; interior lighting power and controls; HVAC system types, sizes, and controls; and service water heating systems and controls. (b) All conditioned spaces in the proposed design shall be simulated as being both heated and cooled even if no cooling or heating system is being installed. (c) When the energy cost budget method is applied to buildings in which energy-related features have not yet been designed (e.g., a lighting system), those yet-to-be-designed features shall be described in the proposed design so that they minimally comply with applicable mandatory and prescriptive requirements of this code. Where the space classification for a building is not known, the building shall be categorized as an office building. |
| Additions and alterations | Same as proposed | It is acceptable to demonstrate compliance using building models that exclude parts of the existing building provided all of the following conditions are met: (a) Work to be performed under the current permit application in excluded parts of the building shall meet the applicable mandatory and prescriptive requirements of this code. (b) Excluded parts of the building are served by HVAC systems that are entirely separate from those serving parts of the building that are included in the building model. (c) Design space temperature and HVAC system operating setpoints and schedules, on either side of the boundary between included and excluded parts of the building, are identical. (d) If a declining block or similar utility rate is being used in the analysis and the excluded and included parts of the building are on the same utility meter, the rate shall reflect the utility block or rate for the building plus the addition. |
| Space use classification | Same as proposed. | The space use classification shall be chosen in accordance with Table 505.5.1.2 for all areas of the building covered by this permit. Where the space use classification for a building is not known, the building shall be categorized as an office building. More than one building type category may be used in a building if it is a mixed-use facility. |
| Roofs | Type: Insulation entirely above-deck Gross area: same as proposed U-Factor: from Table 502.1.2 Solar Absorptance: 0.75 Emittance: 0.90 | As proposed As proposed As proposed As proposed As proposed |
| Walls, above-grade | Type: Mass wall if proposed wall is mass; otherwise steel-framed wall Gross Area: same as proposed U-Factor: from Table 502.1.2 Solar Absorptance: 0.75 Emittance: 0.90 | As proposed As proposed As proposed As proposed As proposed |
| Walls, below-grade | Type: Mass wall Gross Area: same as proposed U-Factor: from Table 502.1.2 with insulation layer on interior side of walls | As proposed As proposed As proposed |
| Floors, above-grade | Type: joist/framed floor Gross Area: same as proposed U-Factor: from Table 502.1.2 | As proposed As proposed As proposed |
| Floors, slab-on-grade | Type: Unheated F-Factor: from Table 502.1.2 | As proposed As proposed |
| Doors | Type: Swinging Area: Same as proposed U-Factor: from Table 502.2(1) | As proposed As proposed As proposed |
| Glazing | Area: (a) The proposed glazing area; where the proposed glazing area is less than 40 % of above-grade wall area (b) 40 % of above-grade wall area; where the proposed glazing area is 40 % or more of the above grade wall Area U-factor: from Table 502.3 SHGC: from Table 502.3 except that for climates with no requirement (NR) SHGC = 0.40 shall be used External Shading and PF: None | As proposed As proposed As proposed As proposed |
| Skylights | Area: (a) The proposed skylight area; where the proposed skylight area is less than 3 percent of gross area of roof assembly (b) 3 percent of gross area of roof assembly; where the proposed skylight area is 3 percent or more of gross area of roof assembly U-factor: from Table 502.3 SHGC: from Table 502.3 except that for climates with no requirement (NR) SHGC = 0.40 shall be used | As proposed As proposed As proposed |
| Building envelope | The standard reference design shall have identical conditioned floor area and identical exterior dimensions and orientations as the proposed design, except as noted in (a), (b), and (c) in this clause. (a) Opaque assemblies such as roof, floors, doors, and walls shall be modeled as having the same heat capacity as the proposed design but with the minimum U-factor required in the Commission approved compliance software EnergyGauge Summit Fla/Com program1 for new buildings or additions and alterations. (b) Roof albedo—All roof surfaces shall be modeled with a reflectivity of 0.3. (c) Fenestration—No shading projections are to be modeled; fenestration shall be assumed to be flush with the exterior wall or roof. If the fenestration area for new buildings or additions exceeds the maximum allowed by the Commission approved compliance software EnergyGauge Summit Fla/Com program 1, the area shall be reduced proportionally along each exposure until the limit set in the Commission approved compliance software EnergyGauge Summit Fla/Com program 1 is met. Fenestration U-factor shall be the minimum required for the climate, and the solar heat gain coefficient shall be the maximum allowed for the climate and orientation. The fenestration model for envelope alterations shall reflect the limitations on area, U-factor, and solar heat gain coefficient as allowed by Section 101.4.3. | All components of the building envelope in the proposed design shall be modeled as shown on architectural drawings or as installed for existing building envelopes. Exceptions: The following building elements are permitted to differ from architectural drawings. (a) Any envelope assembly that covers less than 5% of the total area of that assembly type (e.g., exterior walls) need not be separately described. If not separately described, the area of an envelope assembly must be added to the area of the adjacent assembly of that same type. (b) Exterior surfaces whose azimuth orientation and tilt differ by no more than 45 degrees and are otherwise the same may be described as either a single surface or by using multipliers. (c) For exterior roofs other than roofs with ventilated attics, the roof surface may be modeled with a reflectance of 0.45 if the reflectance of the proposed design roof is greater than 0.70 and its emittance is greater than 0.75. The reflectance and emittance shall be determined by a laboratory accredited by a nationally recognized accreditation organization and shall be labeled and certified by the manufacturer. All other roof surfaces shall be modeled with a reflectance of 0.3. Manually operated fenestration shading devices such as blinds or shades shall not be modeled. Permanent shading devices such as fins, overhangs, and light shelves shall be modeled. (d) Manually operated fenestration shading devices such as blinds or shades shall not be modeled. Permanent shading devices such as fins, overhangs, and lightshelves shall be modeled. |
| Lighting, interior | Lighting power in the standard reference design shall be determined using the same categories as the proposed design with lighting power set equal to the maximum allowed for the corresponding method and category in Table 505.5.1.2. Power for fixtures not included in the lighting power density calculation shall be modeled identically in the proposed design and standard reference design. Lighting controls shall be the minimum required. The interior lighting power shall be determined in accordance with Table 505.5.2. Where the occupancy of the building is not known, the lighting power density shall be 1.0 Watt per square foot (10.73 W/m2) based on the categorization of buildings with unknown space classification as offices | Lighting power in the proposed design shall be determined as follows: (a) Where a complete lighting system exists, the actual lighting power shall be used in the model. (b) Where a lighting system has been designed, lighting power shall be determined in accordance with 505.5.1.2. (c) Where no lighting exists or is specified, lighting power shall be determined for the appropriate building type. (d) Lighting system power shall include all lighting system components shown or provided for on plans (including lamps, ballasts, task fixtures, and furniture-mounted fixtures). As proposed |
| Lighting, exterior | The lighting power shall be determined in accordance with Table 505.6.2. Areas and dimensions of tradable and non-tradable surfaces shall be the same as proposed. | As proposed. |
| Internal gains | Same as proposed | Receptacle, motor and process loads shall be modeled and estimated based on the space use classification. All end-use load components within and associated with the building shall be modeled to include, but not limited to the following: exhaust fans, parking garage ventilation fans, exterior building lighting, swimming pool heaters and pumps, elevators, escalators, refrigeration equipment and cooking equipment. |
| Schedules | Same as proposed | Operating schedules shall include hourly profiles for daily operation and shall account for variations between weekdays, weekends, holidays, and any seasonal operation. Schedules shall model the time-dependant variations in occupancy, illumination, receptacle loads, thermostat settings, mechanical ventilation, HVAC equipment availability, service hot water usage, and any process loads. The schedules shall be typical of the proposed building type as determined by the designer and approved by the jurisdiction. Required schedules shall be identical for the proposed design and standard reference design. |
| Mechanical Ventilation | Same as proposed | As proposed, in accordance with Section 503.2.5. |
| HVAC systems | The HVAC system type and related performance parameters for the standard reference design shall be determined from Figure B-2.6.1, the system descriptions in Table B-2.6.1 and accompanying notes. | The HVAC system type and all related performance parameters, such as equipment capacities and efficiencies, in the proposed design shall be determined as follows: (a) Where a complete HVAC system exists, the model shall reflect the actual system type using actual component capacities and efficiencies. (b) Where an HVAC system has been designed, the HVAC model shall be consistent with design documents. Mechanical equipment efficiencies shall be adjusted from actual design conditions to the standard rating conditions specified in Sections 503.3 or 503.4, if required by the simulation model. (c) Where no heating system exists or no heating system has been specified, the heating system shall be modeled as fossil fuel. The system characteristics shall be identical to the system modeled in the standard reference design. (d) Where no cooling system exists or no cooling system has been specified, the cooling system shall be modeled as an air-cooled single-zone system, one unit per thermal block. The system characteristics shall be identical to the system modeled in the standard reference design. |
| Thermal blocks | Same as proposed | See criteria in Section B-2.6.2. |
| Heating systems | Fuel Type: same as proposed design Equipment Type1: from Table 506.5.1(2) and Table 506.5.1(3) Efficiency: from Table 503.2.3(4) and Table 503.2.3(5) Capacity2: sized proportionally to the capacities in the proposed design based on sizing runs, and shall be established such that no smaller number of unmet heating load hours and no larger heating capacity safety factors are provided than in the proposed design. | As proposed As proposed As proposed As proposed |
| Cooling systems | Fuel Type: same as proposed design Equipment Type3: from Table 506.5.1(2) and Table 506.5.1(3) Efficiency: from Table 503.2.3(1), Table 503.2.3(2) and Table 503.2.3(3) Capacityb: sized proportionally to the capacities in the proposed design based on sizing runs, and shall be established such that no smaller number of unmet cooling load hours and no larger cooling capacity safety factors are provided than in the proposed design. Economizer4: same as proposed, in accordance with Section 503.4.1 | As proposed As proposed As proposed As proposed As proposed |
| Service water heating | The service hot water system type and related performance in the standard reference design shall be identical to the proposed design except where a combination total space heating and water heating system is installed in a building. In this case the boiler shall be split into a separate space heating boiler and hot water heater with efficiency requirements set to the least efficient allowed. Fuel type: same as proposed Efficiency: from Table 504.2 Capacity: same as proposed Where no service water hot water system exists or is specified in the proposed design, no service hot water heating shall be modeled | The service hot water system type and all related performance parameters, such as equipment capacities and efficiencies, in the proposed design shall be determined as follows: (a) Where a complete service hot water system exists, the model shall reflect the actual system type using actual component capacities and efficiencies. (b) Where a service hot water system has been designed, the service hot water model shall be consistent with design documents. (c) Where no service hot water system exists or is specified, no service hot water heating shall be modeled. As proposed As proposed As proposed |
| Miscellaneous loads | Receptacle, motor and process loads shall be modeled and estimated based on the building type or space type category and shall be assumed to be identical in the proposed and standard reference design. These loads shall be included in simulations of the building and shall be included when calculating the energy cost budget and design energy cost. All end use load components within and associated with the building shall be modeled, unless specifically excluded by the Commission approved compliance software EnergyGauge Summit Fla/Com program 1: including, but not limited to, exhaust fans, parking garage ventilation fans, exterior building lighting, swimming pool heaters and pumps, elevators and escalators, refrigeration equipment, and cooking equipment. | Receptacle, motor, and process loads shall be modeled and estimated based on the building type or space type category and shall be assumed to be identical in the proposed and standard reference design. These loads shall be included in simulations of the building and shall be included when calculating the energy cost budget and design energy cost. All end-use load components within and associated with the building shall be modeled, unless specifically excluded by the EnergyGauge Summit Fla/Com program1: including, but not limited to, exhaust fans, parking garage ventilation fans, exterior building lighting, swimming pool heaters and pumps, elevators and escalators, refrigeration equipment, and cooking equipment. |

1 Where no heating system exists or no heating system has been specified, the heating system shall be modeled as fossil fuel. The system characteristics shall be identical in both the Standard Reference Design and Proposed Design.

2 The ratio between the capacities used in the annual simulations and the capacities determined by sizing runs shall be the same for both the Standard Reference Design and Proposed Design.

3 Where no cooling system exists or no cooling system has been specified, the cooling system shall be modeled as an air-cooled single-zone system, one unit per thermal zone. The system characteristics shall be identical in both the Standard Reference Design and Proposed Design.

4 If an economizer is required as per Table 503.3.1 (1), and if no economizer exists or is specified in the proposed design, then a supply air economizer shall be provided in accordance with Section 503.4.1.

1 Specifications utilized in the Commission approved compliance software EnergyGauge Summit Fla/Com program are those specified by Chapter 11 of ASHRAE Standard 90.1-2004.

[MOD 4753]

B-2.6 HVAC systems.

B-2.6.1 Standard reference design.  The HVAC system type and related performance parameters for the standard reference design shall be determined from Figure B-2.6.1, the system descriptions in Table B-2.6.1 and accompanying notes, and the following rules.

(a) Components and parameters not listed in Figure B-2.6.1 and Table B-2.6.1 or otherwise specifically addressed in this subsection shall be identical to those in the proposed design.

Exception: Where there are specific requirements in Section 503, the component efficiency in the standard reference design shall be adjusted to the lowest efficiency level allowed by the requirement for that component type.

(b) All HVAC and service water heating equipment in the standard reference design shall be modeled at the minimum efficiency levels, both part load and full load, in accordance with Sections 503 and 504.

(c) Where efficiency ratings,such as EER and COP, include fan energy, the descriptor shall be broken down into its components so that supply fan energy can be modeled separately. Supply and return/relief system fans shall be modeled as operating at least whenever the spaces served are occupied except as specifically noted in Table B-2.6.1 506.5.1(3).

(d) Minimum outdoor air ventilation rates shall be the same for both the standard reference design and proposed building.

(e) Reserved.

(f) If the proposed design system has a preheat coil, the standard reference design’s system shall be modeled with a preheat coil controlled in the same manner.

(g) System design supply air rates for the standard reference budget building design shall be based on a supply-air-to-room-air temperature difference of 20°F. If return or relief fans are specified in the proposed design, the standard reference budget building design shall also be modeled with the same fan type sized for the budget system supply fan air quantity less the minimum outdoor air, or 90% of the supply fan air quantity, whichever is larger.

(h) Fan system efficiency (BHP per cfm of supply air including the effect of belt losses but excluding motor and motor drive losses) shall be the same as the proposed design or up to the limit prescribed in Section 503.2.10.1, whichever is smaller. If this limit is reached, each fan shall be proportionally reduce. d in brake horsepower until the limit is met. Fan electrical power shall then be determined by adjusting the calculated fan HP by the minimum motor efficiency prescribed by Section 505.7.5 for the appropriate motor size for each fan.

(i) The equipment capacities for the standard reference design shall be sized proportionally to the capacities in the proposed design based on sizing runs; i.e., the ratio between the capacities used in the annual simulations and the capacities determined by the sizing runs shall be the same for both the proposed design and standard reference design. Unmet load hours for the proposed design shall not differ from unmet load hours for the standard reference design by more than 50 hours.

(j) Each HVAC system in a proposed design is mapped on a one-to-one correspondence with one of eleven HVAC systems in the standard reference design. To determine the standard reference design system:

1. Enter Figure B-2.6.1 at “Water” if the proposed design system condenser is water or evaporatively cooled; enter at “Air” if the condenser is air-cooled. Closed-circuit dry coolers shall be considered air-cooled. Systems utilizing district cooling shall be treated as if the condenser water type were “water.” If no mechanical cooling is specified or the mechanical cooling system in the proposed design does not require heat rejection, the system shall be treated as if the condenser water type were “Air.” For proposed designs with ground-source or groundwater-source heat pumps, the standard reference design system shall be water-source heat pump (System 6).

2. Select the path that corresponds to the proposed design heat source: electric resistance, heat pump (including air-source and water-source), or fuel-fired. Systems utilizing district heating (steam or hot water) shall be treated as if the heating system type were “Fossil Fuel.” Systems with no heating capability shall be treated as if the heating system type were “Fossil Fuel.” For systems with mixed fuel heating sources, the system or systems that use the secondary heating source type (the one with the smallest total installed output capacity for the spaces served by the system) shall be modeled identically in the standard reference design and the primary heating source type shall be used in Table B-2.6.1  to determine standard reference system type.

3. Select the standard reference design system category: The system under “Single Zone Residential System” shall be selected if the HVAC system in the proposed design is a single-zone system and serves a residential space. The system under “Single Zone Nonresidential System” shall be selected if the HVAC system in the proposed design is a single-zone system and serves other than residential spaces. The system under “All Other” shall be selected for all other cases.

B-2.6.2 506.5.2 Thermal blocks. The standard reference design and proposed design shall be analyzed using identical thermal blocks as required in Section B-2.6.2.1506.5.21.2.1, B-2.6.2.2 506.2.2.2 or B 2.6.2.3 506.5.2.2.3

B-2.6.2.1 506.5.2.2.1 HVAC zones designed. Where HVAC zones are defined on HVAC design drawings, each HVAC zone shall be modeled as a separate thermal block.

Exception: Different HVAC zones shall be allowed to be combined to create a single thermal block or identical thermal blocks to which multipliers are applied provided:

1. The space use classification is the same throughout the thermal block.

2. All HVAC zones in the thermal block that are adjacent to glazed exterior walls face the same orientation or their orientations are within 45 degrees (0.79 rad) of each other.

3. All of the zones are served by the same HVAC system or by the same kind of HVAC system.

B-2.6.2.2 506.5.2.2.2 HVAC zones not designed. Where HVAC zones have not yet been designed, thermal blocks shall be defined based on similar internal load densities, occupancy, lighting, thermal and temperature schedules, and in combination with the following guidelines:

1. Separate thermal blocks shall be assumed for interior and perimeter spaces. Interior spaces shall be those located more than 15 feet (4572 mm) from an exterior wall. Perimeter spaces shall be those located closer than 15 feet (4572 mm) from an exterior wall.

2. Separate thermal blocks shall be assumed for spaces adjacent to glazed exterior walls: a separate zone shall be provided for each orientation, except orientations that differ by no more than 45 degrees (0.79 rad) shall be permitted to be considered to be the same orientation. Each zone shall include floor area that is 15 feet (4572 mm) or less from a glazed perimeter wall, except that floor area within 15 feet (4572 mm) of glazed perimeter walls having more than one orientation shall be divided proportionately between zones

3. Separate thermal blocks shall be assumed for spaces having floors that are in contact with the ground or exposed to ambient conditions from zones that do not share these features.

4. Separate thermal blocks shall be assumed for spaces having exterior ceiling or roof assemblies from zones that do not share these features.

B-2.6.2.3 506.5.2.2.3 Multiple family residential buildings. Residential spaces shall be modeled using one thermal block per space except that those facing the same orientations are permitted to be combined into one thermal block. Corner units and units with roof or floor loads shall only be combined with units sharing these features

FIGURE B-2.6.1 506.5.1(2)

HVAC SYSTEMS MAP

| Condenser Cooling Sourcea | Heating System Classificationb | Standard Reference Design HVC System Typec |  |  |
| --- | --- | --- | --- | --- |
|  |  | Single Zone Residential System | Single Zone Non-Residential System | All Other |
| Water/Ground | Electric Resistance | System 5 | System 5 | System 1 |
|  | Heat Pump | System 6 | System 6 | System 6 |
|  | Fossil Fuel | System 7 | System 7 | System 2 |
| Air/None | Electric Resistance | System 8 | System 9 | System 3 |
|  | Heat Pump | System 8 | System 9 | System 3 |
|  | Fossil Fuel | System 10 | System 11 | System 4 |

a. Select “Water/Ground” if the proposed design system condenser is water or evaporatively cooled; select “Air/None” if the condenser is air-cooled. Closed-circuit dry-coolers shall be considered air-cooled. Systems utilizing district cooling shall be treated as if the condenser water type were “water.” If no mechanical cooling is specified or the mechanical cooling system in the proposed design does not require heat rejection, the system shall be treated as if the condenser water type were “Air.” For proposed designs with ground-source or groundwater-source heat pumps, the standard reference design HVAC system shall be water-source heat pump (System 6).

b. Select the path that corresponds to the proposed design heat source: electric resistance, heat pump (including air-source and water-source), or fuel-fired. Systems utilizing district heating (steam or hot water) shall be treated as if the heating system type were “Fossil Fuel.” Systems with no heating capability shall be treated as if the heating system type were “Fossil Fuel.” For systems with mixed fuel heating sources, the system or systems that use the secondary heating source type (the one with the smallest total installed output capacity for the spaces served by the system) shall be modeled identically in the standard reference design and the primary heating source type shall be used to determine standard reference design HVAC system type.

c. Select the standard reference design HVAC system category: The system under “Single Zone Residential System” shall be selected if the HVAC system in the proposed design is a single-zone system and serves a residential space. The system under “Single Zone Nonresidential System” shall be selected if the HVAC system in the proposed design is a single-zone system and serves other than residential spaces. The system under “All Other” shall be selected for all other cases.

TABLE B-2.6.1  506.5.1(3)

SPECIFICATIONS FOR THE STANDARD REFERENCE DESIGN HVAC SYSTEM DESCRIPTIONS

| System No. | System Type | Fan Control | Cooling Type | Heating Type |
| --- | --- | --- | --- | --- |
| 1 | Variable air volume with parallel fan-powered boxes a | VAV d | Chilled Water e | Electric Resistance |
| 2 | Variable air volume with reheat b | VAV d | Chilled Water e | Hot Water Fossil Fuel Boiler f |
| 3 | Packaged variable air volume with parallel fan-powered boxes a | VAV d | Direct Expansion c | Electric Resistance |
| 4 | Packaged variable air volume with reheat b | VAV d | e | Hot Water Fossil Fuel Boiler f |
| 5 | Two-pipe fan-coil | Constant Volume i | e | Electric Resistance |
| 6 | Water-source heat pump | Constant Volume i | Direct Expansion c | Electric Heat Pump and Boiler g |
| 7 | Four-pipe fan coil | Constant Volume i | Chilled Water e | Hot Water Fossil Fuel Boiler f |
| 8 | Packaged terminal heat pump | Constant Volume i | Direct Expansion c | Electric Heat Pump h |
| 9 | Packaged rooftop heat pump | Constant Volume i | Direct Expansion c | Electric Heat Pump h |
| 10 | Packaged terminal air conditioner | Constant Volume i | Direct Expansion | Hot Water Fossil Fuel Boiler f |
| 11 | Packaged rooftop air conditioner | Constant Volume i | Direct Expansion | Fossil Fuel Furnace |

a. VAV with parallel boxes: Fans in parallel VAV fan-powered boxes shall be sized for 50% of the peak design flow rate and shall be modeled with 0.35 W/cfm fan power. Minimum volume setpoints for fan-powered boxes shall be equal to the minimum rate for the space required for ventilation consistent with 503.4.5 Exception (5) 1. Supply air temperature setpoint shall be constant at the design condition.

b. VAV with reheat: Minimum volume setpoints for VAV reheat boxes shall be 0.4 cfm/ft2 of floor area, or the minimum ventilation rate, whichever is larger. Supply air temperature shall be reset based on zone demand from the design temperature difference to a 10°F temperature difference under minimum load conditions. Design air flow rates shall be sized for the reset supply air temperature, i.e., a 10°F temperature difference. [4429]

c. Direct Expansion: The fuel type for the cooling system shall match that of the cooling system in the proposed design.

d. VAV: Constant volume can be modeled if the system qualifies for Exception (1) to 503.4.5. When the proposed design system has a supply, return, or relief fan motor 25 hp or larger, the corresponding fan in the VAV system of the standard reference design shall be modeled assuming a variable speed drive. For smaller fans, a forward curved centrifugal fan with inlet vanes shall be modeled. If the proposed design’s system has a direct digital control system at the zone level, static pressure setpoint reset based on zone requirements in accordance with 503.4.2 shall be modeled.

e. Chilled Water: For systems using purchased chilled water, the chillers are not explicitly modeled and chilled water costs shall be based as determined in 506.3 and 506.5.2. Otherwise, the standard reference design’s chiller plant shall be modeled with chillers having the number as indicated in Table B-2.6.1A 506.5.1(4) as a function of standard reference building chiller plant load and type as indicated in Table B-2.6.1B 506.5.1(5) as a function of individual chiller load. Where chiller fuel source is mixed, the system in the standard reference design shall have chillers with the same fuel types and with capacities having the same proportional capacity as the proposed design’s chillers for each fuel type. Chilled water supply temperature shall be modeled at 44°F design supply temperature and 56°F return temperature. Piping losses shall not be modeled in either building model. Chilled water supply water temperature shall be reset in accordance with 503.4.3.4. Pump system power for each pumping system shall be the same as the proposed design; if the proposed design has no chilled water pumps, the standard reference design pump power shall be 22 W/gpm (equal to a pump operating against a 75 ft head, 65% combined impeller and motor efficiency). The chilled water system shall be modeled as primary-only variable flow with flow maintained at the design rate through each chiller using a bypass. Chilled water pumps shall be modeled as riding the pump curve or with variable-speed drives when required in 503.4.3.4. The heat rejection device shall be an axial fan cooling tower with two-speed fans if required in 503.4.4. Condenser water design supply temperature shall be 85°F or 10°F approach to design wet-bulb temperature, whichever is lower, with a design temperature rise of 10°F. The tower shall be controlled to maintain a 70°F leaving water temperature where weather permits, floating up to leaving water temperature at design conditions. Pump system power for each pumping system shall be the same as the proposed design; if the proposed design has no condenser water pumps, the standard reference design pump power shall be 19 W/gpm (equal to a pump operating against a 60 ft head, 60% combined impeller and motor efficiency). Each chiller shall be modeled with separate condenser water and chilled water pumps interlocked to operate with the associated chiller.

f. Fossil Fuel Boiler: For systems using purchased hot water or steam, the boilers are not explicitly modeled and hot water or steam costs shall be based on actual utility rates. Otherwise, the boiler plant shall use the same fuel as the proposed design and shall be natural draft. The standard reference design boiler plant shall be modeled with a single boiler if the standard reference design plant load is 600,000 Btu/h and less and with two equally sized boilers for plant capacities exceeding 600,000 Btu/h. Boilers shall be staged as required by the load. Hot water supply temperature shall be modeled at 180°F design supply temperature and 130°F return temperature. Piping losses shall not be modeled in either building model. Hot water supply water temperature shall be reset in accordance with 503.4.3.4. Pump system power for each pumping system shall be the same as the proposed design; if the proposed design has no hot water pumps, the standard reference design pump power shall be 19 W/gpm (equal to a pump operating against a 60 ft head, 60% combined impeller and motor efficiency). The hot water system shall be modeled as primary-only with continuous variable flow. Hot water pumps shall be modeled as riding the pump curve or with variable speed drives when required by 503.4.3.4.

g. Electric Heat Pump and Boiler: Water-source heat pumps shall be connected to a common heat pump water loop controlled to maintain temperatures between 60°F and 90°F. Heat rejection from the loop shall be provided by an axial fan closed-circuit evaporative fluid cooler with two-speed fans if required in 503.4.2. Heat addition to the loop shall be provided by a boiler that uses the same fuel as the proposed design and shall be natural draft. If no boilers exist in the proposed design, the standard reference building boilers shall be fossil fuel. The standard reference design boiler plant shall be modeled with a single boiler if the standard reference design plant load is 600,000 Btu/h or less and with two equally sized boilers for plant capacities exceeding 600,000 Btu/h. Boilers shall be staged as required by the load. Piping losses shall not be modeled in either building model. Pump system power shall be the same as the proposed design; if the proposed design has no pumps, the standard reference design pump power shall be 22 W/gpm, which is equal to a pump operating against a 75 foot head, with a 65% combined impeller and motor efficiency. Loop flow shall be variable with flow shutoff at each heat pump when its compressor cycles off as required by 503.4.3.3. Loop pumps shall be modeled as riding the pump curve or with variable speed drives when required by 503.4.3.4.

h. Electric Heat Pump: Electric air-source heat pumps shall be modeled with electric auxiliary heat. The system shall be controlled with a multi-stage space thermostat and an outdoor air thermostat wired to energize auxiliary heat only on the last thermostat stage and when outdoor air temperature is less than 40°F.

i. Constant Volume: Fans shall be controlled in the same manner as in the proposed design; i.e., fan operation whenever the space is occupied or fan operation cycled on calls for heating and cooling. If the fan is modeled as cycling and the fan energy is included in the energy efficiency rating of the equipment, fan energy shall not be modeled explicitly.

TABLE B-2.6.1A 506.5.1(4)

NUMBER OF CHILLERS

| TOTAL CHILLER PLANT CAPACITY | NUMBER OF CHILLERS |
| --- | --- |
| ≤300 tons | 1 |
| >300 tons, < 600 tons | 2 sized equally |
| ≥600 tons | 2 minimum with chillers added so that no chiller is larger than 800 tons, all sized equally |

TABLE B-2.6.1B 506.5.1(5)

WATER CHILLER TYPES

| INDIVIDUAL CHILLER PLANT CAPACITY | ELECTRIC CHILLER TYPE | FOSSIL FUEL CHILLER TYPE |
| --- | --- | --- |
| ≤100 tons | Reciprocating | Single-effect absorption, direct fired |
| >100 tons, <300 tons | Screw | Double-effect absorption, direct fired |
| ≥300 tons | Centrifugal | Double-effect absorption, direct fired |