Florida Building Code, Energy Conservation

Residential Building Thermal Envelope Approach

FORM 402-2010  									All climate zones

Scope: Compliance with Section 402 of the Florida Building Code, Energy Conservation, shall be demonstrated by the use of Form 402 for single- and multiple-family residences of three stories or less in height, additions to existing residential buildings, renovations to existing residential buildings, new heating, cooling, and water heating systems in existing buildings, and site-added components of manufactured homes and manufactured buildings, as applicable.To comply, a building must meet or exceed all of the energy efficiency requirements on Table 402A and all applicable mandatory requirements summarized in Table 402B of this form. If a building does not comply with this method or Alternate Form 402, the printout from FlaResCheck, it may still comply under Section 405 of the Florida Building Code, Energy Conservation.

| PROJECT NAME: AND ADDRESS: |  | BUILDER: |
| --- | --- | --- |
|  |  | PERMITTING OFFICE: |
|  |  | JURISDICTION NUMBER: |
| OWNER: |  | PERMIT NUMBER: |

General Instructions:

1. New construction which incorporates any of the following features cannot comply using this method: glass areas in excess of 20 percent of conditioned floor area, electric resistance heat and air handlers located in attics.  Additions ≤ 600 sq.ft., renovations and equipment changeouts may comply by this method with exceptions given.

2. Fill in all the applicable spaces of the “To Be Installed” column on Table 402A with the information requested. All “To Be Installed” values must be equal to or more efficient than the required levels.

3. Complete page 1 based on the “To Be Installed” column information.

4. Read the requirements of Table 402B and check each box to indicate your intent to comply with all applicable items.

5. Read, sign and date the “Prepared By” certification statement at the bottom of page 1. The owner or owner’s agent must also sign and date the form.

Check

- New construction, addition, or existing building			1.______________________	____

- Single-family detached or multiple-family attached			2. _____________________	____

- If multiple-family, number of units covered by this submission		3. _____________________	____

- Is this a worst case? (yes/no)					4. _____________________	____

- Conditioned floor area (sq. ft.)					5. _____________________	____

- Glass type and area:

- U-factor:								6a.____________________	____

- SHGC:								6b.____________________	____

- Glass area							6c.____________________	____

- Percentage of glass to floor area					7. _____________________	____

- Floor type, area or perimeter, and insulation:

  - Slab-on-grade (R-value)					8a. ____________________	____

  - Wood, raised (R-value)					8b. ____________________	____

  - Wood, common (R-value)					8c. ____________________	____

  - Concrete, raised (R-value)					8d. ____________________	____

  - Concrete, common (R-value)				8e. ____________________	____

- Wall type, area and insulation:

  - Exterior:      1. Wood frame (Insulation R-value)		9a1.____________________	____

2.  Masonry (Insulation R-value)			9a2.____________________	____

  - Adjacent:    1.  Wood frame (Insulation R-value)		9b1.____________________	____

2.  Masonry (Insulation R-value)			9b2.____________________	____

- Ceiling type, area and insulation

  - Attic (Insulation R-value)					10a.____________________	____

  - Single assembly (Insulation R-value)			10b.____________________	____

- Air distribution system: Duct insulation, location, Qn

  - Duct location, insulation					11a.____________________	____

  - AHU location						11b.____________________	____

c)    Qn, Test report attached (≤0.03; yes/no)			11c.____________________	____

- Cooling system: a) type b) efficiency					12a.____________________	____

12b.____________________	____

- Heating system: a) type b) efficiency:				13a.____________________	____

13b. ____________________	____

- HVAC sizing calculation:  attached					14.  _____________________	____

- Water heating system: a) type b) efficiency				15a. ____________________	____											15b. ____________________	____

| I herby certify that the plans and specifications covered by this form are in compliance with the Florida energy code. PREPARED BY:____________________________ Date__________ I hereby certify that this building is in compliance with the Florida energy code. OWNER/AGENT:___________________________ Date:__________ | Review of plans and specifications covered by this form indicate compliance with the Florida energy code. Before construction is complete, this building will this building will be inspected for compliance in accordance with Section 553.908, F.S. CODE OFFICIAL:______________________________ Date:_________ |
| --- | --- |

| TABLE 402A ALL CLIMATE ZONES |  |  |  |
| --- | --- | --- | --- |
| BUILDING COMPONENT | PERFORMANCE CRITERIA1 | INSTALLED VALUES |  |
| Windows 2: Skylights | U-Factor ≤ 0.65 SHGC = 0.30 % of CFA ≤ 20 % U-factor ≤ 0.75 | U-Factor = SHGC = % of CFA = U-factor = |  |
| Doors: Exterior door U-factor | U-factor ≤ 0.65 | U-factor: |  |
| Floors: Slab-on-Grade Over unconditioned spaces3 | No requirement R-13 | R-Value = |  |
| Walls – Ext. and Adj. 3 Frame Mass 3 Interior of wall: Exterior of wall | R-13 R-7.8 R-6 | R-Value = R-Value = R-Value = |  |
| Ceilings3: Reflectance | R=30 0.25 | R-Value = Reflectance= | Test report Attached? Yes/No |
| Air distribution system4 Ductwork & air handling unit: Unconditioned space Conditioned space Duct R-value Air leakage Qn | Not allowed R-value ≥ R-6 Qn ≤ 0.03 | Location: R-Value = Qn = | Test report Attached? Yes/No |
| Air conditioning systems5 | SEER = 13.0 | SEER= |  |
| Heating system Heat pump5 Cooling: Heating: Gas furnace Oil furnace Electric resistance: Not allowed5 | SEER = 13.0 HSPF = 7.7 AFUE = 78% AFUE = 78% | SEER = HSPF = AFUE = AFUE = |  |
| Water heating system (storage type): Electric6: Gas fired6 Other (describe): | 40 gal: EF = 0.92 50 gal: EF = 0.90 40 gal: EF = 0.59 50 gal: EF = 0.58 | Gallons = EF = Gallons = EF = |  |

(1) Each component present in the As Proposed home must meet or exceed each of the applicable performance criteria in order to comply with this code using this method; otherwise Section 405 compliance must be used.

(2) Windows and doors qualifying as glazed fenestration areas must comply with both the maximum U-Factor and the maximum SHGC (solar Heat Gain Coefficient) criteria and have a maximum total window area equal to or less than 20 % of the conditioned floor area (CFA); otherwise Section 405 must be used for compliance.

Exceptions: 1. Additions of 600 square feet (56 m2) or less may have a maximum glass to CFA of 50 percent.  2. Renovations with new windows under ≥2 foot overhang whose lower edge does not extend further than 8 feet from the overhang may have tinted glazing or double-pane clear glazing. Replacement skylights installed in renovations shall be double paned or single paned with a diffuser.

(3) R-values are for insulation material only as applied in accordance with manufacturers’ installation instructions. For mass walls, the “interior of wall” requirement must be met except if at least 50% of the R-6 insulation required for the “exterior of wall” is installed exterior of, or integral to, the wall.

(4) Ducts & AHU installed substantially leak free per Section 403.2.2.1. Test by Class 1 BERS rater required.

Exception: Ducts installed onto an existing air distribution system as part of an addition or renovation; duct must be R-6 installed per Sec. 503.2.7.2.

(5) For all conventional units with capacities greater than 30,000 Btu/hr.  For other types of equipment, see Tables 503.2.3(1-8 10).

Exception: Electric resistance heat prohibition does not apply to additions, renovations, and new heating systems installed in existing buildings.

(6) For other electric storage volumes, min. EF = 0.97 - (0.00132 * volume) ; for other natural gas storage volumes, min. EF = 0.67 - (0.0019 * volume)

| TABLE 402B MANDATORY REQUIREMENTS |  |  |  |
| --- | --- | --- | --- |
| Component | Section | Summary of Requirement(s) | Check |
| Air leakage | 402.4 | To be caulked, gasketed, weatherstripped or otherwise sealed. Recessed lighting IC-rated as meeting ASTM E 283. Windows and doors ≤ 0.30 cfm/sq.ft. Testing or visual inspection required. Fireplaces: gasketed doors & outdoor combustion air. |  |
| Ceilings/knee walls | 405.2.1 | R-19 space permitting. |  |
| Programmable thermostat | 403.1.1 | Where forced-air furnace is primary system, programmable thermostat is required. |  |
| Air distribution system | 403.2 | Ducts in attics or on roofs insulated to R-8; other ducts R-6. Ducts not in conditioned space tested to Qn=0.03 by Class 1 BERS rater. |  |
| Water heaters | 403.4 | Heat trap required for vertical pipe risers. Comply with efficiencies in Table 403.4.3.2. Provide switch or clearly marked circuit breaker (electric) or shutoff (gas). Circulating system pipes insulated to ≥ R-2 + accessible manual OFF switch. |  |
| Swimming pools & spas | 403.9 | Spas and heated pools must have vapor-retardant covers or a liquid cover or other means proven to reduce heat loss except if 70% of heat from site-recovered energy; where >90oF, R-12 pool cover. Off/timer switch required. Gas heaters minimum thermal efficiency=78% (82% after 4/16/13). Heat pump pool heaters minimum COP= 4.0. |  |
| Cooling/heating equipment | 403.6 | Sizing calculation performed & attached. Minimum efficiencies per Tables 503.2.3. Equipment efficiency verification required. Special occasion cooling or heating capacity requires separate system or variable capacity system. Electric heat >10kW must be divided into two or more stages. |  |
| Lighting equipment | 404.1 | At least 50% of permanently installed lighting fixtures shall be high-efficacy lamps. |  |