CHAPTER 3

DESIGN CRITERIA CLIMATE ZONES

SECTION 301

CLIMATE ZONES

301.1 General. Climate zones shown in from Figure 301.1 or Table 301.1 constitute the zones recognized for Florida by the International Energy Conservation Code. shall be used in determining the applicable requirements from Chapters 4 and 5. Locations not in Table 301.1 (outside the United States) shall be assigned a climate zone based on Section 301.3.  Prescriptive envelope compliance methods in this code, Section 402 (residential) and Section 502 (commercial) have no difference in compliance criteria by climate zone. Climate criteria for the performance-based code compliance methods, Section 405 (residential) and Section 506 (commercial), are determined by climate data from the weather data collection station nearest to the building’s location.

301.2 Warm humid counties. All Florida counties are considered Wwarm humid counties are identified in Table 301.1 by an asterisk.

FIGURE 301.1

CLIMATE ZONES

Reserved

TABLE 301.1

CLIMATE ZONES, MOISTURE REGIMES, AND WARM-HUMID DESIGNATIONS  BY STATE, COUNTY AND TERRITORY

Key:  A – Moist, Asterisk (*) indicates a warm-humid location.

| COUNTY | CLIMATE ZONE | COUNTY | CLIMATE ZONE | COUNTY | CLIMATE ZONE |
| --- | --- | --- | --- | --- | --- |
| Alachua | 2A* | Hardee | 2A* | Okeechobee | 2A* |
| Baker | 2A* | Hendry | 2A* | Orange | 2A* |
| Bay | 2A* | Hernando | 2A* | Osceola | 2A* |
| Bradford | 2A* | Highlands | 2A* | Palm Beach | 2A* |
| Brevard | 2A* | Hillsborough | 2A* | Pasco | 2A* |
| Broward | 1A* | Holmes | 2A* | Pinellas | 2A* |
| Calhoun | 2A* | Indian River | 2A* | Polk | 2A* |
| Charlotte | 2A* | Jackson | 2A* | Putnam | 2A* |
| Citrus | 2A* | Jefferson | 2A* | Santa Rosa | 2A* |
| Clay | 2A* | Lafayette | 2A* | Sarasota | 2A* |
| Collier | 2A* | Lake | 2A* | Seminole | 2A* |
| Columbia | 2A* | Lee | 2A* | St. Johns | 2A* |
| DeSoto | 2A* | Leon | 2A* | St. Lucie | 2A* |
| Dixie | 2A* | Levy | 2A* | Sumter | 2A* |
| Duval | 2A* | Liberty | 2A* | Suwannee | 2A* |
| Escambia | 2A* | Madison | 2A* | Taylor | 2A* |
| Flagler | 2A* | Manatee | 2A* | Union | 2A* |
| Franklin | 2A* | Marion | 2A* | Volusia | 2A* |
| Gadsden | 2A* | Martin | 2A* | Wakulla | 2A* |
| Gilchrist | 2A* | Miami-Dade | 1A* | Walton | 2A* |
| Glades | 2A* | Monroe | 1A* | Washington | 2A* |
| Gulf | 2A* | Nassau | 2A* |  |  |
| Hamilton | 2A* | Okaloosa | 2A* |  |  |

[Mod 4650]]

301.3 International climate zones. Reserved. The climate zone for any location outside the United States shall be determined by applying Table 301.3(1) and then Table 301.3(2).

TABLE 301.3(1)

INTERNATIONAL CLIMATE ZONE DEFINITIONS

Reserved

MAJOR CLIMATE TYPE DEFINITIONS

Warm-humid Definition—Moist (A) locations where either of the following wet-bulb temperature conditions shall occur during the warmest six consecutive months of the year: - 67oF (19.4oC) or higher for 3,000 or more hours; or - 73oF (22.8oC) or higher for 1,500 or more hours

Dry (B) Definition – Locations meeting the following criteria: Not marine and Pm< 0.44 x (TF – 19.5) [Pcm < 2.0 x (TC + 7) in SI units] Where: Pin = Annual precipitation in inches (cm) T = Annual mean temperature in oF (oC)

Moist (A) Definition – Locations that are not marine and not dry.

For SI: oC = [(oF) – 32]/1.8; 1 inch = 2.54 cm.

TABLE  301.3(2)

INTERNATIONAL CLIMATE ZONE DEFINITIONS

Reserved

| ZONE NUMBER | THERMAL CRITERIA |  |
| --- | --- | --- |
|  | IP Units | SI Units |
| 1 | 9000 < CDD50oF | 5000 < CDD 10 oC. |
| 2 | 6300 < CDD 50oF ≤ 9000 | 3500 < CDD 10 oC ≤ 5000 |

For SI: oC = [(oF) – 32]/1.8

SECTION 302

DESIGN CONDITIONS

302.1 Interior design conditions. The interior design temperatures used for heating and cooling load calculations shall be a maximum of 72ºF (22ºC) for heating and minimum of 75ºF (24ºC) for cooling.

SECTION 303

MATERIALS, SYSTEMS AND EQUIPMENT

303.1 Identification. Materials, systems and equipment shall be identified in a manner that will allow a determination of compliance with the applicable provisions of this code.

303.1.1 Building thermal envelope insulation. An R-value identification mark shall be applied by the manufacturer to each piece of building thermal envelope insulation 12 inches (305 mm) or greater in width. Alternately, the insulation installers shall provide a certification listing the type, manufacturer and R-value of insulation installed in each element of the building thermal envelope. For blown or sprayed insulation (fiberglass and cellulose), the initial installed thickness, settled thickness, settled R-value, installed density, coverage area and number of bags installed shall be listed on the certification. For sprayed polyurethane foam (SPF) insulation, the installed thickness of the areas covered and R-value of installed thickness shall be listed on the certification. The insulation installer shall sign, date and post the certification in a conspicuous location on the job site.

303.1.1.1 Blown or sprayed roof/ceiling insulation. The thickness of blown-in or sprayed roof/ceiling insulation (fiberglass or cellulose) shall be written in inches (mm) on markers that are installed at least one for every 300 square feet (28 m2) throughout the attic space. The markers shall be affixed to the trusses or joists and marked with the minimum initial installed thickness with numbers a minimum of 1 inch (25 mm) in height. Each marker shall face the attic access opening. Spray polyurethane foam thickness and installed R-value shall be listed on certification provided by the insulation installer

303.1.2 Insulation mark installation. Insulating materials shall be installed such that the manufacturer’s R-value mark is readily observable upon inspection.

303.1.3 Fenestration product rating. U-factors of fenestration products (windows, doors and skylights) shall be determined in accordance with NFRC 100 by an accredited, independent laboratory, and labeled and certified by the manufacturer. Products lacking such a labeled U-factor shall be assigned a default U-factor from Table 303.1.3(1) or 303.1.3(2). The solar heat gain coefficient (SHGC) of glazed fenestration products (windows, glazed doors and skylights) shall be determined in accordance with NFRC 200 by an accredited, independent laboratory, and labeled and certified by the manufacturer. Products lacking such a labeled SHGC shall be assigned a default SHGC from Table 303.1.3(3).

TABLE 303.1.3(1)

DEFAULT GLAZED FENESTRATION U-FACTOR

| Frame Type | Single Pane | Double pane | Skylight |  |
| --- | --- | --- | --- | --- |
|  |  |  | Single | Double |
| Metal | 1.20 | 0.80 | 2.00 | 1.30 |
| Metal with thermal break | 1.10 | 0.65 | 1.90 | 1.10 |
| Nonmetal or metal clad | 0.95 | 0.55 | 1.75 | 1.05 |
| Glazed block | 0.60 |  |  |  |

TABLE 303.1.3(2)

DEFAULT DOOR U-FACTORS

| Door Type | U-Factor |
| --- | --- |
| Uninsulated metal | 1.20 |
| Insulated metal | 0.60 |
| Wood | 0.50 |
| Insulated, nonmetal edge, max. 45% glazing, any glazing double pane | 0.35 |

TABLE 303.1.3(3)

DEFAULT GLAZED FENESTRATION SHGC

| Single Glazed |  | Double Glazed |  | Glazed Block |
| --- | --- | --- | --- | --- |
| Clear | Tinted | Clear | Tinted |  |
| 0.8 | 0.7 | 0.7 | 0.6 | 0.6 |

303.1.4 Insulation product rating. The thermal resistance (R-value) of insulation shall be determined in accordance with the U.S. Federal Trade Commission R-value rule (CFR Title 16, Part 460, May 31, 2005) in units of h ft2 °F/Btu at a mean temperature of 75°F (24°C).

303.2 Insulation iInstallation. Insulation materials shall comply with the requirements of their respective ASTM standard specification and shall be installed in accordance with their respective ASTM installation practice in Table 303.2 in such a manner as to achieve rated R-value of insulation. Open-blown or poured loose-fill insulation shall not be used in attic roof spaces when the slope of the ceiling is more than three in twelve. When eave vents are installed, baffling of the vent openings shall be provided to deflect the incoming air above the surface of the insulation. All materials, systems and equipment shall be installed in accordance with the manufacturer’s installation instructions and the International Building Code.

Exception: Where metal building roof and metal building wall insulation is compressed between the roof or wall skin and the structure.

303.2.1 Compressed insulation. Insulation that has been compressed to 85-percent or less of the manufacturer’s rated thickness for the product shall use the R-values given in Table 303.2.1. These values are to be used except where data developed by an independent testing laboratory is provided.

303.2.2  Substantial Contact. Insulation shall be installed in a permanent manner in substantial contact with the inside surface in accordance with manufacturer’s recommendations for the framing system used. Flexible batt insulation installed in floor cavities shall be supported in a permanent manner by supports no greater than 24 inches (610 mm) on center (o.c.).

Exception: Insulation materials that rely on airspaces adjacent to reflective surfaces for their rated performance.

TABLE 303.2

INSULATION INSTALLATION STANDARDS

| Insulation Material |  | Standard Specification |  | Installation Practice |  |
| --- | --- | --- | --- | --- | --- |
| Mineral Fiber Batt/Blanket |  | ASTM C 665 |  | ASTM C 1320 |  |
| Mineral Fiber Loose Fill |  | ASTM C 764 |  | ASTM C 1015 |  |
| Cellulose Loose Fill |  | ASTM C 739 |  | ASTM C 1015 |  |
| Polystyrene Foam |  | ASTM C 578 |  |  |  |
| Polyisocyanurate Foam |  | ASTM C 1289 |  |  |  |
| Reflective |  | ASTM C 1224 |  | ASTM C 727 |  |
| Radiant Barrier |  | ASTM C 1313 |  | ASTM C 1158 |  |
| Vermiculite |  | ASTM C 516 |  |  |  |
| Perlite |  | ASTM C 549 |  |  |  |
| Spray-Applied Rigid Cellular Polyurethane Foam |  | ASTM C 1029 |  |  |  |
| Interior Radiation Control Coating Systems |  |  |  | ASTM C 1321 |  |

TABLE 303.2.1

R-VALUES OF COMPRESSED INSULATION

| % of Original Thickness | R-5 | R-7 | R-11 | R-14 | R-19 | R-30 | R-38 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 90 | 5 | 6 | 10 | 13 | 18 | 28 | 36 |
| 80 | 4 | 6 | 10 | 12 | 17 | 26 | 33 |
| 70 | 4 | 5 | 9 | 11 | 15 | 24 | 30 |
| 60 | 3 | 5 | 8 | 10 | 14 | 22 | 27 |
| 50 | 3 | 4 | 7 | 9 | 12 | 18 | 24 |
| 40 | 2 | 4 | 6 | 8 | 10 | 15 | 20 |
| 30 | 2 | 3 | 4 | 6 | 8 | 12 | 16 |
| 20 | 20 | 2 | 2 | 3 | 4 | 10 | 10 |

303.2.3 Recessed Equipment. Lighting fixtures; heating, ventilating, and air-conditioning equipment, including wall heaters, ducts, and plenums; and other equipment shall not be recessed in such a manner as to affect the insulation thickness unless:

1. The total combined area affected (including necessary clearances) is less than one percent of the opaque area of the assembly, or

2. The entire roof, wall, or floor is covered with insulation to the full depth required, or

3. The effects of reduced insulation are included in calculations using an area-weighted average method and compressed insulation values obtained from Table 303.2.1.1.

In all cases, air leakage through or around the recessed equipment to the conditioned space shall be limited in accordance with Section 404.2.5 or 502.3.8, as applicable.

303.2.4 Insulation Protection. Exterior insulation shall be covered with a protective material to prevent damage from sunlight, moisture, landscaping operations, equipment maintenance, and wind. In attics and mechanical rooms, a way to access equipment that prevents damaging or compressing the insulation shall be provided. Foundation vents shall not interfere with the insulation. Insulation materials in ground contact shall have a water absorption rate no greater than .3 percent when tested in accordance with ASTM C272,

303.2.1 Protection of exposed foundation insulation. Insulation applied to the exterior of basement walls, crawlspace walls and the perimeter of slab-on-grade floors shall have a rigid, opaque and weather-resistant protective covering to prevent the degradation of the insulation’s thermal performance. The protective covering shall cover the exposed exterior insulation and shall extend a minimum of 6 inches (153 mm) below grade.

(4433)

303.3 Maintenance information. Maintenance instructions shall be furnished for equipment and systems that require preventive maintenance. Required regular maintenance actions shall be clearly stated and incorporated on a readily accessible label. The label shall include the title or publication number for the operation and maintenance manual for that particular model and type of product.

303.3.1 Commercial buildings.  The code official shall ensure that the construction documents require an operating and maintenance manual be transmitted to the building owner for all commercial buildings. The manual shall include basic data relating to the design, operation and maintenance of HVAC and lighting systems and equipment. Required routine maintenance actions shall be clearly identified. Where applicable, control information such as diagrams, schematics, control sequence descriptions, and maintenance and calibration information shall be included.

SECTION 304

MATERIALS TESTING AND THERMAL PROPERTIES

304.1 Building material thermal properties, general.

304.1.1 Commerical and residential high rise.  R-values for building materials used to demonstrate code compliance with Chapter 5shall be taken from ASHRAE 90.1 Normative Appendix A, from the EnergyGauge Summit Fla/Com computer program, from manufacturer’s product literature or from other nationally recognized engineering sources. Assembly U-factor calculations shall follow the procedure(s) detailed in section 304.3 or be tested in accordance with procedures(s) described in section 304.2.

Concrete block R-values shall be calculated using the isothermal planes method or a two-dimensional calculation program, thermal conductivities from ASHRAE 90.1 Normative Appendix A, from the EnergyGauge Summit Fla/Com program and dimensions from ASTM C90. The parallel path calculation method is not acceptable.

Exception: R-values for building materials or thermal conductivities determined from testing in accordance with Section 304.2.

[MOD 4651]

304.1.2 Residential one- and two-family. R-values referenced in Chapter 4 of this code refer to the R-values of the added insulation only. The R-values of structural building materials such as framing members, concrete blocks or gypsum board shall not be included. Insulation levels shall be achieved with insulation products tested and rated according to the procedures recognized by the Federal Trade Commission (FTC) in 16 CFR Part 460.

304.1.2.1 When installing two layers of bulk or board insulation, the R-values of each material may be added together for a total R-value. When installing two separate reflective insulation products in layers, the total R-value of the system shall have been achieved by testing under FTC regulations, 16 CFR Part 460.

304.2 Testing of Building Materials Thermal Properties.

304.2.1 Single materials. If building material R-values or thermal conductivities are determined by testing, one of the following test procedures shall be used:

a. ASTM C177

b. ASTM C236

c. ASTM C518

For concrete, the oven-dried conductivity shall be multiplied by 1.2 to reflect the moisture content as typically installed.

304.2.2 Assembly U-factors. If assembly U-factors are determined by testing, ASTM C1363 shall be used.

Product samples tested shall be production line material or representative of material as purchased by the consumer or contractor. If the assembly is too large to be tested at one time in its entirety, then either a representative portion shall be tested or different portions shall be tested separately and a weighted average determined. To be representative, the portion tested shall include edges of panels, joints with other panels, typical framing percentages, and thermal bridges.

304.3 Calculation procedures and assumptions. The following procedures and assumptions shall be used for all Chapter 5 code calculations. R-values for air films, insulation, and building materials shall be taken from Sections 304.3.1 or 304.3.2, respectively.  In addition, the appropriate assumptions listed, including framing factors, shall be used.

304.3.1 Air Films: Prescribed R-values for air films shall be as follows:

R-Value             Condition

0.17                    All exterior surfaces

0.46                    All semi-exterior surfaces

0.61                    Interior horizontal surfaces, heat flow up

0.92                    Interior horizontal surfaces, heat flow down

0.68                    Interior vertical surfaces

304.3.1.1 Exterior surfaces are areas exposed to the wind.

304.3.1.2 Semi-exterior surfaces are protected surfaces that face attics, crawl spaces, and parking garages with natural or mechanical ventilation.

304.3.1.3 Interior surfaces are surfaces within enclosed spaces.

304.3.1.4 The R-value for cavity airspaces included in the EnergyGauge Summit Fla/Com program are shall be taken from ASHRAE 90.1 Normative Appendix A. No credit shall be given for airspaces in cavities that contain any insulation or less than 0.5 inch (12.7 mm). The values for 3.5 inch (84 mm) cavities shall be used for cavities of that width and greater. [MOD 4652, MOD 4767]

304.3.2 Assembly U-Factor, C-Factor and F-Factor Calculation

304.3.2.1 Pre-calculated assembly U-factors, C-factors, F-factors, or heat capacities. The U-factors, C-factors, F-factors, and heat capacities for typical construction assemblies included in the EnergyGauge Summit Fla/Com computer program are taken from ASHRAE 90.1 Normative Appendix A. These values shall be used for all calculations unless otherwise allowed by applicant-determined assembly U-factors, C-factors, F-factors, or heat capacities. Interpolation between values for rated R-values of insulation, including insulated sheathing is allowed; extrapolation beyond values in the ASHRAE 90.1 Normative Appendix A tables is not. [MOD 4768]

304.3.2.2 Applicant-determined assembly U-factors, C-factors, F-factors, or heat capacities. If the building official determines that the proposed construction assembly is not adequately represented in the appropriate table of ASHRAE 90.1 Normative Appendix A, the applicant shall determine appropriate values for the assembly using the assumptions in ASHRAE 90.1 Normative Appendix A. An assembly is deemed to be adequately represented if:

a. the interior structure, hereafter referred to as the base assembly, for the class of construction is the same as described in Normative Appendix A and

b. changes in exterior or interior surface building materials added to the base assembly do not increase or decrease the R-value by more than 2 from that indicated in the descriptions in ASHRAE 90.1 Normative Appendix A.

Insulation, including insulated sheathing, is not considered a building material.

(4438)