Florida Supplement to the 2009 IBC

Note:  throughout the document, change International Building Code to Florida Building Code, Building; change the ICC Electrical Code to Chapter 27 of the Florida Building Code, Building; change the International Energy Conservation Code to Chapter 13 of the Florida Building Code, Building; change the International Existing Building Code to Florida Building Code, Existing Building; change the International Fire code to Florida Fire Prevention Code; change International Fuel Gas Code to Florida Building Code, Fuel Gas; change the International Mechanical Code to Florida Building Code, Mechanical; change the International Plumbing Code to Florida Building Code, Plumbing; change the International Residential Code to Florida Building Code, Residential.

Chapter 1, Scope and  Administration

Section 101 General

101.1 Title.  Change to read as shown:

101.1 Title.  These regulations shall be known as the Florida Building Code, hereinafter referred to as “this code.”

101.2 Scope, Exceptions.  Change to read as shown.

Exceptions:

1.	Detached one- and two-family dwellings and multiple single-family dwellings (town houses) not more than three stories above grade plane in height with a separate means of egress and their accessory structures shall comply with the Florida Building Code, Residential.

2.	Existing buildings undergoing repair, alterations or additions and change of occupancy shall comply with Chapter 34 of this code.

101.4 Referenced codes.  Change to read as shown.

101.4 Referenced codes.  The other codes listed in Sections 101.4.1 through 101.4.8 and referenced elsewhere in this code shall be considered part of the requirements of this code to the prescribed extent of each such reference.

101.4.1 Gas.  Change to read as shown.

101.4.1 Gas.  The provisions of the Florida Building Code, Fuel Gas shall apply to the installation of gas piping from the point of delivery, gas appliances and related accessories as covered in this code. These requirements apply to gas piping systems extending from the point of delivery to the inlet connections of appliances and the installation and operation of residential and commercial gas appliances and related accessories.

101.4.2Mechanical.  Change to read as shown.

101.4.2 Mechanical.  The provisions of the Florida Building Code, Mechanical shall apply to the installation, alterations, repairs and replacement of mechanical systems, including equipment, appliances, fixtures, fittings and/or appurtenances, including ventilating, heating, cooling, air-conditioning and refrigeration systems, incinerators and other energy-related systems.

101.4.3 Plumbing.  Change to read as shown.

101.4.3 Plumbing.  The provisions of the Florida Building Code, Plumbing shall apply to the installation, alteration, repair and replacement of plumbing systems, including equipment, appliances, fixtures, fittings and appurtenances, and where connected to a water or sewage system and all aspects of a medical gas system.

101.4.4 Property maintenance.  Change to read as shown.

101.4.4Property maintenance. Reserved.

101.4.5 Fire prevention.  Change to read as shown.

101.4.5 Fire prevention.  For provisions related to fire prevention, refer to the Florida Fire Prevention Code. The Florida Fire Prevention Code shall apply to matters affecting or relating to structures, processes and premises from the hazard of fire and explosion arising from the storage, handling or use of structures, materials or devices; from conditions hazardous to life, property or public welfare in the occupancy of structures or premises; and from the construction, extension, repair, alteration or removal of fire suppression and alarm systems or fire hazards in the structure or on the premises from occupancy or operation.

101.4.6 Energy.  Change to read as shown.

101.4.6 Energy.  The provisions of the Florida Building Code, Energy Conservation, shall apply to all matters governing the design and construction of buildings for energy efficiency.

101.4.7 Accessibility Change to read as shown.

101.4.7 Accessibility. For provisions related to accessibility, refer to Chapter 11 of the Florida Building Code, Building. the Florida Building Code, Accessibility .

[CA4598]

101.4.8 Manufactured buildings.  Add to read as shown.

101.4.8 Manufactured buildings.  For additional administrative and special code requirements, see section 428, Florida Building Code, Building, and Rule 9B-1 F.A.C.

102.1.1  Add to read as shown.

102.1.1  The Florida Building Code does not apply to, and no code enforcement action shall be brought with respect to, zoning requirements, land use requirements and owner specifications or programmatic requirements which do not pertain to and govern the design, construction, erection, alteration, modification, repair or demolition of public or private buildings, structures or facilities or to programmatic requirements that do not pertain to enforcement of the Florida Building Code.  Additionally, a local code enforcement agency may not administer or enforce the Florida Building Code, Building to prevent the siting of any publicly owned facility, including, but not limited to, correctional facilities, juvenile justice facilities, or state universities, community colleges, or public education facilities, as provided by law.

102.2 Building.  Change to read as shown.

102.2 Building.  The provisions of the Florida Building Code shall apply to the construction, erection, alteration, modification, repair, equipment, use and occupancy, location, maintenance, removal and demolition of every public and private building, structure or facility or floating residential structure, or any appurtenances connected or attached to such buildings, structures or facilities. Additions, alterations, repairs and changes of use or occupancy group in all buildings and structures shall comply with the provisions provided in Chapter 34 of this code.  The following buildings, structures and facilities are exempt from the Florida Building Code as provided by law, and any further exemptions shall be as determined by the legislature and provided by law:

(a)	Building and structures specifically regulated and preempted by the federal government.

(b)	Railroads and ancillary facilities associated with the railroad.

(c)	Nonresidential farm buildings on farms.

(d)	Temporary buildings or sheds used exclusively for construction purposes.

(e)	Mobile or modular structures used as temporary offices, except that the provisions of Part II (Section 553.501-553.513, Florida Statutes) relating to accessibility by persons with disabilities shall apply to such mobile or modular structures.

(f)	Those structures or facilities of electric utilities, as defined in Section 366.02, Florida Statutes, which are directly involved in the generation, transmission, or distribution of electricity.

(g)	Temporary sets, assemblies, or structures used in commercial motion picture or television production, or any sound-recording equipment used in such production, on or off the premises.

(h)	Chickees constructed by the Miccosukee Tribe of Indians of Florida or the Seminole Tribe of Florida. As used in this paragraph, the term “chickee” means an open-sided wooden hut that has a thatched roof of palm or palmetto or other traditional materials, and that does not incorporate any electrical, plumbing, or other nonwood features.

Revise Section 102.2 to add a new item (i) as follows:

(i) Family mausoleums not exceeding 250 square feet in area which are prefabricated and assembled on site or preassembled and delivered on site and have walls, roofs, and a floor constructed of granite, marble, or reinforced concrete. (3871A1)

Revise Section 102.2 to add (j) as a new item as follows:

(j) Temporary housing provided by the Department of Corrections to any prisoner in the state correctional system. (3871A2)

102.2.1 Add to read as shown.

102.2.1 In addition to the requirements of Section 553.79 and 553.80, Florida Statutes, facilities subject to the provisions of Chapter 395, Florida Statutes, and Part II of Chapter 400, Florida Statutes, shall have facility plans reviewed and construction surveyed by the state agency authorized to do so under the requirements of Chapter 395, Florida Statutes, and Part II of Chapter 400, Florida Statutes, and the certification requirements of the federal government.

102.2.2 Add to read as shown.

102.2.2 Residential buildings or structures moved into or within a county or municipality shall not be required to be brought into compliance with the state minimum building code in force at the time the building or structure is moved, provided:

1.	The building or structure is structurally sound and in occupiable condition for its intended use;

2.	The occupancy use classification for the building or structure is not changed as a result of the move;

3.	The building is not substantially remodeled;

4.	Current fire code requirements for ingress and egress are met;

5.	Electrical, gas and plumbing systems meet the codes in force at the time of construction and are operational and safe for reconnection; and

6.	Foundation plans are sealed by a professional engineer or architect licensed to practice in this state, if required by the Florida Building Code, Building for all residential buildings or structures of the same occupancy class.

102.2.3 Add to read as shown.

102.2.3 The building official shall apply the same standard to a moved residential building or structure as that applied to the remodeling of any comparable residential building or structure to determine whether the moved structure is substantially remodeled.

The cost of the foundation on which the moved building or structure is placed shall not be included in the cost of remodeling for purposes of determining whether a moved building or structure has been substantially remodeled.

102.2.4 Add to read as shown.

102.2.4 This section does not apply to the jurisdiction and authority of the Department of Agriculture and Consumer Services to inspect amusement rides or the Department of Financial Services to inspect state-owned buildings and boilers.

102.2.5 add to read as shown.

102.2.5 Each enforcement district shall be governed by a board, the composition of which shall be determined by the affected localities.

1. At its own option, each enforcement district or

local enforcement agency may adopt promulgate rules granting to

the owner of a single-family residence one or more exemptions

from the Florida Building Code relating to:

a.(a) Addition, alteration, or repairs performed by the

property owner upon his or her own property, provided any

addition or alteration shall not exceed 1,000 square feet or the

square footage of the primary structure, whichever is less.

b.(b) Addition, alteration, or repairs by a nonowner

within a specific cost limitation set by rule, provided the

total cost shall not exceed $5,000 within any 12-month period.

c.(c) Building and inspection fees.

2. However, the exemptions under subparagraph 1. do not

apply to single-family residences that are located in mapped

flood hazard areas, as defined in the code, unless the

enforcement district or local enforcement agency has determined

that the work, which is otherwise exempt, does not constitute a

substantial improvement, including the repair of substantial

damage, of such single-family residences.

3. Each code exemption, as defined in sub-subparagraphs

1a, 1b., and 1c. paragraphs (a), (b), and (c), shall be certified

to the local board 10 days prior to implementation and shall

only be effective in the territorial jurisdiction of the

enforcement district or local enforcement agency implementing

it.

[CA4824]

102.2.6 Add to read as shown.

102.2.6 This section does not apply to swings and other playground equipment accessory to a one- or two-family dwelling.

Exception: Electrical service to such playground equipment shall be in accordance with Chapter 27 of this code.

102.5 Partial invalidity.  Change to read as shown.

102.5 Partial invalidity. Reserved.

102.6 Existing structures.  Change to read as shown.

102.6 Existing structures.  The legal occupancy of any structure existing on the date of adoption of this code shall be permitted to continue without change, except as is specifically covered in this code, or the Florida Fire Prevention Code, or as is deemed necessary by the building official for the general safety and welfare of the occupants and the public.

102.7 Relocation of manufactured buildings.  Add to read as shown.

102.7 Relocation of manufactured buildings.

(1)	Relocation of an existing manufactured building does not constitute an alteration.

(2)	A relocated building shall comply with wind speed requirements of the new location, using the appropriate wind speed map.  If the existing building was manufactured in compliance with the Standard Building Code (prior to March 1, 2002), the wind speed map of the Standard Building Code shall be applicable. If the existing building was manufactured in compliance with the Florida Building Code (after March 1, 2002), the wind speed map of the Florida Building Code shall be applicable.

(3) A relocated building shall comply with the flood hazard area requirements of the new location, if applicable.{3894}

Add Section 102.8 as a new section to read as follows:

102.8  Existing mechanical equipment. An agency or local government may not require that existing mechanical equipment on the surface of a roof be installed in compliance with the requirements of the Florida Building Code until the equipment is required to be removed or replaced. (3871A3)

Section 103 Department of Building Safety.  Change to read as shown.

Section 103 Department of Building Safety Reserved.

Section 104 Duties and Powers of the Building Official

104.1 General.  Change to read as shown.

104.1 General. Reserved.

104.2 Applications and permits.  Change to read as shown.

104.2 Applications and permits.  Reserved.

104.3 Notices and orders.  Change to read as shown.

104.3 Notices and orders.  Reserved.

104.4 Inspections.  Change to read as shown.

104.4 Inspections.  Reserved.

104.5 Identification.  Change to read as shown.

104.5 Identification.  Reserved.

104.6 Right of entry.  Change to read as shown.

104.6 Right of entry.  Reserved.

104.7 Department records.  Change to read as shown.

104.7 Department records. Reserved.

104.8 Liability.  Change to read as shown.

104.8 Liability.  Reserved.

104.10 Modifications.  Change to read as shown.

104.10 Modifications.  Reserved.

104.11 Alternative materials, design and methods of construction and equipment.  Change to read as shown.

104.11 Alternative materials, design and methods of construction and equipment.

The provisions of this code are not intended to prevent the installation of any material or to prohibit any design or method of construction not specifically prescribed by this code, provided that any such alternative has been approved. An alternative material, design or method of construction shall be approved where the building official finds that the proposed design is satisfactory and complies with the intent of the provisions of this code, and that the material, method or work offered is, for the purpose intended, at least the equivalent of that prescribed in this code in quality, strength, effectiveness, fire resistance, durability and safety. When alternate life safety systems are designed, the SFPE Engineering Guide to Performance-Based Fire Protection Analysis and Design of Buildings, or other methods approved by the building official may be used. The building official shall require that sufficient evidence or proof be submitted to substantiate any claim made regarding the alternative.

104.11.3 Accessibility.  Add to read as shown.

104.11.3 Accessibility.  Alternative designs and technologies for providing access to and usability of a facility for persons with disabilities shall be in accordance with Section 11.2.2.  provisions of the Florida Building Code, Accessibility.

[CA4599]

Section 105 Permits

Section 105.1 Required.  Change to read as shown.

105.1 Required.   Any owner or authorized agent who intends to construct, enlarge, alter, repair, move, demolish, or change the occupancy of a building or structure, or to erect, install, enlarge, alter, repair, remove, convert or replace any required impact resistant coverings, electrical, gas, mechanical or plumbing system, the installation of which is regulated by this code, or to cause any such work to be done, shall first make application to the building official and obtain the required permit. {4351}

105.1.1 Annual permit.  Change to read as shown.

105.1.1 Annual facility permit. In lieu of an individual permit for each alteration to an existing electrical, gas, mechanical, plumbing or interior nonstructural office system(s), the building official is authorized to issue an annual permit for any occupancy to facilitate routine or emergency service, repair, refurbishing, minor renovations of service systems or manufacturing equipment installations/relocations. The building official shall be notified of major changes and shall retain the right to make inspections at the facility site as deemed necessary. An annual facility permit shall be assessed with an annual fee and shall be valid for one year from date of issuance. A separate permit shall be obtained for each facility and for each construction trade, as applicable. The permit application shall contain a general description of the parameters of work intended to be performed during the year.

105.1.3 Food permit.  Add to read as shown.

105.1.3 Food permit.  As per Section 500.12, Florida Statutes, a food permit from the Department of Agriculture and Consumer Services is required of any person who operates a food establishment or retail store.

105.2 Work exempt from permit.  Change to read as shown.

105.2 Work exempt from permit.  Exemptions from permit requirements of this code shall not be deemed to grant authorization for any work to be done in any manner in violation of the provisions of this code. Permits shall not be required for the following:

Gas:

1.	Portable heating appliance.

2.	Replacement of any minor part that does not alter approval of equipment or make such equipment unsafe.

Mechanical:

1.	Portable heating appliance.

2.	Portable ventilation equipment.

3.	Portable cooling unit.

4.	Steam, hot or chilled water piping within any heating or cooling equipment regulated by this code.

5.	Replacement of any part which does not alter its approval or make it unsafe.

6.	Portable evaporative cooler.

7.	Self-contained refrigeration system containing 10 pounds (4.54 kg) or less of refrigerant and actuated by motors of 1 horsepower (746 W) or less.

8.	The installation, replacement, removal or metering of any load management control device.

Plumbing:

1.	The stopping of leaks in drains, water, soil, waste or vent pipe provided, however, that if any concealed trap, drain pipe, water, soil, waste or vent pipe becomes defective and it becomes necessary to remove and replace the same with new material, such work shall be considered as new work and a permit shall be obtained and inspection made as provided in this code.

2.	The clearing of stoppages or the repairing of leaks in pipes, valves or fixtures, and the removal and reinstallation of water closets, provided such repairs do not involve or require the replacement or rearrangement of valves, pipes or fixtures.

105.2.2 Repairs.  Change to read as shown.

105.2.2 Minor repairs.  Ordinary minor repairs may be made with the approval of the building official without a permit, provided  the repairs do not include the cutting away of any wall, partition or portion thereof, the removal or cutting of any structural beam or load-bearing support, or the removal or change of any required means of egress, or rearrangement of parts of a structure affecting the egress requirements; additionally, ordinary minor repairs shall not include addition to, alteration of, replacement or relocation of any standpipe, water supply, sewer, drainage, drain leader, gas, soil, waste, vent or similar piping, electric wiring systems or mechanical equipment or other work affecting public health or general safety, and such repairs shall not violate any of the provisions of the technical codes.

105.2.3 Public service agencies.  Change to read as shown.

105.2.3 Public service agencies.  Reserved.

105.3 Application for permit.  Change to read as shown.

105.3 Application for permit.  To obtain a permit, the applicant shall first file an application therefor in writing on a form furnished by the building department for that purpose. Permit application forms shall be in the format prescribed by a local administrative board, if applicable, and must comply with the requirements of Section 713.135(5) and (6), Florida Statutes.

Each application shall be inscribed with the date of application, and the code in effect as of that date.  For a building permit for which an application is submitted prior to the effective date of the Florida Building Code, the state minimum building code in effect in the permitting jurisdiction on the date of the application governs the permitted work for the life of the permit and any extension granted to the permit.

105.3.1 Action on application.  Change to read as shown.

105.3.1 Action on application.  The building official shall examine or cause to be examined applications for permits and amendments thereto within a reasonable time after filing. If the application or the construction documents do not conform to the requirements of pertinent laws, the building official shall reject such application in writing, stating the reasons therefor. If the building official is satisfied that the proposed work conforms to the requirements of this code and laws and ordinances applicable thereto, the building official shall issue a permit therefor as soon as practicable. When authorized through contractual agreement with a school board, in acting on applications for permits, the building official shall give first priority to any applications for the construction of, or addition or renovation to, any school or educational facility.

105.3.1.1 Add text to read as shown.

105.3.1.1  If a state university, state community Florida college or public school district elects to use a local government’s code enforcement offices, fees charged by counties and municipalities for enforcement of the Florida Building Code on buildings, structures, and facilities of state universities, state colleges, and public school districts shall not be more than the actual labor and administrative costs incurred for plans review and inspections to ensure compliance with the code. [3641]

105.3.1.2  Add text to read as shown.

105.3.1.2  No permit may be issued for any building construction, erection, alteration, modification, repair, or addition unless the applicant for such permit provides to the enforcing agency which issues the permit any of the following documents which apply to the construction for which the permit is to be issued and which shall be prepared by or under the direction of an engineer registered under Chapter 471, Florida Statutes:

1.	Plumbing documents for any new building or addition which requires a plumbing system with more than 250 fixture units or which costs more than $125,000.

2.	Fire sprinkler documents for any new building or addition which includes a fire sprinkler system which contains 50 or more sprinkler heads. A Contractor I, Contractor II, or Contractor IV, certified under Section 633.521 Florida Statutes, may design a fire sprinkler system of 49 or fewer heads and may design the alteration of an existing fire sprinkler system if the alteration consists of the relocation, addition or deletion of not more than 49 heads, notwithstanding the size of the existing fire sprinkler system.

3.	Heating, ventilation, and air-conditioning documents for any new building or addition which requires more than a 15-ton-per-system capacity which is designed to accommodate 100 or more persons or for which the system costs more than $125,000. This paragraph does not include any document for the replacement or repair of an existing system in which the work does not require altering a structural part of the building or for work on a residential one, two, three or four-family structure.

An air-conditioning system may be designed by an installing air-conditioning contractor certified under Chapter 489, Florida Statutes, to serve any building or addition which is designed to accommodate fewer than 100 persons and requires an air-conditioning system with a value of $125,000 or less; and when a 15-ton-per system or less is designed for a singular space of a building and each 15-ton system or less has an independent duct system. Systems not complying with the above require design documents that are to be sealed by a professional engineer.

Example 1: When a space has two 10-ton systems with each having an independent duct system, the contractor may design these two systems since each unit (system) is less than 15 tons.

Example 2: Consider a small single-story office building which consists of six individual offices where each office has a single three-ton package air conditioning heat pump. The six heat pumps are connected to a single water cooling tower. The cost of the entire heating, ventilation and air-conditioning work is $47,000 and the office building accommodates fewer than 100 persons. Because the six mechanical units are connected to a common water tower this is considered to be an 18-ton system. It therefore could not be designed by a mechanical or air conditioning contractor.

NOTE: It was further clarified by the Commission that the limiting criteria of 100 persons and $125,000 apply to the building occupancy load and the cost for the total air-conditioning system of the building.

4.	Any specialized mechanical, electrical, or plumbing document for any new building or addition which includes a medical gas, oxygen, steam, vacuum, toxic air filtration, halon, or fire detection and alarm  system which costs more than $5,000.

5.  Electrical documents.  See Florida Statutes 471.003(2)(h).

Documents requiring an engineer seal by this part shall not be valid unless a professional engineer who possesses a valid certificate of registration has signed, dated, and stamped such document as provided in Section 471.025, Florida Statutes.

105.3.3  Add text to read as shown.

105.3.3 An enforcing authority may not issue a building permit for any building construction, erection, alteration,  modification, repair or addition unless the permit either includes on its face or there is attached to the permit the following statement: “NOTICE: In addition to the requirements of this permit, there may be additional restrictions applicable to this property that may be found in the public records of this county, and there may be additional permits required from other governmental entities such as water management districts, state agencies, or federal agencies.”

105.3.4 Add text to read as shown.

105.3.4 A building permit for a single-family residential dwelling must be issued within 30 working days of application therefor unless unusual circumstances require a longer time for processing the application or unless the permit application fails to satisfy the Florida Building Code or the enforcing agency’s laws or ordinances.

105.3.5 Identification of minimum premium policy.  Add text to read as shown.

105.3.5 Identification of minimum premium policy. Except as otherwise provided in Chapter 440, Florida Statutes, Workers’ Compensation, every employer shall, as a condition to receiving a building permit, show proof that it has secured  compensation for its employees as provided in Section 440.10 and 440.38, Florida Statutes.

105.3.6 Asbestos removal.  Add text to read as shown.

105.3.6 Asbestos removal.  Moving, removal or disposal of asbestos-containing materials on a residential building where the owner occupies the building, the building is not for sale or lease, and the work is performed according to the owner-builder limitations provided in this paragraph. To qualify for exemption under this paragraph, an owner must personally appear and sign the building permit application. The permitting agency shall provide the person with a disclosure statement in substantially the following form:

Disclosure Statement: State law requires asbestos abatement to be done by licensed contractors. You have applied for a permit under an exemption to that law. The exemption allows you, as the owner of your property, to act as your own asbestos abatement contractor even though you do not have a license. You must supervise the construction yourself. You may move, remove or dispose of asbestos-containing materials on a residential building where you occupy the building and the building is not for sale or lease, or the building is a farm outbuilding on your property.  If you sell or lease such building within 1 year after the asbestos abatement is complete, the law will presume that you intended to sell or lease the property at the time the work was done, which is a violation of this exemption.  You may not hire an unlicensed person as your contractor.  Your work must be done according to all local, state and federal laws and regulations which apply to asbestos abatement projects.  It is your responsibility to make sure that people employed by you have licenses required by state law and by county or municipal licensing ordinances.

105.3.7 Applicable Code for Manufactured Buildings. Manufacturers should be permitted to complete all buildings designed and approved prior to the effective date of a new code edition, provided a clear signed contract is in place. The contract shall provide specific data mirroring that required by an application for permit, specifically, without limitation, date of execution, building owner or dealer, and anticipated date of completion. However, the construction activity must commence within 6 months of the contract's execution. The contract is subject to verification by the Department of Community Affairs. {3672}

105.4 Validity of permit.  Change to read as shown.

105.4 Conditions of the permit.

105.4.1 Permit intent.  Add text to read as shown.

105.4.1 Permit intent.  A permit issued shall be construed to be a license to proceed with the work and not as authority to violate, cancel, alter or set aside any of the provisions of the technical codes, nor shall issuance of a permit prevent the building official from thereafter requiring a correction of errors in plans, construction or violations of this code.  Every permit issued shall become invalid unless the work authorized by such permit is commenced within six months after its issuance, or if the work authorized by such permit is suspended or abandoned for a period of six months after the time the work is commenced.

105.4.1.1  Add text to read as shown.

105.4.1.1  If work has commenced and the permit is revoked, becomes null and void, or expires because of lack of progress or abandonment, a new permit covering the proposed construction shall be obtained before proceeding with the work.

105.4.1.2  Add text to read as shown.

105.4.1.2  If a new permit is not obtained within 180 days from the date the initial permit became null and void, the building official is authorized to require that any work which has been commenced or completed be removed from the building site.  Alternately, a new permit may be issued on application, providing the work in place and required to complete the structure meets all applicable regulations in effect at the time the initial permit became null and void and any regulations which may have become effective between the date of expiration and the date of issuance of the new permit.

105.4.1.3  Add text to read as shown.

105.4.1.3  Work shall be considered to be in active progress when the permit has received an approved inspection within 180 days. This provision shall not be applicable in case of civil commotion or strike or when the building work is halted due directly to judicial injunction, order or similar process.

105.4.1.4  Add text to read as shown.

105.4.1.4  The fee for renewal reissuance and extension of a permit shall be set forth by the administrative authority.

105.5 Expiration.  Change to read as shown.

105.5 Expiration.  Reserved.

105.6 Suspension or revocation.  Change to read as shown.

105.6 Suspension or revocation.  Reserved.

105.8 Notice of commencement.  Add text to read as shown.

105.8 Notice of commencement.  As per Section 713.135, Florida Statutes, when any person applies for a building permit, the authority issuing such permit shall print on the face of each permit card in no less than 14-point, capitalized, boldfaced type:  “WARNING TO OWNER: YOUR FAILURE TO RECORD A NOTICE OF COMMENCEMENT MAY RESULT IN YOUR PAYING TWICE FOR IMPROVEMENTS TO YOUR PROPERTY. IF YOU INTEND TO OBTAIN FINANCING, CONSULT WITH YOUR LENDER OR AN ATTORNEY BEFORE RECORDING YOUR NOTICE OF COMMENCEMENT.”

105.9  Asbestos.  Add text to read as shown.

105.9 Asbestos.  The enforcing agency shall require each building permit for the demolition or renovation of an existing structure to contain an asbestos notification statement which indicates the owner’s or operator’s responsibility to comply with the provisions of Section 469.003, Florida Statutes, and to notify the Department of Environmental Protection of his or her intentions to remove asbestos, when applicable, in accordance with state and federal law.

105.10 Certificate of protective treatment for prevention of termites.  Add text to read as shown.

105.10 Certificate of protective treatment for prevention of termites.   A weather-resistant job-site posting board shall be provided to receive duplicate treatment certificates as each required protective treatment is completed, providing a copy for the person the permit is issued to and another copy for the building permit files. The treatment certificate shall provide the product used, identity of the applicator, time and date of the treatment, site location, area treated, chemical used, percent concentration and number of gallons used, to establish a verifiable record of protective treatment. If the soil chemical barrier method for termite prevention is used, final exterior treatment shall be completed prior to final building approval.

105.11 Notice of termite protection.  Add text to read as shown.

105.11 Notice of termite protection.  A permanent sign which identifies the termite treatment provider and need for reinspection and treatment contract renewal shall be provided. The sign shall be posted near the water heater or electric panel.

105.12 Work starting before permit issuance.  Add text to read as shown.

105.12 Work starting before permit issuance.  Upon approval of the building official, the scope of work delineated in the building permit application and plan may be started prior to the final approval and issuance of the permit, provided any work completed is entirely at risk of the permit applicant and the work does not proceed past the first required inspection.

105.13 Phased permit approval.  Add text to read as shown.

105.13 Phased permit approval.  After submittal of the appropriate construction documents, the building official is authorized to issue a permit for the construction of foundations or any other part of a building or structure before the construction documents for the whole building or structure have been submitted. The holder of such permit for the foundation or other parts of a building or structure shall proceed at the holder’s own risk with the building operation and without assurance that a permit for the entire structure will be granted. Corrections may be required to meet the requirements of the technical codes.

105.14 Permit issued on basis of an affidavit.  Add text to read as shown.

105.14 Permit issued on basis of an affidavit.  Whenever a permit is issued in reliance upon an affidavit or whenever the work to be covered by a permit involves installation under conditions which, in the opinion of the building official, are hazardous or complex, the building official shall require that the architect or engineer who signed the affidavit or prepared the drawings or computations shall supervise such work. In addition, they shall be responsible for conformity to the permit, provide copies of inspection reports as inspections are performed, and upon completion make and file with the building official written affidavit that the work has been done in conformity to the reviewed plans and with the structural provisions of the technical codes. In the event such architect or engineer is not available, the owner shall employ in his stead a competent person or agency whose qualifications are reviewed by the building official. The building official shall ensure that any person conducting plans review is qualified as a plans examiner under Part XII of Chapter 468, Florida Statutes, and that any person conducting inspections is qualified as a building inspector under Part III of Chapter 468, Florida Statutes.

Section 105.15, add text to read as follows:

105.15  Opening protection.  When any activity requiring a building permit that is applied for on or after July 1, 2008, and for which the estimated cost is $50,000 or more for a building site built single – family detached residential structures that is located in the wind borne debris region as defined in the Florida Building in this Code and that has an insured value of $750,000 or more, or, if the building site built single – family detached residential structures is uninsured or for which documentation of insured value is not presented, has a just valuation for the structure for purposes of ad valorem taxation of $750,000 or more. ; oOpening protections as required within the Florida Building Code, Building this Code or Florida Building Code, Residential for new construction shall be provided.

Exception: Single family residential structures permitted subject to the Florida Building Code are not required to comply with this section.

Section 107  Submittal Documents

Revise 107.1 General to read as follows:

107.1 General.   Construction documents, special inspection and structural observation programs, and other data shall be submitted in one or more sets with each application for a permit. The construction documents shall be prepared by a design registered design professional where required by the Chapter 471, Florida Statutes or Chapter 481, Florida  Sstatutes. Where special conditions exist, the building official is authorized to require additional construction documents to be prepared by a registered design professional.

Exception: The building official is authorized to waive the submission of construction documents and other data not required to be prepared by a registered design professional if it is found that the nature of the work applied for is such that review of construction documents is not necessary to obtain compliance with this code.

107.2.1 Information on construction documents.  Change to read as shown.

107.2.1 Information on construction documents.  Construction documents shall be dimensioned and drawn upon suitable material. Electronic media documents are permitted to be submitted when approved by the building official. Construction documents shall be of sufficient clarity to indicate the location, nature and extent of the work proposed and show in detail that it will conform to the provisions of this code and relevant laws, ordinances, rules and regulations, as determined by the building official (see also Section 107.3.5).

107.2.1.1 Fire protection system shop drawings. Shop drawings for the fire protection system(s) shall be submitted to indicate conformance to this code and the construction documents

and shall be approved prior to the start of system installation. Shop drawings shall contain all information as required by the referenced installation standards in Chapter 9.

107.2.1.2 Add text to read as shown.

107.2.1.2 For roof assemblies required by the code, the construction documents shall illustrate, describe, and delineate the type of roofing system, materials, fastening requirements, flashing requirements and wind resistance rating that are required to be installed.  Product evaluation and installation shall indicate compliance with the wind criteria required for the specific site or a statement by an architect or engineer for the specific site must be submitted with the construction documents.

107.2.3 Means of egress.  Change to read as shown.

107.2.3  Means of egress.  Reserved.

107.2.4 Exterior wall envelope.  Change to read as shown.

107.2.4  Exterior wall envelope. Reserved.

107.2.5 Site plan.  Change to read as shown.

107.2.5  Site plan.  Reserved.

107.3 Examination of documents.  Change to read as shown.

107.3 Examination of documents.  The building official shall examine or cause to be examined the accompanying submittal documents and shall ascertain by such examinations whether the construction indicated and described is in accordance with the requirements of this code and other pertinent laws or ordinances.

Exceptions:

1.	Building plans approved pursuant to Section 553.77(5), Florida Statutes, and state-approved manufactured buildings are exempt from local codes enforcing agency plan reviews except for provisions of the code relating to erection, assembly or construction at the site. Erection, assembly and construction at the site are subject to local permitting and inspections.  Photocopies of plans approved according to FAC 9B-1.009, F.A.C., shall be sufficient for local permit application documents of record for the modular building portion of the permitted project. {3920}

2.	Industrial construction on sites where design, construction and fire safety are supervised by appropriate design and inspection professionals and which contain adequate in-house fire departments and rescue squads is exempt, subject to local government option, from review of plans and inspections, providing owners certify that applicable codes and standards have been met and supply appropriate approved drawings to local building and fire-safety inspectors.

107.3.3. Phased approval.  Change to read as shown.

107.3.3 Phased approval.  Reserved

107.3.4 Design professional in responsible charge.  Change to read as shown.

107.3.4 Design professional in responsible charge.  Reserved.

107.3.4.1 General.  Change to read as shown.

107.3.4.1 General.  Reserved

107.3.4.2 Deferred submittals.  Change to read as shown.

107.3.4.2 Deferred submittals.  Reserved

107.3.4.3 Add text to read as shown.

107.3.4.3  Certifications by contractors authorized under the provisions of Section 489.115(4)(b), Florida Statutes, shall be considered equivalent to sealed plans and specifications by a person licensed under Chapter 471, Florida Statutes, or Chapter 481 Florida Statutes, by local enforcement agencies for plans review for permitting purposes relating to compliance with the wind-resistance provisions of the code or alternate methodologies approved by the Florida Building Commission for one- and two-family dwellings. Local enforcement agencies may rely upon such certification by contractors that the plans and specifications submitted conform to the requirements of the code for wind resistance. Upon good cause shown, local government code enforcement agencies may accept or reject plans sealed by persons licensed under Chapters 471, 481 or 489, Florida Statutes.

107.3.5 Minimum plan review criteria for buildings.  Add text to read as shown.

107.3.5 Minimum plan review criteria for buildings. The examination of the documents by the building official shall include the following minimum criteria and documents: a floor plan; site plan; foundation plan; floor/roof framing plan or truss layout; all fenestration penetrations; flashing; and rough opening dimensions; and all exterior elevations: (3577, 3615)

Commercial Buildings:

Building

1.	Site requirements:

Parking

Fire access

Vehicle loading

Driving/turning radius

Fire hydrant/water supply/post indicator valve (PIV)

Set back/separation (assumed property lines)

Location of specific tanks, water lines and sewer lines

Flood hazard areas, flood zones, and design flood elevations {3894}

2.	Occupancy group and special occupancy requirements shall be determined.

3.	Minimum type of construction shall be determined (see Table 503).

4.	Fire-resistant construction requirements shall include the following components:

Fire-resistant separations

Fire-resistant protection for type of construction

Protection of openings and penetrations of rated walls

Fire blocking and draftstopping and calculated fire resistance

5.	Fire suppression systems shall include:

Early warning smoke evacuation systems Schematic fire sprinklers

Standpipes

Preengineered systems

Riser diagram

Same as above.

6.	Life safety systems shall be determined and shall include the following requirements:

Occupant load and egress capacities

Early warning

Smoke control

Stair pressurization

Systems schematic

7.	Occupancy load/egress requirements shall include:

Occupancy load

Gross

Net

Means of egress

Exit access

Exit

Exit discharge

Stairs construction/geometry and protection

Doors

Emergency lighting and exit signs

Specific occupancy requirements

Construction requirements

Horizontal exits/exit passageways

8.	Structural requirements shall include:

Soil conditions/analysis

Termite protection

Design loads

Wind requirements

Building envelope

Impact resistant coverings or systems {4352}

Structural calculations (if required)

Foundation

Flood requirements in accordance with Section 1612, including lowest floor elevations, enclosures, flood damage-resistant materials {3894}

Wall systems

Floor systems

Roof systems

Threshold inspection plan

Stair systems

9.	Materials shall be reviewed and shall at a minimum include the following:

Wood

Steel

Aluminum

Concrete

Plastic

Glass

Masonry

Gypsum board and plaster

Insulating (mechanical)

Roofing

Insulation

10.	Accessibility requirements shall include the following:

Site requirements

Accessible route

Vertical accessibility

Toilet and bathing facilities

Drinking fountains

Equipment

Special occupancy requirements

Fair housing requirements

11.	Interior requirements shall include the following:

Interior finishes (flame spread/smoke development)

Light and ventilation

Sanitation

12.	Special systems:

Elevators

Escalators

Lifts

13.	Swimming pools:

Barrier requirements

Spas

Wading pools

Electrical

1.	Electrical:

Wiring

Services

Feeders and branch circuits

Overcurrent protection

Grounding

Wiring methods and materials

GFCIs

2.	Equipment

3.	Special occupancies

4.	Emergency systems

5.	Communication systems

6.	Low voltage

7.   Load calculations

8. Design flood elevation {3894}

Plumbing

1.	Minimum plumbing facilities

2.	Fixture requirements

3.	Water supply piping

4.	Sanitary drainage

5.	Water heaters

6.	Vents

7.	Roof drainage

8.	Back flow prevention

9.	Irrigation

10.	Location of water supply line

11.	Grease traps

12.	Environmental requirements

13. Plumbing riser

14. Design flood elevation {3894}

Mechanical

1.	Energy calculations

2.	Exhaust systems:

Clothes dryer exhaust

Kitchen equipment exhaust

Specialty exhaust systems

3.	Equipment

4.	Equipment location

5.	Make-up air

6.	Roof-mounted equipment

7.	Duct systems

8.	Ventilation

9.	Combustion air

10.	Chimneys, fireplaces and vents

11.	Appliances

12.	Boilers

13.	Refrigeration

14.	Bathroom ventilation

15. Laboratory

16. Design flood elevation {3894}

Gas

1.	Gas piping

2.	Venting

3.	Combustion air

4.	Chimneys and vents

5.	Appliances

6.	Type of gas

7.	Fireplaces

8.	LP tank location

9.   Riser diagram/shutoffs

10. Design flood elevation{3894}

Demolition

1.   Asbestos removal

Residential (one- and two-family)

1.	Site requirements

Set back/separation (assumed property lines)

Location of septic tanks

2.	Fire-resistant construction (if required)

3.	Fire

4.	Smoke detector locations

5.	Egress

Egress window size and location stairs construction requirements

6.	Structural requirements shall include:

Wall section from foundation through roof, including assembly and materials connector tables wind requirements structural calculations (if required)

Flood hazard areas, flood zones, design flood elevations, lowest floor elevations, enclosures, equipment, and flood damage-resistant materials {3894}

7.   Accessibility requirements: show/identify accessible bath

8. impact resistant coverings or systems{4352}

Exemptions.

Plans examination by the building official shall not be required for the following work:

1.	Replacing existing equipment such as mechanical units, water heaters, etc.

2.	Reroofs

3.	Minor electrical, plumbing and mechanical repairs

4.	Annual maintenance permits

5.	Prototype plans

Except for local site adaptions, siding, foundations and/or modifications.

Except for structures that require waiver.

6.    Manufactured buildings plan except for foundations and modifications of buildings on site.

107.5 Retention of construction documents.  Change text to read as shown.

107.5 Retention of construction documents.  One set of approved construction documents shall be retained by the building official for a period of not less than 180 days from date of completion of the permitted work, or as required by Florida Statutes.

107.6  Affidavits.  Add text to read as shown.

107.6  Affidavits.  The building official may accept a sworn affidavit from a registered architect or engineer stating that the plans submitted conform to the technical codes. For buildings and structures, the affidavit shall state that the plans conform to the laws as to egress, type of construction and general arrangement and, if accompanied by drawings, show the structural design and that the plans and design conform to the requirements of the technical codes as to strength, stresses, strains, loads and stability. The building official may without any examination or inspection accept such affidavit, provided the architect or engineer who made such affidavit agrees to submit to the building official copies of inspection reports as inspections are performed and upon completion of the structure, electrical, gas, mechanical or plumbing systems a certification that the structure, electrical, gas, mechanical or plumbing system has been erected in accordance with the requirements of the technical codes. Where the building official relies upon such affidavit, the architect or engineer shall assume full responsibility for compliance with all provisions of the technical codes and other pertinent laws or ordinances. The building official shall ensure that any person conducting plans review is qualified as a plans examiner under Part XII of Chapter 468, Florida Statutes, and that any person conducting inspections is qualified as a building inspector under Part XII of Chapter 468, Florida Statutes.

108.3 Temporary power.  Change text to read as shown.

108.3 Temporary power.  The building official is authorized to give permission to temporarily supply and use power in part of an electric installation before such installation has been fully completed and the final certificate of completion has been issued. The part covered by the temporary certificate shall comply with the requirements specified for temporary lighting, heat or power in Chapter 27 of the Florida Building Code, Building.

109.1 Prescribed fees.  Change text to read as shown.

109.1 Prescribed fees.  A permit shall not be issued until fees authorized under Section 553.80, Florida Statutes, have been paid. Nor shall an amendment to a permit be released until the additional fee, if any, due to an increase in the estimated cost of the building, structure, electrical, plumbing, mechanical, or gas systems, has been paid.

109.3 Building permit valuations.  Change text to read as shown.

109.3 Building permit valuations.  Reserved.

109.4 Work commencing before permit issuance.   Change text to read as shown.

109.4 Work commencing before permit issuance.  Any person who commences any work on a building, structure, electrical, gas, mechanical or plumbing system before obtaining the building official’s approval or the necessary permits shall be subject to a penalty of 100 percent of the usual permit fee in addition to the required permit fees.

109.5 Related fees.  Change text to read as shown.

109.5 Related fees.  Reserved.

109.6 Refunds.   Change text to read as shown.

109.6 Refunds.  Reserved.

110.3 Required inspections.  Change text to read as shown.

110.3 Required inspections.  The building official upon notification from the permit holder or his or her agent shall make the following inspections, and shall either release that portion of the construction or shall notify the permit holder or his or her agent of any violations which must be corrected in order to comply with the technical codes. The building official shall determine the timing and sequencing of when inspections occur and what elements are inspected at each inspection.

Building

1.	Foundation inspection. To be made after trenches are excavated and forms erected and shall at a minimum include the following building components:

·Stem-wall

·Monolithic slab-on-grade

·Piling/pile caps

·Footers/grade beams

1.1. In flood hazard areas, upon placement of the lowest floor, including basement, and prior to further vertical construction, the elevation certification shall be submitted to the authority having jurisdiction. {3894}

2.	Framing inspection. To be made after the roof, all framing, fireblocking and bracing is in place, all concealing wiring, all pipes, chimneys, ducts and vents are complete and shall at a minimum include the following building components:

·Window/door framing

·Vertical cells/columns

·Lintel/tie beams

·Framing/trusses/bracing/connectors

·Draft stopping/fire blocking

·Curtain wall framing

·Energy insulation

·Accessibility.

·Verify rough opening dimensions are within tolerances.

3.	Sheathing inspection. To be made either as part of a dry-in inspection or done separately at the request of the contractor after all roof and wall sheathing and fasteners are complete and shall at a minimum include the following building components:

·Roof sheathing

·Wall sheathing

·Sheathing fasteners

·Roof/wall dry-in.

4.	Roofing inspection. Shall at a minimum include the following building components:

·Dry-in

·Insulation

·Roof coverings

·Flashing

5.	Final inspection. To be made after the building is completed and ready for occupancy.

5.1. In flood hazard areas, as part of the final inspection, a final certification of the lowest floor elevation shall be submitted to the authority having jurisdiction.{3894}

6.	Swimming pool inspection. First inspection to be made after excavation and installation of reinforcing steel, bonding and main drain and prior to placing of concrete.

Final inspection to be made when the swimming pool is complete and all required enclosure requirements are in place.

In order to pass final inspection and receive a certificate of completion, a residential swimming pool must meet the requirements relating to pool safety features as described in Section 424.2.17.

7.	Demolition inspections. First inspection to be made after all utility connections have been disconnected and secured in such manner that no unsafe or unsanitary conditions shall exist during or after demolition operations.

Final inspection to be made after all demolition work is completed.

8.   Manufactured building inspections. The building department shall inspect construction of foundations; connecting buildings to foundations; installation of parts identified on plans as site installed items, joining the modules, including utility crossovers; utility connections from the building to utility lines on site; and any other work done on site which requires compliance with the Florida Building Code. Additional inspections may be required for public educational facilities (see Section 423.27.20).

9. Where impact resistant coverings or impact resistant systems are installed to meet requirements of this code, the building official shall schedule adequate inspections of impact resistant coverings or impact resistant systems to determine the following: {4353}

The system indicated on the plans was installed.

The system is installed in accordance with the manufacturer’s installation instructions and the product approval.

Electrical

1.	Underground inspection. To be made after trenches or ditches are excavated, conduit or cable installed, and before any backfill is put in place.

2.	Rough-in inspection. To be made after the roof, framing, fireblocking and bracing is in place and prior to the installation of wall or ceiling membranes.

3.	Final inspection. To be made after the building is complete, all required electrical fixtures are in place and properly connected or protected, and the structure is ready for occupancy.

Plumbing

1.	Underground inspection. To be made after trenches or ditches are excavated, piping installed, and before any backfill is put in place.

2.	Rough-in inspection. To be made after the roof, framing, fireblocking and bracing is in place and all soil, waste and vent piping is complete, and prior to this installation of wall or ceiling membranes.

3.	Final inspection. To be made after the building is complete, all plumbing fixtures are in place and properly connected, and the structure is ready for occupancy.

Note: See Section P312 of the Florida Building Code, Plumbing for required tests.

Mechanical

1.	Underground inspection. To be made after trenches or ditches are excavated, underground duct and fuel piping installed, and before any backfill is put in place.

2.	Rough-in inspection. To be made after the roof, framing, fire blocking and bracing are in place and all ducting, and other concealed components are complete, and prior to the installation of wall or ceiling membranes.

3.	Final inspection. To be made after the building is complete, the mechanical system is in place and properly connected, and the structure is ready for occupancy.

Gas

1.	Rough piping inspection. To be made after all new piping authorized by the permit has been installed, and before any such piping has been covered or concealed or any fixtures or gas appliances have been connected.

2.	Final piping inspection. To be made after all piping authorized by the permit has been installed and after all portions which are to be concealed by plastering or otherwise have been so concealed, and before any fixtures or gas appliances have been connected. This inspection shall include a pressure test.

3.	Final inspection. To be made on all new gas work authorized by the permit and such portions of existing systems as may be affected by new work or any changes, to ensure compliance with all the requirements of this code and to assure that the installation and construction of the gas system is in accordance with reviewed plans.

110.3.1 Footing and foundation inspection.  Change text to read as shown.

110.3.1 Footing and foundation inspection.  Reserved.

110.3.2 Concrete slab and under-floor inspection.  Change text to read as shown.

110.3.2 Concrete slab and under-floor inspection.  Reserved.

110.3.3  Reinforcing steel and structural frames

110.3.3 Reinforcing steel and structural frames.  Reinforcing steel or structural frame work of any part of any building or structure shall not be covered or concealed without first obtaining a release from the building official.

110.3.4 Frame inspection.  Change to read as follows.

110.3.4 Termites.  Building components and building surroundings required to be protected from termite damage in accordance with Section 1503.6, Section 2304.13 or Section 2304.11.6, specifically required to be inspected for termites in accordance with Section 2114, or required to have chemical soil treatment in accordance with Section 1816 shall not be covered or concealed until the release from the building official has been received.

110.3.5 Shoring.  Change to read as follows:

110.3.5 Shoring.  For threshold buildings, shoring and associated formwork or falsework shall be designed and inspected by a Florida licensed professional engineer, employed by the permit holder or subcontractor, prior to any required mandatory inspections by the threshold building inspector.

110.3.7 Energy efficiency inspections.  Revise to read as follows:

110.3.7 Threshold building.

110.3.7.1 The enforcing agency shall require a special inspector to perform structural inspections on a threshold building pursuant to a structural inspection plan prepared by the engineer or architect of record. The structural inspection plan must be submitted to the enforcing agency prior to the issuance of a building permit for the construction of a threshold building. The purpose of the structural inspection plans is to provide specific inspection procedures and schedules so that the building can be adequately inspected for compliance with the permitted documents. The special inspector may not serve as a surrogate in carrying out the responsibilities of the building official, the architect, or the engineer of record. The contractor's contractual or statutory obligations are not relieved by any action of the special inspector.

110.3.7.2 The special inspector shall determine that a professional engineer who specializes in shoring design has inspected the shoring and reshoring for conformance with the shoring and reshoring plans submitted to the enforcing agency. A fee simple title owner of a building, which does not meet the minimum size, height, occupancy, occupancy classification, or number-of-stories criteria which would result in classification as a threshold building under s. 553.71(7), may designate such building as a threshold building, subject to more than the minimum number of inspections required by the Florida Building Code.

110.3.7.3 The fee owner of a threshold building shall select and pay all costs of employing a special inspector, but the special inspector shall be responsible to the enforcement agency.  The inspector shall be a person certified, licensed or registered under Chapter 471, Florida Statutes, as an engineer or under Chapter 481, Florida Statutes, as an architect.

110.3.7.4 Each enforcement agency shall require that, on every threshold building:

110.3.7.4.1 The special inspector, upon completion of the building and prior to the issuance of a certificate of occupancy, file a signed and sealed statement with the enforcement agency in substantially the following form: “To the best of my knowledge and belief, the above described construction of all structural load-bearing components complies with the permitted documents, and the shoring and reshoring conforms to the shoring and reshoring plans submitted to the enforcement agency.”

110.3.7.4.2 Any proposal to install an alternate structural product or system to which building codes apply be submitted to the enforcement agency for review for compliance with the codes and made part of the enforcement agency’s recorded set of permit documents.

110.3.7.4.3 All shoring and reshoring procedures, plans and details be submitted to the enforcement agency for recordkeeping. Each shoring and reshoring installation shall be supervised, inspected and certified to be in compliance with the shoring documents by the contractor.

110.3.7.4.4 All plans for the building which are required to be signed and sealed by the architect or engineer of record contain a statement that, to the best of the architect’s or engineer’s knowledge, the plans and specifications comply with the applicable minimum building codes and the applicable fire-safety standards as determined by the local authority in accordance with this section and Chapter 633, Florida Statutes.

110.3.7.5 No enforcing agency may issue a building permit for construction of any threshold building except to a licensed general contractor, as defined in Section 489.105(3)(a), Florida Statutes, or to a licensed building contractor, as defined in Section 489.105(3)(b), Florida Statutes, within the scope of her or his license. The named contractor to whom the building permit is issued shall have the responsibility for supervision, direction, management and control of the construction activities on the project for which the building permit was issued.

110.3.7.6 The building department may allow a special inspector to conduct the minimum structural inspection of threshold buildings required by this code, Section 553.73, Florida Statutes, without duplicative inspection by the building department.  The building official is responsible for ensuring that any person conducting inspections is qualified as a building inspector under Part XII of Chapter 468, Florida Statutes, or certified as a special inspector under Chapter 471 or 481, Florida Statutes. Inspections of threshold buildings required by Section 553.79(5), Florida Statutes, are in addition to the minimum inspections required by this code.

110.3.8  Other inspections.  Change to read as shown.

110.3.8  Reinforcing steel and structural frames

110.3.9  Special inspections.  Change to read as shown.

110.3.9  Special inspections.  Reserved.

110.3.10  Final inspections.  Change to read as shown.

110.3.10  Final inspections.  Reserved.

109.4 Inspection agencies.   Change to read as shown.

109.4 Inspection agencies.  Reserved.

SECTION 111

CERTIFICATES OF OCCUPANCY AND COMPLETION

Revise 111.2 Certificate Issued, to read as follows:

111.2 Certificate issued. After the building official inspects the building or structure and finds no violations of the provisions of this code or other laws that are enforced by the department of building safety, the building official shall issue a certificate of occupancy that contains the following:

1. The building permit number.

2. The address of the structure.

3. The name and address of the owner.

4. A description of that portion of the structure for which the certificate is issued.

5. A statement that the described portion of the structure has been inspected for compliance with the requirements of this code for the occupancy and division of occupancy and the use for which the proposed occupancy is classified.

6. For buildings and structures in flood hazard areas, a statement that documentation of the as-built lowest floor elevation has been provided and is retained in the records of the department of building safety.

6 7. The name of the building official.

7 8. The edition of the code under which the permit was issued.

8 9. The use and occupancy, in accordance with the provisions of Chapter 3.

9 10. The type of construction as defined in Chapter 6.

10 11. The design occupant load.

11 12. If an automatic sprinkler system is provided, whether the sprinkler system is required.

13. Any special stipulation and conditions of the building permit.

{3894}

Section 111.4 Certificate of Completion.  Add to read as shown.

111.4 Certificate of Completion.  A Certificate of Completion is proof that a structure or system is complete and for certain types of permits is released for use and may be connected to a utility system. This certificate does not grant authority to occupy a building, such as shell building, prior to the issuance of a Certificate of Occupancy.

Section 110.5 Revocation.  Change to read as shown.

111.4 111.5 Revocation.  The building official is authorized to, in writing, suspend or revoke a certificate of occupancy or completion issued under the provisions of this code wherever the certificate is issued in error, or on the basis of incorrect information supplied, or where it is determined that the building or structure or portion thereof is in violation of any ordinance or regulation or any of the provisions of this code.

Section 113 Board of Appeals.  Change to read as shown.

Section 113 Board of Appeals.  Reserved.

Section 114 Violations.  Change to read as shown.

Section 114 Violations.  Reserved.

Section 116 Unsafe Structures And Equipment.  Change to read as shown.

Section 116 Unsafe Structures And Equipment.  Reserved.

Chapter 2 Definitions

Section 201 General

201.3 Terms defined in other codes. Change to read as shown.

201.3 Terms defined in other codes.  Reserved.

201.4 Terms not defined.  Change to read as shown.

201.4 Words not defined.  Words not defined herein shall have the meanings stated in the Florida Building Code, Plumbing, Mechanical and Fuel Gas, or the Florida Fire Prevention Code. Words not defined in the Florida Building Codes, shall have the meanings in Webster’s Third New International Dictionary of the English Language, Unabridged.

202 Definitions.  Change to read as shown

Change the following terms to read as shown.

ACCESSIBLE. See Section 11-3.5. theFlorida Building Code, Accessibility.

Change to read as shown.

ACCESSIBLE ROUTE.  See Section 11-3.5. theFlorida Building Code, Accessibility.

Change to read as shown.

Accessible Unit.  Reserved. See the Florida Building Code, Accessibility.

ADDITION. An extension or increase in floor area, number of stories or height of a building or structure.

{3854}

AGRICULTURAL, BUILDING. Reserved.

Add to read as shown.

APPLICABLE GOVERNING BODY. A city, county, state, state agency or other political government subdivision or entity authorized to administer and enforce the provisions of this code, as adopted or amended. Also applies to administrative authority.

Add to read as shown.

ARCHITECT. A Florida-registered architect.

AWNING. Any rigid or movable (retractable) roof-like structure, cantilevered, or otherwise entirely supported from a building. An awning is comprised of a lightweight rigid or removable skeleton structure over which an approved cover is attached.

Change to read as shown.

Brittle.  Reserved.

Add to read as shown.

BURIAL CHAMBER MAUSOLEUM. A family mausoleum consisting of 6 or fewer casket placement crypts plus a chamber to be used for loading of caskets from the interior of the mausoleum which is not below the level of the ground and which is substantially exposed above ground.

CANOPY. Any fixed roof-like structure, not movable like an awning, and which is cantilevered in whole or in part self-supporting, but having no side walls or curtains other than valances not more than 18 inches (457 mm) deep.  Lean-to canopies, fixed umbrellas and similar structures are included in this classification. Structures having side walls or valances more than 18 inches (457 mm) deep shall be classified as a tent as set forth herein.

Add to read as shown.

[F] CARBON DIOXIDE EXTINGUISHING SYSTEMS. See Section 902.1.

CARBON MONOXIDE ALARM. A device for the purpose of detecting carbon monoxide, that produces a distinct audible alarm, and is listed or labeled with the appropriate standard, either ANSI/UL 2034 - 96, Standard for Single and Multiple Station CO Alarms, or UL 2075 - 04, Gas and Vapor Detector Sensor, in accordance with its application.

Add to read as shown.

CHAPEL MAUSOLEUM. A mausoleum for the public that has heat or air conditioning, with or without a committal area or office.

Add to read as shown.

CIRCULAR STAIRS. See Section 1002.

Circulation Path.  See the Florida Building Code, Accessibility.

Add to read as shown.

COLUMBARIUM. A permanent structure consisting of niches.

Add to read as shown.

COMMISSION. The Florida Building Commission.

Add to read as shown.

COMPANION CRYPT. A permanent chamber in a mausoleum for the containment of human remains of more than one individual.

Add to read as shown.

Crane load.  The dead, live and impact loads and forces resulting from the operation of permanent cranes.

Add to read as shown.

CRYPT. A permanent chamber in a mausoleum for the containment of human remains.

Add to read as shown.

DAY-CARE HOME. A building or a portion of a building in which more than 3 but not more than 12 clients receive care, maintenance, and supervision, by other than their relative(s) or legal guardian(s), for less than 24 hr per day.

Add to read as shown.

DAY-CARE OCCUPANCY. A building or a portion of a building in which more than 12 clients receive care, maintenance, and supervision, by other than their relative(s) or legal guardian(s), for less than 24 hr per day.

Add to read as shown.

DECORATIVE CEMENTITIOUS COATING. A skim coat, as defined in ASTM C 926, of portland cement based plaster applied to concrete or masonry surfaces intended for cosmetic purposes.

Revise text to read as follows:

DESIGN DISPLACEMENT. Reserved See Section 1908.1.3.

DESIGN EARTHQUAKE GROUND MOTION.  Reserved.

Change to read as shown.

DETECTABLE WARNING. See the Florida Building Code, Accessibility.

Change to read as shown.

Dwelling unit or sleeping unit, multiple story.  Reserved.

Change to read as shown.

Dwelling unit or sleeping unit, type A.  Reserved.

Change to read as shown.

Dwelling unit or sleeping unit, type B.  Reserved.

Change to read as shown.

Edge distance.  Reserved.

Change to read as shown.

Effective embedment depth.  Reserved.

Add to read as shown.

EMPLOYEE WORK AREA. Reserved..See theFlorida Building Code, Accessibility.

Add to read as shown.

ENGINEER. A Florida-registered engineer.

Add to read as shown.

ENFORCEMENT AGENCY.

Add to read as shown.

Local enforcement agency. Means an agency of local government with authority to make inspections of buildings and to enforce the codes which establish standards for design, construction, erection, alteration, repair, modification or demolition of public or private buildings, structures or facilities.

Add to read as shown.

State enforcement agency. Means the agency of state government with authority to make inspections of buildings and to enforce the codes, as required by this part, which establish standards for design, construction, erection, alteration, repair, modification or demolition of public or private buildings, structures or facilities.

Add to read as shown.

FABRIC COVERED FRAMEWORK (FCF). A nonpressurized structure which is composed of a rigid framework to support tensioned membrane or fabric which provides the weather barrier.

Add to read as shown.

FACILITY. See the Florida Building Code, Accessibility.

Add to read as follows.

Family Day Care Homes means an occupied residence in which child care is regularly provided for at least 2 unrelated families which receive payment, fee, or grant for any of the children receiving care, whether or not operated for profit.  A Family Day Care Home shall be allowed to care one of the following groups of children, which shall include those children under 13 years of age who are related to the care giver: A.  A maximum of 4 childr4en from birth to 12 months of age.  B.  A maximum of 3 children to birth to 12 years of age and other children for maximum total of 6 children.  C.  A maximum of 6 preschool children if all are older than 12 months of age.  D.  A maximum of 10 children if no more than 5 are preschool age and, of those 5, no more than 2 are under 12 months of age.

Add to read as shown.

Family mausoleum.  A mausoleum for the private use of a family or group of family members.

Add to read as shown.

FLEXIBLE PLAN BUILDINGS. Buildings used for day-care homes which have movable corridor walls and movable partitions of full-height construction with doors leading from rooms to corridors.

Add to read as shown.

FLOATING RESIDENTIAL UNIT. Means a structure primarily designed or constructed as a living unit, built on a floating base, which is not designed primarily as a vessel, is not self-propelled although it may be towed about from place to place, and is primarily intended to be anchored or otherwise moored in a fixed location.

Add to read as shown

FLOODPLAIN MANAGEMENT ORDINANCE. See Section 1612.2. [3873]

Add text to read as follows:

FOSSIL FUEL. Coal, kerosene, oil, fuel gases, or other petroleum or hydrocarbon product that emits carbon monoxide as a by-product of combustion.

Add to read as shown.

FRAMEWORK. A skeletal or structural frame; an openwork frame structure.

Add to read as shown.

GARDEN MAUSOLEUM. A mausoleum for the public built without heat or air conditioning but may contain an open-air committal area.

Add to read as shown.

Group day care home.  A day care home in which at least seven but not more than 12 client receive care, maintenance, and supervision by other than their relative(s) or legal guardian(s) for less than 24 hours per day with no more than three clients incapable of self-reservation.

Change the following to read as shown.

HABITABLE SPACE.  A space in a structure for living, sleeping, eating or cooking.  Bathrooms, toilet compartments, closets, halls, screen enclosures, sunroom Categories I, II and III as defined in the AAMA/NPEA/NSA 2100, storage or utility space and similar areas are not considered habitable space.

Add to read as shown.

HEATING. See Chapter 28 of the Florida Building Code, Building and the Florida Building Code, Mechanical.

Add to read as shown.

HEIGHT, THRESHOLD BUILDING. The height of the building is at the mean distance between the eaves and the ridge of the roofing structure. If the distance from grade to the line which is the mean distance between the eaves and the ridge of the roofing structure is more than 50 feet, the building is to be considered a "threshold building" within the contemplation of the Threshold Building Act.

Add to read as shown.

HIGH VELOCITY HURRICANE ZONE. This zone consists of Broward and Dade counties.

Change to read as shown.

HISTORIC BUILDINGS. Buildings that are listed in or eligible for listing in the National Register of Historic Places, or designated as historic under an appropriate state or local law (see Chapter 10 of the Florida Existing Building Code).

HYDROGEN CUTOFF ROOM.  See Section 440.2.

Add to read as shown.

INSULATING CONCRETE FORM (ICF). A concrete forming system using stay-in-place forms of rigid foam plastic insulation, a hybrid of cement and foam insulation, a hybrid of cement and wood chips, or other insulating material for constructing cast-in-place concrete walls.

Change to read as shown.

Intended to be occupied as a residence.  Reserved.

Add to read as shown.

LANDSCAPE ARCHITECT. A Florida-registered landscape architect.

Add to read as shown.

MATERIAL CODE VIOLATION. A material code violation is a violation that exists within a completed building, structure or facility which may reasonably result, or has resulted, in physical harm to a person or significant damage to the performance of a building or its systems.

Add to read as shown.

MATERIAL VIOLATION. As defined in Florida Statutes.

Add to read as shown.

MAUSOLEUM. A permanent structure or building which is substantially exposed above the ground and is intended for the interment, entombment, or inurnment of human remains.

Change to read as shown.

MAXIMUM CONSIDERED EARTHQUAKE GROUND MOTION. Reserved.  See Section 1613.2.

Means of escape.  See section 1002.

MECHANICAL SYSTEMS. Reserved. See Section 1613.2.

Add to read as shown.

Niche.  A permanent chamber in a columbarium or mausoleum to hold the cremated remains of one or more individuals.

Add to read as shown.

NON-VISITATION CRYPT MAUSOLEUM. A mausoleum for the public where the crypts are not accessible to the public.

Add to read as shown.

OPEN PLAN BUILDINGS. Buildings used for day-care homes which have rooms and corridors delineated by tables, chairs, desks, bookcases, counters, low-height [maximum 5-ft (1.5-m)] partitions, or similar furnishings.

Add to read as shown.

Openings.  Apertures or holes in a building envelope and which are designed as “open” during design winds as defined by these provisions.

Revise text to read as follows:

ORDINARY PRECAST STRUCTURALWALL. Reserved

ORDINARY REINFORCED CONCRETE STRUCTURALWALL. Reserved

ORDINARY STRUCTURAL PLAIN CONCRETE WALL. Reserved

ORTHOGONAL. Reserved. See Section 1613.2.

Add to read as shown.

PLANS. All construction drawings and specifications for any structure necessary for the building official to review in order to determine whether a proposed structure, addition or renovation will meet the requirements of this code and other applicable codes.

Change to read as shown.

Public entrance.  Reserved.

Change to read as shown.

Public-use areas.  Reserved.

Add to read as shown.

Registered termiticide.  Product listed as registered for use as a preventative treatment for termites for new construction by the Florida Department of Agriculture and Consumer Services under authority of Chapter 487, Florida Statutes.

Add to read as shown.

RESIDENT SLEEPING UNIT. A single unit providing sleeping facilities for one or more persons. Resident sleeping units can also include permanent provisions for living, eating and sanitation, but do not include kitchen facilities.

Change to read as shown.

RESTRICTED ENTRANCE. Reserved.

Add to read as shown.

RETAINING WALL, SEGMENTAL. A retaining wall formed of modular block units stacked dry without mortar.

Change to read as shown.

Retractable awning.  Reserved.

Add to read as shown.

SCREEN ENCLOSURE. A building or part thereof, in whole or in part self-supporting, and having walls of insect screening with or without removable vinyl or acrylic wind break panels and a roof of insect screening, plastic, aluminum or similar lightweight material.

SEISMIC DESIGN CATEGORY. Reserved. See Section 1613.2.

SEISMIC-FORCE-RESISTING SYSTEM. Reserved. See Section 1613.2.

Change to read as shown.

Self-service storage facility.  Reserved.

Add to read as shown.

SELF-PRESERVATION. A client who is capable of self-preservation is one who can evacuate the building without direct intervention by a staff member.

Add to read as shown.

SEPARATE ATMOSPHERE. The atmosphere that exists between rooms, spaces, or areas that are separated by an approved smoke barrier.

Change to read as shown.

Service entrance.  Reserved.

Change definition of “shear wall” as shown:

SHEAR WALL. A wall designed to resist lateral forces parallel to the plane of the wall.

Change to read as shown.

Site.  Reserved.

Change to read as shown.

Site class. Reserved.

Change to read as shown.

Site coefficients.  Reserved.

Add to read as shown:

Smoke layer interface.  Reserved.

Change to read as shown.

Special inspection.  Reserved.

Change to read as shown.

Special continuous inspection.  Reserved.

Change to read as shown.

Special periodic inspection.  Reserved.

Change to read as shown.

SPECIAL STRUCTURAL WALL. Reserved.  See Section 1908.1.1.

[S4658]

SPIRAL STAIRS. A stairway with steps that have a central connecting point, and the travel path is a corkscrew or spiral.

Add to read as shown.

STREET. Any public thoroughfare, street, avenue, boulevard or space more than 20 ft (6096 mm) wide which has been  dedicated or deeded for vehicular use by the public and which can be used for access by fire department vehicles.

Change to read as shown.

Structural observation.  Reserved.

Change to read as shown.

SUNROOM ADDITION. Reserved.

Change to read as shown.

SWIMMING POOLS. See Section 424.2.1.

Change to read as shown.

Technically infeasible.  Reserved.

Add to read as shown.

TENANT. Any person, agent, firm, corporation or division, who uses or occupies land, a building or portion of a building by title, under a lease, by payment of rent or who exercises limited control over the space.

Add to read as shown.

THRESHOLD BUILDING. In accordance with Florida Statute, any building which is greater than 3 stories or 50 feet in height, or which has an assembly occupancy classification that exceeds 5,000 square feet in area and an occupant content of greater than 500 persons.

Revise text to read as follows:

TOWNHOUSE. A single-family dwelling unit constructed in a group of three or more attached units with property lines separating each unit in which each unit extends from foundation to roof and with open space on at least two sides.

Add to read as shown.

TUBULAR DAYLIGHTING DEVICE (TDD). A non-operable fenestration unit primarily designed to transmit daylight from a roof surface to an interior ceiling via a tubular conduit. The basic unit consists of an exterior glazed weathering surface, a light-transmitting tube with a reflective interior surface, and an interior-sealing device such as a translucent ceiling panel. The unit may be factory assembled, or field-assembled from a manufactured kit. (4332)

VALLEY. The internal angle formed by the intersection of two (2) sloping roof planes running from the ridge to the eave or terminating at an intermediate juncture, into which water is directed and channeled to provide water runoff. {3399}

VALUE. The estimated current replacement cost of the building in kind.

Add to read as shown.

WALKWAY, COVERED. A roofed, unobstructed walkway connecting buildings and used as a means of travel by persons and where less than 50 percent of the perimeter is enclosed and the maximum width perpendicular to the direction of travel is less than 30 ft (9144 mm).

Add to read as shown.

WALKWAY, ENCLOSED. A roofed, unobstructed walkway connecting buildings and used as a means of travel by persons and where 50 percent or more of the perimeter is enclosed and the maximum width perpendicular to the direction of travel is less than 30 ft (9144 mm).

Change to read as shown.

WALL PIER. Reserved. See Section 1908.1.3.

Wheelchair space.  Reserved. ..See theFlorida Building Code, Accessibility.

Change to read as shown.

Wheelchair space cluster.  Reserved.

Add to read as shown.

WIND-BORNE DEBRIS IMPACT RESISTANT PRODUCTS. Those products meeting TAS 201, TAS 202 and TAS 203, ASTM E 1886 or ASTM E 1996 or AAMA 506, SSTD 12, or ANSI/DASMA  115. Those products meeting TAS 201, TAS 202 and TAS 203, or ASTM E 1886 or and ASTM E 1996, or AAMA 506, or SSTD 12, or ANSI/DASMA 115.

Chapter 3, Use and Occupancy Classification

Section 302 Classification

Section 302.1 General, revise text to read as follows:

302.1 General. Structures or portions of structures shall be classified with respect to occupancy in one or more of the groups listed below. A room or space that is intended to be occupied at different times for different purposes shall comply with all of the requirements that are applicable to each of the purposes for which the room or space will be occupied. Structures with multiple occupancies or uses shall comply with Section 508. Where a structure is proposed for a purpose that is not specifically provided for in this code, such structure shall be classified in the group that the occupancy most nearly resembles, according to the fire safety and relative hazard involved.

1. Assembly (see Section 303): Groups A-1, A-2, A-3, A-4 and A-5

2. Business (see Section 304): Group B

3. Educational (see Section 305): Group E

4. Factory and Industrial (see Section 306): Groups F-1, F-2 and F-3.

5. High Hazard (see Section 307): Groups H-1, H-2, H-3, H-4 and H-5

6. Institutional (see Section 308): Groups I-1, I-2 and I-3

7. Mercantile (see Section 309): Group M

8. Residential (see Section 310): Groups R-1, R-2, R-3 as applicable in Section 101.2, and R-4

9. Storage (see Section 311): Groups S-1 and S-2

10. Utility and Miscellaneous (see Section 312): Group U

11. Day care (see Section 313): Group D

Section 303 Assembly Group A

303.1.1Change to read as shown.

303.1.1 Restaurants and drinking establishments with an occupant load of less than 50 persons shall be classified as Group M, mercantile.

Section 304 Business Group B

304.2 Add to read as shown.

304.2 Sections 423(1) and 423(2) are applicable to community Florida colleges. [3641]

304.2 Public and private colleges and universities shall comply with Section 443.

304.3Sections 423(1) and 423(2) are applicable to community Florida colleges shall comply with Section 423.

[SP4764, CA4765]

Section 305 Educational Group E

305.2 Day care. Change to read as shown.

305.2  Public education occupancies shall comply with Section 423.  Public and private educational occupancies shall comply with Section 443.

305.3 Public education occupancies shall comply with Section 423.

[SP4764, CA4765]

Section 306 Factory Group F

306.4 Special purpose F-3.  Add to read as shown.

306.4 Special purpose F-3.  Factory-industrial occupancy includes industrial operations in buildings designed for and suitable only for particular types of operations, characterized by a relatively low density of employee population, with much of the area occupied by machinery or equipment.  Group F-3 special purpose factory-industrial occupancy shall include, among others, the occupancies listed in this section: steel mills, paper plants and generating plants.

Section 307 High-Hazard Group H

[F] 307.1 High-hazard Group H.  [F] 307.1 High-hazard Group H. High-hazard Group H occupancy includes, among others, the use of a building or structure, or a portion thereof, that involves the manufacturing, processing, generation or storage of materials that constitute a

physical or health hazard in quantities in excess of those allowed in control areas complying with Section 414, based on the maximum allowable quantity limits for control areas set

forth in Tables 307.1(1) and 307.1(2). Hazardous occupancies are classified in Groups H-1, H-2, H-3, H-4 and H-5 and shall be in accordance with this section, the requirements of Section

415 and the Florida Fire Prevention Code. Hazardous materials stored, or used on top of roofs or canopies shall be classified as outdoor storage or use and shall comply with the Florida Fire Prevention Code.

Exceptions: The following shall not be classified in Group H, but shall be classified in the occupancy that they most nearly resemble:

1.	Buildings and structures occupied for the application of flammable finishes, provided that such buildings or areas conform to the requirements of Section 416 and the Florida Fire Prevention Code.

2.	Wholesale and retail sales and storage of flammable and combustible liquids in mercantile occupancies conforming to the Florida Fire Prevention Code.

3- 8 (no change).

9.	Stationary batteries utilized for facility emergency power, uninterrupted power supply or telecommunication facilities, provided that the batteries are provided with safety venting caps and ventilation is provided in accordance with the Florida Building Code, Mechanical.

10.	Corrosives shall not include personal or household products in their original packaging used in retail display or commonly used building materials.

11.	Buildings and structures occupied for aerosol storage shall be classified as Group S-1, provided that such buildings conform to the requirements of the Florida Fire Prevention Code.

12.	Display and storage of nonflammable solid and nonflammable or noncombustible liquid hazardous materials in quantities not exceeding the maximum allowable quantity per control area in Group M or S occupancies complying with Section 414.2.5.

13.	The storage of black powder, smokeless propellant and small arms primers in Groups M and R-3 and special industrial explosive devices in Groups B, F, M and S, provided such storage conforms to the quantity limits and requirements prescribed in the Florida Fire Prevention Code.

14.	Mercantile occupancies offering for retail sale sparklers, novelties and trick noisemakers as defined at Section 791.01, Florida Statutes, and that are not defined as fireworks by Chapter 791, Florida Statutes. Storage of sparklers and other novelties or trick noisemakers as defined in Chapter 791, Florida Statutes, within mercantile occupancies shall be in accordance with Section 791.055, Florida Statutes.

307.1.1 Hazardous materials.  Change to read as shown.

307.1.1 Hazardous materials. Hazardous materials in any quantity shall conform to the requirements of this code, including Section 414, and the Florida Fire Prevention Code.

[F] TABLE 307.1(1) MAXIMUM ALLOWABLE QUANTITY PER CONTROL AREA OF HAZARDOUS MATERIALS POSING A PHYSICAL HAZARDa, j, m, n, p  Change to read as shown.

Table 307.1(1) Footnotes e, i, j, and p.

e. Maximum allowable quantities shall be increased 100 percent when stored in approved storage cabinets, day boxes, gas cabinets or exhausted enclosures or in listed safety cans in accordance with Section 2703.9.10 of the International  Florida Fire Prevention Code. Where Note d also applies, the increase for both notes shall be applied accumulatively.

i. The maximum allowable quantity shall not apply to fuel oil storage complying with Section 603.3.2 of the International Florida Fire Prevention Code.

j. Quantities in parenthesis indicate quantity units in parenthesis at the head of each column.

m. For gallons of liquids, divide the amount in pounds by 10 in accordance with Section 2703.1.2 of the International Florida Fire Prevention Code.

p. The following shall not be included in determining the maximum allowable quantities:

1. Liquid or gaseous fuel in fuel tanks on vehicles.

2. Liquid or gaseous fuel in fuel tanks on motorized equipment operated in accordance with this code.

3. Gaseous fuels in piping systems and fixed appliances regulated by the International Florida Building Code, Fuel Gas Code.

4. Liquid fuels in piping systems and fixed appliances regulated by the International Florida Building Code, Mechanical Code.

Table 307.1(2) Maximum Allowable Quantity per Control Area of Hazardous Materials Posing a Physical Hazard.  Change to read as shown.

Table 307.1(2) Footnotes f, g, & i.

f. Maximum allowable quantities shall be increased 100 percent when stored in approved storage cabinets, gas cabinets or exhausted enclosures as specified in the Florida Fire Prevention Code. Where Note e also applies, the increase for both notes shall be applied accumulatively.

g. Allowed only when stored in approved exhausted gas cabinets or exhausted enclosures as specified in the Florida Fire Prevention Code.

i. For gallons of liquids, divide the amount in pounds by 10 in accordance with Section 2703.1.2 of the International Florida Fire Prevention Code.

307.2 Definitions.  Change to read as shown.

CONTROL AREA. Spaces within a building where quantities of hazardous materials not exceeding the maximum allowable quantities per control area are stored, dispensed, used or handled. See also the definition of "Outdoor control area" in the Florida Fire Prevention Code.

DAY BOX. A portable magazine designed to hold explosive materials constructed in accordance with the requirements for a Type 3 magazine as defined and classified in Chapter 33 of the Florida Fire Prevention Code.

HAZARDOUS MATERIALS. Those chemicals or substances that are physical hazards or health hazards as defined and classified in this section and the Florida Fire Prevention Code, whether the materials are in usable or waste condition.

308 Institutional Group I

308.1 Institutional Group I.  Change to read as shown.

308.1 Institutional Group I.   Institutional Group I occupancy includes, among others, the use of a building or structure, or a portion thereof, in which people are cared for or live in a supervised environment, having physical limitations because of health or age are harbored for medical treatment or other care or treatment, or in which people are detained for penal or correctional purposes or in which the liberty of the occupants is restricted. Institutional occupancies shall be classified as Group I-1, I-2 or I-3.

308.2 Group I-1.  Change to read as shown.

308.2 Group I-1.   This occupancy shall include buildings, structures or parts thereof housing more than 16 persons, on a 24-hour basis, who because of age, mental disability or other reasons, live in a supervised residential environment that provides personal care services. The occupants are capable of responding to an emergency situation without physical assistance from staff. This group shall include, but not be limited to, the following:

Residential board and care facilities

Assisted living facilities

Halfway houses

Group homes

Congregate care facilities

Social rehabilitation facilities

Alcohol and drug centers

Convalescent facilities

A facility such as the above with five or fewer persons shall be classified as a Group R-3 or shall comply with the Florida Building Code, Residential in accordance with Section 101.2. A facility such as above, housing at least six and not more than 16 persons, shall be classified as Group R-4.

308.5 Group I-4, day care facilities.  Change to read as shown.

308.5 Group I-4, day care facilities.  Reserved.

Section 309 Mercantile Group M

309.1 Mercantile Group M.  Change to read as shown.

309.1 Mercantile Group M.   Mercantile Group M occupancy includes, among others, buildings and structures or a portion thereof, for the display and sale of merchandise, and involves stocks of goods, wares or merchandise incidental to such purposes and accessible to the public. Mercantile occupancies shall include, but not be limited to, the following:

Department stores

Drug stores

Markets

Motor fuel-dispensing facilities

Retail or wholesale stores

Restaurants and drinking establishments with an occupant load of less than 50 persons

Sales rooms

310.1 Residential Group R.  Change to read as shown.

310.1 Residential Group R. Residential Group R includes, among others, the use of a building or structure, or a portion thereof, for sleeping purposes when not classified as an Institutional Group I or when not regulated by the Florida Building Code, Residential in accordance with Section 101.2. Residential occupancies shall include the following:

R-1 Residential occupancies containing sleeping units where the occupants are primarily transient in nature, including:

Boarding houses (transient)

Hotels (transient)

Motels (transient)

Congregate living facilities (transient) with 10or fewer occupants are permitted to comply with the construction requirements for Group R-3.

R-2  Residential occupancies containing sleeping units or more than two dwelling units where the occupants are primarily permanent in nature, including:

Apartment houses

Boarding houses (not transient)

Convents

Dormitories

Fraternities and sororities

Hotels (nontransient)

Live/work units

Monasteries

Motels (nontransient)

Vacation timeshare properties

Congregate living facilities with 16 or fewer occupants are permitted to comply with the construction requirements for Group R-3.

R-3 Residential occupancies where the occupants are primarily permanent in nature and not classified as Group R-1, R-2, R-4 or I, including:

Buildings that do not contain more than two dwelling units.

Adult care facilities that provide accommodations for five or fewer persons of any age for less than 24 hours.

Child care facilities that provide accommodations for five or fewer persons of any age for less than 24 hours.

Congregate living facilities with 16 or fewer persons.

Adult and child care facilities that are within a single-family home are permitted to comply with the Florida Building Code, Residential.

R-4 Residential occupancies shall include buildings arranged for occupancy as residential care/assisted living facilities including more than five but not more than 16 occupants, excluding staff.

Group R-4 occupancies shall meet the requirements for construction as defined for Group R-3, except as otherwise provided for in this code, or shall comply with the Florida Building Code, Residential provided the building is protected by an automatic sprinkler system installed in accordance with Section 903.2.8.

Section 313 Day-Care Occupancy Group D.  Add text to read as shown.

313 Day-Care Occupancy Group D.

313.1 Scope.  Add text to read as shown.

313.1 Scope. Group D occupancy is the use of a building or structure, or any portion thereof, in which three or more clients receive care, maintenance and supervision, by other than their relative(s) or legal guardian(s), for less than 24 hours per day. Occupancies that include part-day preschools, kindergartens and other schools whose purpose is primarily educational even though the children are of preschool age shall comply with the provisions for Group E occupancies.

313.2 Subclassifications.  Add text to read as shown.

313.2 Subclassifications. Day care occupancies in which more than 12 clients receive care, maintenance and supervision, by other than their relative(s) or legal guardian(s), for less than 24 hours per day shall be classified as day care occupancies. Day care occupancies of 12 or fewer clients shall be classified as day care homes and shall be divided into classifications as set forth in this section.

313.2.1 Family day care home.  Add text to read as shown.

313.2.1 Family day care home. A family day care home is a day care home in which more than three but fewer than seven clients receive care, maintenance and supervision by other than their relative(s) or legal guardian(s) for less than 24 hours per day with no more than two clients incapable of self-preservation.

313.2.2 Group day care home.  Add text to read as shown.

313.2.2 Group day care home. A group day care home is a day-care home in which at least seven but not more than 12 clients receive care, maintenance, and supervision by other than their relative(s) or legal guardian(s) for less than 24 hours per day with no more than three clients incapable of self-preservation.

313.2.3 Adult day care.  Add text to read as shown.

313.2.3 Adult day care.   Adult day care shall include any building or portion thereof used for less than 24 hours per day to house more than three adults requiring care, maintenance and supervision by other than their relative(s). Clients shall be ambulatory or semiambulatory and shall not be bedridden. They shall not exhibit behavior that is harmful to themselves or others.

313.2.4 Group D occupancies.  Add text to read as shown.

313.2.4 Group D occupancies.   Group D occupancies shall include, among others, the following:

Child day care occupancies

Adult day care occupancies, except where part of a health care occupancy

Nursery schools

Day care homes

Kindergarten classes that are incidental to a child day care occupancy

In cases where care is incidental to some other occupancy, the section of this code governing such other occupancy shall apply.

Chapter 4, Special Detailed Requirements Based on Use and Occupancy

See Chapter 4

history

Chapter 5, General Building Heights and Areas

Section 503 General Height and Area Limitations.

Table 503 Allowable Height and Building Areas.  Change to read as shown.

Under “Group” -  Change “E” to “E/D” and “F2” to “F2/F3”.and remove “I -4” from the Table.

Section 503.1.1 Special industrial occupancies, revise to read as follows:

503.1.1 Special industrial occupancies. Reserved. Buildings and structures designed to house special industrial processes that require large areas and unusual heights to accommodate craneways or special machinery and equipment, including, among others, rolling mills; structural metal fabrication shops and foundries; or the production and distribution of electric, gas or steam power, shall be exempt from the height and area limitations of Table 503.

503.1.4 Basements.  Add to read as shown.

503.1.4 Basements.  A basement of a building shall not count as a story when applying Table 503 for allowable building height.

503.1.5 Group A and E basements.  Add to read as shown.

503.1.5 Group A and E basements.  Group A and E basements used as classrooms or assembly rooms shall be counted as a story.

Section 504 Building Height

504.1 General.  Change to read as shown.

504.1 General Special unlimited height.  The height of Group B, M and R occupancies of Type I-B construction shall not be limited, provided the fire resistance of all columns shall be not less than 3 hours and the other structural members including floors shall be not less than that shown in Chapter 6, but in no case less than 2 hours except that roofs and their supporting beams, girders, trusses and arches shall be not less than 1½ hours.  The building height permitted by Table 503shall be increased in accordance with this section.

Exception: No change

1. The height of Group B, M and R occupancies of Type I-B construction shall not be limited, provided the fire resistance of all columns shall be not less than 3 hours and the other structural members including floors shall be not less than that shown in Chapter 6, but in no case less than 2 hours except that roofs and their supporting beams, girders, trusses and arches shall be not less than 1½ hours.

2. The building height of one-story aircraft hangars, aircraft paint hangars and buildings used for the manufacturing of aircraft shall not be limited if the building is provided with an automatic fire-extinguishing system in accordance with Chapter 9 and is entirely surrounded by public ways or yards not less in width than one and one-half times the building height.

[F4617]

504.2 Automatic sprinkler system increase, Exception 3.  Change to read as shown.

504.2 Automatic sprinkler system increase. …..

Exceptions:

1 – 2 no change

3. Fire-resistance rating substitution in accordance with Table 601, Note hd.

Section 505 Mezzanines

505.2 Area limitation.  Change to read as shown.

505.2 Area limitation. The aggregate area of a mezzanine or mezzanines within a room shall not exceed one-third of the floor area of that room or space in which they are located. The enclosed portion of a room shall not be included in a determination of the floor area of the room in which the mezzanine is located. In determining the allowable mezzanine area, the area of the mezzanine shall not be included in the floor area of the room.

Exceptions:

1. The aggregate area of mezzanines in buildings and structures of Type I or II construction for special industrial occupancies in accordance with Section 306.4 shall not exceed two-thirds of the area of the room.

2. The aggregate area of mezzanines in buildings and structures of Type I or II construction shall not exceed one-half of the area of the room in buildings and structures equipped throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1 and an approved emergency voice/alarm communication system in accordance with Section 907.5.2.2.

3.    In sprinklered Group S2 occupancies of Type III construction, the enclosed and unenclosed areas under mezzanines shall be allowed to be included when calculating the permissible size of mezzanines.

506.3 Automatic sprinkler system increase. – Change to read as shown.

506.3 Automatic sprinkler system increase. (no change to text).

Exceptions: The building area limitation increases shall not be permitted for the following conditions:

1. (no change)

2. (no change)

3. Fire-resistance rating substitution in accordance with Table 601, Note d h.

[F4619]

Section 507 Unlimited Area Buildings

507.2 Nonsprinklered, one story. Change to read as shown.

507.2 Nonsprinklered, one story. Reserved.

507.10 Group E buildings, Item 1.  Change to read as shown.

507. 10 Group E buildings.  The area …..

1.	Each classroom shall have not less than two means of egress, with one of the means of egress being a direct exit to the outside of the building complying with Section 1020 or the building is provided with smoke barriers having a minimum 1-hour fire-resistance rating dividing the building into areas not to exceed 30,000 square feet (2,787 m2) in floor area.

2 – 3 no change.

Section 508 Mixed Use and Occupancy

508.1 General. – Change to read as shown.

508.1 General. Each portion of a building shall be individually classified in accordance with Section 302.1. Where a building contains more than one occupancy group, the building or portion thereof shall comply with the applicable provisions of Section 508.2, 508.3 or 508.4, or a combination of these sections.

Exceptions:

1. Occupancies separated in accordance with Section

509.

2. Where required by Table 415.3.2, areas of Groups

H-1, H-2 and H-3 occupancies shall be located in a separate and detached building or structure.

3. Uses within live/work units, complying with Section 438 419, are not considered separate occupancies.

[F4620]

Table 508.4 Required Separation of Occupancies (hours). Make the following changes:

Under  “Occupancy” -  add “D” to the “E,A” in the 3rd raw ; remove “I-4” from the 4th raw; add F3 to the 8th raw.

In the 1st raw add “D” to “A,E”; remove “I-4” from “I-1, I-3, I-4”; add “F3” to “F2,F3,S2, U”.

Section 509 Special Provisions

509.4 Parking beneath Group R.  Change to read as shown.

509.4 Parking beneath Group R.  Where a maximum one-story above grade plane Group S-2 parking garage, enclosed or open, or combination thereof, of Type I construction or open of Type IV construction, with grade entrance, is provided under a building of Group R, the number of stories to be used in determining the minimum type of construction shall be measured from the floor above such a parking area. The number of stories to be used in determining the height in stories in accordance with Section 903.2.11.3 903.6 shall include the parking garage as a story. The floor assembly between the parking garage and the Group R above shall comply with the type of construction required for the parking garage and shall also provide a fire-resistance rating not less than the mixed occupancy separation required in Section 508.4.

[F4621]

Chapter 6, Types of Construction

Section 601 General

Table 601 Fire Resistance Rating Requirements for Building Elements (hours).  Change to read as shown.

| TABLE 601 |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| FIRE-RESISTANCE RATING REQUIREMENTS FOR BUILDING ELEMENTS (hours) |  |  |  |  |  |  |  |  |  |
| BUILDING ELEMENT | TYPE I |  | TYPE II |  | TYPE III |  | TYPE IV | TYPE V |  |
|  | A | B | A | B | A | B | HT | A | B |
| Primary Structural frameg (See Section 202) | 3a,ih | 2a | 1 | 0 | 1 | 0 | HT | 1 | 0 |
| Bearing walls |  |  |  |  |  |  |  |  |  |
| Exterior f, g | 4 | 3 | 1 | 0 | 2 | 2 | 2 | 1 | 0 |
| Interior | 4a | 3a | 1 | 0 | 1 | 0 | 2ab /HT | 1 | 0 |
| Nonbearing walls and partitions |  |  |  |  |  |  |  |  |  |
| Exterior | See Table 602 |  |  |  |  |  |  |  |  |
| Nonbearing walls and partitions Interior e | 0 | 0 | 0 | 0 | 0 | 0 | See Section 602.4.6 | 0 | 0 |
| Floor construction and secondary members Including supporting beams and joists (See Section 202) | 3ih | 2 | 1de | 0deji | 1d | 0d,i | HT | 1 | 0ji |
| Roof construction and secondary members Including supporting beams and joists (See Section 202) | 11/2 b,ih | 1b, c | 1b, c | 0 c | 1b, c | 0 | HT | 1b, c | 0 |
| For SI: 1 foot = 304.8 mm. |  |  |  |  |  |  |  |  |  |
| a. : Fire-resistance ratings of primary structural frame and bearing walls are permitted to be reduced by 1 hour where supporting one floor or one roof only. |  |  |  |  |  |  |  |  |  |
| b. Except in Group F-1, H, I, M and S-1 occupancies, fire protection of structural members shall not be required, including protection of roof framing and decking where every part of the roof construction is 20 feet or more above any floor immediately below. Fire-retardant-treated wood members shall be allowed to be used for such unprotected members. |  |  |  |  |  |  |  |  |  |
| c. In all occupancies, heavy timber shall be allowed where a 1-hour or less fire-resistance rating is required. |  |  |  |  |  |  |  |  |  |
| d. Group B and M occupancies of Type II or III construction five or more stories in height shall be required to have a minimum 2-hour fire-resistance rating for the floor construction located over the basement. |  |  |  |  |  |  |  |  |  |
| e. Not less than the fire-resistance rating required by other sections of this code. |  |  |  |  |  |  |  |  |  |
| f. Not less than the fire-resistance rating based on fire separation distance (see Table 602). |  |  |  |  |  |  |  |  |  |

g. Not less than the fire-resistance rating as referenced in Section 704.10.

hih. For Group A, B, E, F and R occupancies and parking garages, the required fire-resistance ratings for the structural frame, floor and roof construction, including supporting beams and joists, shall be permitted to be reduced by 1-hour where the building is protected throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1 , but the fire resistance rating shall not be less than 1-hour.

iji. For unsprinklered Group E occupancies of Type, II-B, III-B, IV or V-B construction, the floor construction located immediately above useable space in basements shall have a fire-resistance rating of not less than 1-hour.

[F4667]

Section 602 Construction Classification.

Table 602 Fire-Resistance Rating Requirements for Exterior Walls Based on Fire Separation Distance.  Change to read as shown.

TABLE 602 
FIRE-RESISTANCE RATING REQUIREMENTS FOR EXTERIOR 
WALLS BASED ON FIRE SEPARATION DISTANCE a, e

| FIRE SEPARATION DISTANCE = x (feet) | TYPE OF CONSTRUCTION | GROUP Hf | GROUP F-1, M, S-1g | GROUP A, B, E, F-2, I, R b , S-2g, Ub |
| --- | --- | --- | --- | --- |
| xc | I-A, I-B, III-A, III-B, IV Others | 3 3 | 3 2 | 3 1 |
| 5  x < 10 | I-A, I-B, III-A, III-B, IV Others | 3 2 | 2 1 | 2 1 |
| 10  x < 20 | I-A, I-B, III-A, III-B, IV IIB, VB Others | 2 1 1 | 2 0 1 | 2 d 0 1 d |
| 20  x < 30 | I-A, I-B, III-A, III-B, IV Others | 1 1 | 1 0 | 1 d 0 |
| x30 | All | 0 | 0 | 0 |

For SI:     1 foot = 304.8 mm.

a. Load-bearing exterior walls shall also comply with the fire-resistance rating requirements of Table601.

b. For special requirements for Group U occupancies see Section 406.1.2

c. See Section 706.1.1 705.1.1 for party walls.

[F4666]

d. Open parking garages complying with Section 406 shall not be required to have a fire-resistance rating.

e. The fire-resistance rating of an exterior wall is determined based upon the fire separation distance of the exterior wall and the story in which the wall is located.

f. For special requirements for Group H occupancies, see Section 415.3.

g. For special requirements for Group S aircraft hangars, see Section 412.4.1.

Section 603 Combustible Material in Type I and II Construction

603.1 Allowable materials.  Change to read as shown.

603.1 Allowable materials…..

Exceptions:  1 – 24 no change.

25.	Materials exposed within plenums complying with Section 602 of the Florida Building Code, Mechanical.

603.1.1 Ducts.  Change to read as shown.

603.1.1 Ducts. The use of nonmetallic ducts shall be permitted when installed in accordance with the limitations of the Florida Building Code, Mechanical.

603.1.2 Piping.  Change to read as shown.

603.1.2 Piping. The use of combustible piping materials shall be permitted when installed in accordance with the limitations of the Florida Building Code, Mechanical and the Florida Building Code, Plumbing.

CHAPTER 7 FIRE AND SMOKE PROTECTION FEATURES

Section 702 Definitions

702.1 Definitions.  Change to read as shown.

JOINT. The linear opening in or between adjacent fire-resistance-rated assemblies that is designed to allow independent movement of the building in any plane caused by thermal, seismic, wind or any other loading.

704.12 Seismic isolation systems. Reserved.  Fire-resistance ratings for the isolation system shall meet the fire-resistance rating required for the columns, walls or other structural elements in

which the isolation system is installed in accordance with Table 601. Isolation systems required to have a fire-resistance rating shall be protected with approved materials or construction assemblies designed to provide the same degree of fire resistance as the structural element in which it is installed when tested in accordance with ASTM E 119 or UL 263 (see Section

703.2).

Such isolation system protection applied to isolator units shall be capable of retarding the transfer of heat to the isolator unit in such a manner that the required gravity load-carrying

capacity of the isolator unit will not be impaired after exposure to the standard time-temperature curve fire test prescribed in ASTM E 119 or UL 263 for a duration not less than that

required for the fire-resistance rating of the structure element in which it is installed.

Such isolation system protection applied to isolator units shall be suitably designed and securely installed so as not to dislodge, loosen, sustain damage or otherwise impair its ability

to accommodate the seismic movements for which the isolator unit is designed and to maintain its integrity for the purpose of providing the required fire-resistance protection.

Section 705.8.1 Allowable area of openings, revise text to read as follows:

705.8.1 Allowable area of openings. The maximum area of unprotected and protected openings permitted in an exterior wall in any story of a building shall not exceed the percentages

specified in Table 705.8.

Exceptions:

1. In other than Group H occupancies, unlimited unprotected openings are permitted in the exterior walls of the  first story above grade either:

1.1. Where the wall faces a street and has a fire separation distance of more than 15 feet

(4572 mm); or

1.2. Where the wall faces an unoccupied space.  The unoccupied space shall be on the same

lot or dedicated for public use, shall not be less than 30 feet (9144 mm) in width and

shall have access from a street by a posted fire lane in accordance with the International

Fire Code. Florida Fire Prevention Code.

2. Buildings whose exterior bearing walls, exterior nonbearing walls and exterior primary structural frame are not required to be fire-resistance rated shall be permitted to have unlimited unprotected openings.

Section 706 Fire Walls

706.1.1 Party walls. Any wall located on a lot line between adjacent buildings, which is used or adapted for joint service between the two buildings, shall be constructed as a fire wall and shall provide a 4-hour fire-resistance rating in accordance with Section 706, without openings and shall create separate buildings.

Exception: Openings in a party wall separating an anchor building and a mall shall be in accordance with Section 402.7.3.1. [3658]

Table 706.4 Fire Wall Fire-Resistance Ratings.  Change to read as shown.

Delete reference to Note “c” in the table heading.–.

| TABLE 706.4 FIRE WALL FIRE-RESISTANCE RATINGS c [F4622] |  |
| --- | --- |
| GROUP | FIRE-RESISTANCE RATING (hours) |
| A, B, D, E, H-4, I, R-1, R-2, U | 3a |
| F-1, H-3b, H-5, M, S-1 | 3 |
| H-1, H-2 | 4b |
| F-2, S-2, R-3, R-4 | 2 |
| a. In Type II or V construction, walls shall be permitted to have a 2-hour fire-resistance rating. b. For Group H-1, H-2 or H-3 buildings, also see Sections 415.4 and 415.5. |  |

c. For the purposes of determining height and area in accordance with Table 503, fire walls dividing buildings into separate buildings shall provide a 4-hour fire-resistance rating.[3659]

706.4.1 Townhouse fire separation.  Add to read as shown.

706.4.1 Townhouse fire separation.

706.4.1.1  Add to read as shown.

706.4.1.1   Each townhouse shall be considered a separate building and shall be separated from adjoining townhouses by a party wall complying with Section 706.1.1 or by the use of separate exterior walls meeting the requirements of Tables 601 and 602 for zero clearance from property lines as required for the type of construction. Separate exterior walls shall include one of the following:

1.	A parapet not less than 18 inches (457 mm) above the roof line.

2.	Roof sheathing of noncombustible material or fire retardant treated wood, for not less than a 4 foot (1219 mm) width on each side of the exterior dividing wall.

3.	One layer of 5/8 inch (15.9 mm) Type X gypsum board attached to the underside of roof decking, for not less than a 4 foot  (1219 mm) width on each side of the exterior dividing wall.

706.4.1.2.  Add to read as shown.

706.4.1.2   When not more than three stories in height, townhouses may be separated by a single wall meeting the following requirements:

1.	Such wall shall provide not less than a 2-hour fire-resistance rating. Plumbing, piping, ducts, electrical or other building services shall not be installed within or through the 2-hour wall, unless such materials and methods of penetration have been tested in accordance with Section 703.

2.	Such wall shall be continuous from the foundation to the underside of the roof sheathing or shall have a parapet extending not less than 18 inches (457 mm) and no less than a 4-foot (1219 mm) width on each side of the wall shall be of noncombustible material, or fire-retardant-treated wood, or one layer of 5/8-inch (15.9 mm) Type X gypsum wallboard attached to the underside of the roof decking.

3.	Each dwelling unit sharing such wall shall be designed and constructed to maintain its structural integrity independent of the unit on the opposite side of the wall.

Exception: Said wall may be penetrated by roof and floor structural members provided that the fire-resistance rating and the structural integrity of the wall is maintained.

Section 707 Fire Barriers

707.1 General.  Change to read as shown.

707.1 General. Fire barriers installed as required elsewhere in this code or the Florida Fire Prevention Code shall comply with this section.

Table 707.3.9 Fire-Resistance Rating Requirements for Fire Barrier Assemblies between Fire Areas.  Change to read as shown.

| TABLE 707.3.9 FIRE-RESISTANCE RATING REQUIREMENTS FOR FIRE BARRIER ASSEMBLIES BETWEEN FIRE AREAS |  |
| --- | --- |
| OCCUPANCY GROUP | FIRE-RESISTANCE RATING (hours) |
| H-1, H-2 | 4 |
| F-1, H-3, S-1 | 3 |
| A, B, D, E, F-2, F-3, H-4, H-5, I, M, R, S-2 | 2 |
| U | 1 |

708.2 Shaft enclosure required.  Change to read as shown.

708.2 Shaft enclosure required. Openings through a floor/ceiling assembly shall be protected by a shaft enclosure complying with this section.

Exceptions:

1. – 3.  No change.

4. A shaft enclosure is not required for penetrations by ducts protected in accordance with Section 716.6. Grease ducts shall be protected in accordance with the  Florida Building Code, Mechanical.

[Remaining text no change.]

Section 709 Fire Partitions

709.1 General.  Change to read as shown.

709.1 General. The following wall assemblies shall comply with this section.

1. Walls separating dwelling units in the same building as required by Section 438.2.

2. Walls separating sleeping units in the same building as required by Section 438.2.

3. Walls separating tenant spaces in covered mall buildings as required by Section 402.7.2.

4. Corridor walls as required by Section 1018.1.

5. Elevator lobby separation as required by Section 708.14.1

6. Wall separating individual tenant spaces.

Exceptions:

1.	In Group B and S occupancies, walls used to separate tenants shall not be required to have a fire-resistance rating, provided no area between fire partitions having a 1-hour fire-resistance rating exceeds 3,000 square feet (279 m2).

2.	In aircraft hangar occupancies, walls used to separate tenants shall not be required to have a fire-resistance rating, provided the aircraft hanger is constructed in accordance with the requirements of Section 412.2.

3.	In mini-warehouses/self-storage buildings, walls used to separate tenants shall not be required to have fire-resistance rating, provided a sprinkler system meeting the requirements of Ordinary Hazard Group II as defined by NFPA 13, is installed employing quick response heads.

4. Other than dwelling units or sleeping units, walls used to separate individual tenant spaces shall not be required to have a fire-resistance rating when the building is protected by a complete automatic sprinkler system installed in accordance with section 903.3.1.1.[3523]

709.4.1 Roof construction.  Add to read as shown.

709.4.1 Roof Construction. When the fire partition is continuous to the underside of the roof sheathing in occupancies of Groups R-1, R-2 and R-3 as applicable in Section 101.2, in Type III, IV and V construction the following shall be provided:

709.4.1.1 Roof sheathing.  Add to read as shown.

709.4.1.1 Roof Sheathing. The roof sheathing or deck shall be of approved noncombustible materials or of fire-retardant-treated wood, for a distance of 4 feet (1220 mm); or

709.4.1.2 Roof protection.  Add to read as shown.

709.4.1.2 Roof Protection. The roof shall be protected with 0.625-inch (15.88 mm) Type X gypsum board directly beneath the underside of the roof sheathing or deck, supported by a minimum of nominal 2-inch (51 mm) ledgers attached to the sides of the roof framing members, for a minimum distance of 4 feet (1220 mm).

Section 713 Penetrations

Section 713.6 Add new text to read as follows:

713.6 Fire walls, Fire Barriers, Fire Partitions, Smoke Barriers and Smoke partitions or any other wall required to have protected openings shall be effectively and permanently identified with signs or stenciling in a manner acceptable to the Authority having Jurisdiction.  Such identification shall be above any decorative ceiling and in concealed spaces.  Suggested wording for fire and smoke barriers: “FIRE AND SMOKE BARRIER – PROTECT ALL OPENINGS.”

Section 714 Fire-Resistant Joint Systems

714.4 Exterior curtain wall/floor intersection.  Change to read as shown.

714.4 Exterior curtain wall/floor intersection. Where fire resistance-rated floor or floor/ceiling assemblies are required, voids created at the intersection of the exterior curtain wall assemblies and such floor assemblies shall be sealed with an approved system to prevent the interior vertical spread of fire. Such systems shall be securely installed and tested in accordance with ASTME 2307 to prevent the passage of flame for the time period at least equal to the fire-resistance rating of the floor assembly and prevent the passage of heat and hot gases sufficient to ignite cotton waste. Height and fire-resistance requirements for curtain wall spandrels shall comply with Section

705.8.5.

Section 716 Ducts and Air Transfer Openings

716.2.2 Hazardous exhaust ducts.  Change to read as shown.

716.2.2 Hazardous exhaust ducts.  Fire dampers for hazardous exhaust duct systems shall comply with the Florida Building Code, Mechanical.

Chapter 8 Interior Finishes

Revise Section 801.5 to read as follows:

801.5 Applicability. For buildings in flood hazard areas as established in Section 1612.3, interior finishes, trim and decorative materials that extend below the elevation required by Section 1612.4 design flood elevation shall be flood-damage-resistant materials. [4398]

Section 803 Wall and Ceiling Finishes

Table 803.9 Interior Wall and Ceiling Finish Requirements by Occupancy.

Revise to add “D” to the 4th raw of the 1st column and remove I-4 raw from the Table.

Section 804.4.1 Minimum critical radiant flux, revise text to read as follows:

804.4.1 Minimum critical radiant flux. Interior floor finish and floor covering materials in exit enclosures, exit passageways and corridors shall not be less than Class I in Groups I-1, I-2 and I-3 and not less than Class II in Groups A, B, E, H, I-4, M, R-1, R-2 and S. In all areas, floor covering materials shall comply with the DOCFF-1 “pill test” (CPSC 16 CFR, Part 1630).

Exception: No change

Chapter 9 Fire Protection Systems

Section 901 General

Section 901.1 Scope, revise text to read as follows:

901.1 Scope. The provisions of this chapter shall specify where fire protections systems are required and shall apply to the design, installation and operation of fire protection systems and carbon monoxide detection alarms.

901.2 Fire protection systems.  Change to read as shown.

901.2 Fire protection systems.  Fire protection systems shall be installed, repaired, operated and maintained in accordance with this code and the Florida Fire Prevention Code.

Any fire protection system for which an exception or reduction to the provisions of this code has been granted shall be considered to be a required system.

Exception: Any fire protection system or portion thereof not required by this code shall be permitted to be installed for partial or complete protection provided that such system meets the requirements of this code.

901.3 Modifications.  Change to read as shown.

901.3 Modifications.  No person shall remove or modify any fire protection system installed or maintained under the provisions of this code or the Florida Fire Prevention Code without approval by the building official.

901.5 Acceptance tests.  Change to read as shown.

901.5 Acceptance tests.  Fire protection systems shall be tested in accordance with the requirements of this code and the Florida Fire Prevention Code. When required, the tests shall be conducted in the presence of the building official. Tests required by this code, the Florida Fire Prevention Code and the standards listed in this code shall be conducted at the expense of the owner or the owner’s representative. It shall be unlawful to occupy portions of a structure until the required fire protection systems within that portion of the structure have been tested and approved.

901.6.1 Automatic sprinkler systems.

901.6.1 Automatic sprinkler systems. Automatic sprinkler systems shall be monitored by an approved supervising station.

Exceptions:

1. A supervising station is not required for automatic sprinkler systems protecting one- and two-family dwellings.

2. Limited area systems serving fewer than six 20 sprinklers. [3921]

[F4623]

901.6.2 Fire alarm systems.  Fire alarm systems required by the provisions of Section 907.2 of this code and the Florida Fire Prevention Code shall be monitored by an approved supervising station in accordance with Section 907.6.5.

Exceptions: No change

Section 903 Automatic Sprinkler Systems

903.2.3 Group E.  Change to read as shown.

903.2. 3 Group E.  An automatic sprinkler system shall be provided for Group E occupancies as follows:

1 – 2 No change

Exception: An automatic fire sprinkler system is not required in existing educational buildings unless 50 percent of the aggregate area of the building is being remodeled.

903.2.7.1 High-piled storage.  Change to read a shown.

903.2.7.1 High-piled storage.  An automatic sprinkler system shall be provided in accordance with the Florida Fire Prevention Code in all buildings of Group M where storage of merchandise is in high-piled or rack storage arrays.

903.2.11.3 Buildings over 55 feet in height.  Change to read a shown.

903.2.11.3 Buildings over 55 feet in height. Reserved. Buildings three stories or more in height.

Any building which is of three stories or more in height shall be equipped with an approved automatic sprinkler system installed in accordance with Section 903.1.

Exceptions:

1.           Single- and two-family dwellings.

2.           A stand-alone parking garage constructed with noncombustible materials, the design of which is such that all levels of the garage are uniformly open to the atmosphere on all sides with the percentages of openings equal to or greater than those specified in Section 406.3. Such garages shall be separated from any other structure by not less than 20 feet (6096 mm). A stand-alone parking garage is one that is solely for the parking of vehicles and does not have any other occupancy group in the building.

3.         Telecommunication spaces located within telecommunication buildings, if the spaces are equipped to meet an equivalent fire prevention standard approved by both the Florida Building Commission and the State Fire Marshal.

4.           Telecommunications spaces within telecommunication buildings, if the telecommunications space is equipped with:

4.1. Air sampling smoke detection.

4.2. Remote, propietary or central station fire alarm monitoring.

4.3. Automatic smoke exhaust system.

4.4. One-hour fire-resistance wall separating the telecommunications space from the adjacent areas on the same floor.

4.5. Two-hour floor/ceiling assembly separating the telecommunications space from adjacent floors.

4.6. All other portions ancillary to the telecommunications equipment area shall be provided with fire sprinkler protection.

5.         Sprinkler systems installed solely as a requirement of Section 903.62.11.3 may be a NFPA 13R or NFPA 13D system in accordance with their scopes.

903.2.11.3.1 NFPA 101 as adopted by Florida Fire Prevention Code, as regarding the requirements for fire protection sprinklers, is applicable to all multiple-family residential buildings, whether designated as townhouses, condominiums, apartment houses, tenements, garden apartments or by any other name. The attorney general has determined that for the purpose of the fire protection sprinkler requirements in Section 553.895(2), Florida Statutes, townhouses that are three or more stories tall and consist of three or more units together are multiple-family dwellings. Therefore, these types of townhouses are not exempt from being considered for the requirements to provide fire protection sprinklers (even if there are any other definitions that define a townhouse as a single-family residence). When determining whether townhouses require fire protection sprinkler systems, the building official must consider in parallel: (a) the attorney general’s opinion defining the statutory language for townhouses; (b) the building code requirements, including all life-safety chapters, that provide additional determining criteria, such as construction types, fire-resistance, fire protection systems and egress; and (c) the NFPA 101 as adopted by Florida Fire Prevention Code, egress and protection determining criteria. The more restrictive criteria are then applied.

[3508]

903.2.11.4 Ducts conveying hazardous exhausts.   Change to read a shown.

[F] 903.2.11.4 Ducts conveying hazardous exhausts.  Where required by the Florida Building Code, Mechanical, automatic sprinklers shall be provided in ducts conveying hazardous exhaust, or flammable or combustible materials.

Exception: Ducts in which the largest cross-sectional diameter of the duct is less than 10 inches (254 mm).

903.2.12 During construction.  Change to read as shown.

903.2.12 During construction.  Automatic sprinkler systems required during construction, alteration and demolition operations shall be provided in accordance with the Florida Fire Prevention Code.

Table 903.2.11.6 Additional Required Suppression Systems.  Change the last raw to read as follows:

IFC Florida Fire Prevention Code                    Sprinkler system requirements as set forth in Section 903.2.11.6 of the Florida Fire Prevention Code

903.3.1.4.  Add to read as shown.

903.3.1.4  In Group R4 Small Facilities, an automated sprinkler systems installed in accordance with NFPA 13D or 13R with their scopes shall be permitted, provided the automatic sprinkler system is not be considered an alternative to other requirements of the code.

903.3.5 Water supplies.  Change to read as shown.

903.3.5 Water supplies.  Water supplies for automatic sprinkler systems shall comply with this section and the standards referenced in Section 903.3.1. The potable water supply shall be protected against backflow in accordance with the requirements of this section and the Florida Building Code, Plumbing.

903.3.5.1.1 Limited area sprinkler systems.  Change to read as shown.

903.3.5.1.1 Limited area sprinkler systems.  Limited area sprinkler systems serving six sprinklers or less on any single connection are permitted to be connected to the domestic service where a wet automatic standpipe is not available. Limited area sprinkler systems connected to domestic water supplies shall comply with each of the following requirements:

1 – 2 No change

903.3.5.2 Secondary water supply. Reserved.A secondary on-site water supply equal to the hydraulically calculated sprinkler demand, including the hose stream requirement, shall be provided for high-rise buildings assigned to Seismic Design Category C, D, E or F as determined by this code. The secondary water supply shall have a duration of not less than 30 minutes as determined by the occupancy hazard classification in accordance with

NFPA 13.

Exception: Existing buildings.

[F4624]

903.4 Sprinkler system monitoring and alarms.  Change to read as shown.

903.4 Sprinkler system monitoring and alarms. All valves controlling the water supply for automatic sprinkler systems, pumps, tanks, water levels and temperatures, critical air pressures and water-flow switches on all sprinkler systems shall be electrically supervised by a listed fire alarm control unit. in accordance with NFPA 72.

Exceptions:

1.	No change.

2.	Limited area systems serving six sprinklers or less.

3  -  7    No change.

[3513]

903.5 Testing and maintenance.  Change to read as shown.

903.5 Testing and maintenance.  Sprinkler systems shall be tested and maintained in accordance with the Florida Fire Prevention Code.

Section 904 Alternative Automatic Fire-Extinguishing Systems

904.2.1 Commercial hood and duct systems. Change to read as shown.

[F] 904.2.1 Commercial hood and duct systems. Each required commercial kitchen exhaust hood and duct system required by the Florida Fire Prevention Code or Chapter 5 of the Florida Building Code, Mechanical to have a Type I hood shall be protected with an approved automatic fire-extinguishing system installed in accordance with this code.

904.3.1 Electrical wiring.  Change to read as shown.

904.3.1 Electrical wiring.  Electrical wiring shall be in accordance with the Chapter 27 of this code.

904.11 Commercial cooking systems.  Change to read as shown.

[F] 904.11 Commercial cooking systems.  Change exception to read as follows:

Exception: Factory-built commercial cooking recirculating systems that are tested in accordance with UL 710B and listed, labeled and installed in accordance with Section 304.1 of the Florida Building Code, Mechanical.

Section 905 Standpipe Systems

905.1 General.  Change to read as shown.

905.1 General.

Standpipe systems shall be provided in all new buildings in which:

1.         The highest floor is greater than 30 feet (9144 mm) above the lowest level of fire department vehicle access; or

2.         The highest floor is more than three stories above grade; or

3.         The lowest floor is more than one story below grade; or

4.         The lowest floor is more than 20 feet (6.1 m) below grade.

Standpipe systems shall be provided in new buildings and structures in accordance with this section. Fire hose threads used in connection with standpipe systems shall be approved and shall be compatible with fire department hose threads. The location of fire department hose connections shall be approved. In buildings used for high-piled combustible storage, fire protection shall be in accordance with the Florida Fire Prevention Code. [3514]

905.3.1 Height.  Change to read as shown.

905.3.1 Height. Class III standpipe systems shall be installed throughout buildings where: the floor level of the highest story is located more than 30 feet (9144 mm) above the lowest level of fire department vehicle access, or where the floor level of the lowest story is located more than 30 feet (9144 mm) below the highest level of fire department vehicle access. High-rise buildings shall be protected throughout by a Class I standpipe system.

1. The floor level of the highest story is located more than 30 feet above the lowest level of fire department vehicle access; or

2. The floor level of the lowest story is located more than 20 feet below the highest level of fire department vehicle access; or

3. The lowest floor is more than one story below grade; or

4. The highest floor is more than three stories above grade.

Exceptions:

1 – 5  No change.

6.	In buildings less than 75 feet (22 860 mm) in height which are protected throughout with an approved and maintained fire sprinkler system, a manual wet standpipe, as defined in NFPA 14, Standard for the Installation of Standpipe, Private Hydrant, and Hose Systems, shall be allowed. [3514]

905.3.6 Helistops and heliports.  Change to read as shown.

905.3.6 Helistops and heliports.  Buildings with a helistop or heliport that are equipped with a standpipe shall extend the standpipe to the roof level on which the helistop or heliport is located in accordance with Section 1107.5 of the Florida Fire Prevention Code.

905.3.7 Marinas and boatyards.  Change to read as shown.

[F] 905.3.7 Marinas and boatyards. Standpipes in marinas and boatyards shall comply with Chapter 45 of the Florida Fire Prevention Code.

Section 906 Portable Fire Extinguishers

906.1 General.  Change to read as shown.

[F] 906.1 Where required. Portable fire extinguishers shall be installed in the following locations.

1. In new and existing Group A, B, E, F, H, I, M, R-1, R-2, R-4 and S occupancies.

Exception: In new and existing Group A, B and E occupancies equipped throughout with quick response sprinklers, portable fire extinguishers shall be required only in locations specified in Items 2 through 6.

2. Within 30 feet (9144 mm) of commercial cooking equipment.

3. In areas where flammable or combustible liquids are stored, used or dispensed.

4. On each floor of structures under construction, except Group R-3 occupancies, in accordance with Section 1415.1 of the Florida Fire Prevention Code.

5. Where required by the Florida Fire Prevention Code sections indicated in Table 906.1.

6. Special-hazard areas, including but not limited to laboratories, computer rooms and generator rooms, where required by the fire code official.

Table 906.1 Change to read as shown.

[F] Table 906.1 Additional Required Portable Fire Extinguishers in the International Fire Code.  Reserved.

906.4 Cooking grease fires.  Change to read as shown.

[F] 906.4 Cooking grease fires. Fire extinguishers provided for the protection of cooking grease fires shall be of an approved type compatible with the automatic fire-extinguishing system agent and in accordance with Section 904.11.5 of the Florida Fire Prevention Code.

Section 907 Fire Alarm and Detection Systems

907.1.1 Construction documents.  Change to read as shown.

[F] 907.1.1 Construction documents. Construction documents for fire alarm systems shall be of sufficient clarity to indicate the location, nature and extent of the work proposed and show in detail that it will conform to the provisions of this code, the Florida Fire Prevention Code, and relevant laws, ordinances, rules and regulations, as determined by the fire code building official.

907.1.4 Accessibility.  Add to read as shown.

907.1. 4 Accessibility.  Every required fire alarm system shall include a visible alarm indicating appliances in public and common areas. For more specific accessibility requirements related to alarm indicating appliances, refer to Section 11-4.28. applicable sections of the Florida Building Code, Accessibility .

[F4701]

907.2.2 Group B.  Change to read as shown.

- 907.2.2 Group B.  A manual fire alarm system in accordance with Section 907 shall be provided in all business occupancies where any one of the following conditions exists:

- 1.	The building is two or more stories in height above the level of exit discharge.

- 2.	The occupancy is subject to 50 or more occupants above or below the level of exit discharge.

3.	The occupancy is subject to 300 or more total occupants.

Exception: Manual fire alarm boxes are not required where the building is equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1 and the occupant notification appliances will activate throughout the notification zones upon sprinkler waterflow. [3517]

907.2.4 Group F.  Change to read as shown.

907.2.4 Group F.  A fire alarm system shall be required in accordance with Section 907 for industrial occupancies, unless the total capacity of the building is under 100 persons and of these fewer than 25 persons are above or below the level of exit discharge.

907.2.5 Group H.  Change to read as shown.

907.2.5 Group H.  A manual fire alarm system shall be installed in Group H-5 occupancies and in occupancies used for the manufacture of organic coatings. An automatic smoke detection system shall be installed for highly toxic gases, organic peroxides and oxidizers in accordance with the Florida Fire Prevention Code.

907.2.9.1 Manual fire alarm system.  A manual fire alarm system that activates the occupant notification system in accordance with Section 907.5 shall be installed in Group R-2 occupancies where:

1 - 2 No change.

3. The building contains more than 11 dwelling units or sleeping units.

Exceptions:  No change.

907.2.11.1 Group R-1.  Change to read as shown.

907.2.11.1  Group R-1.  An approved single-station smoke alarm shall be installed in every guestroom and every living area and sleeping room within a guest suite.

907.2.13 High-rise building, Exceptions.

1-3 No change.

4. Reserved.

5-6 No change.

907.2.13.2 Fire department communication system.  Change to read as shown.

[F] 907.2.13.2 Fire department communication system.  Where a wired communication system is approved in lieu of a radio coverage system in accordance with Section 510 of the Florida Fire Prevention Code, the wired fire department communication system shall be designed and installed in accordance with NFPA72 and shall operate between a fire command center complying with Section 911, elevators, elevator lobbies, emergency and standby power rooms, fire pump rooms, areas of refuge and inside enclosed exit stairways. The fire department communication device shall be provided at each floor level within the enclosed exit stairway.

907.2.15 High-piled combustible storage areas.  Change to read as shown.

907.2.15 High-piled combustible storage areas.  An automatic smoke detection system shall be installed throughout high-piled combustible storage areas where required by the Florida Fire Prevention Code.

907.2.16 Aerosol storage uses.  Change to read as shown.

907.2.16 Aerosol storage uses.  Aerosol storage rooms and general-purpose warehouses containing aerosols shall be provided with an approved manual fire alarm system where required by the Florida Fire Prevention Code.

907.3.1 Duct smoke detectors.  Change to read as shown.

[F] 907.3.1 Duct smoke detectors. Smoke detectors installed in ducts shall be listed for the air velocity, temperature and humidity present in the duct. Duct smoke detectors shall be connected to the building’s fire alarm control unit when a fire alarm system is required by Section 907.2. Activation of a duct smoke detector shall initiate a visible and audible supervisory signal at a constantly attended location and shall perform the intended fire safety function in accordance with this code and the Florida Building Code, Mechanical. Duct smoke detectors shall not be used as a substitute for required open area detection.

Exceptions:

1. The supervisory signal at a constantly attended location is not required where duct smoke detectors activate the building’s alarm notification appliances.

2. In occupancies not required to be equipped with a fire alarm system, actuation of a smoke detector shall activate a visible and an audible signal in an approved location. Smoke detector trouble conditions shall activate a visible or audible signal in an approved location and shall be identified as air duct detector trouble.

907.6.1 Wiring.  Change to read as shown.

[F] 907.6.1 Wiring. Wiring shall comply with the requirements of Chapter 27 and NFPA 72. Wireless protection systems utilizing radio-frequency transmitting devices shall comply with the special requirements for supervision of low-power wireless systems in NFPA 72.

907.6.5 Monitoring.  Change to read as follows:

[F] 907.6.5 Monitoring. Fire alarm systems required by this chapter or by the International Fire Code  Florida Fire Prevention Code shall be monitored by an approved supervising station in accordance with NFPA 72.

Exception: No change.

907.8 Monitoring.  Change to read as follows:

[F] 907.8 Inspection, testing and maintenance. The maintenance and testing schedules and procedures for fire alarm and fire detection systems shall be in accordance with Florida Fire Prevention Code  Section 907.9 of the International Fire Code.

907.9 Accessibility.  Add to read as shown.

907.9 Accessibility.  Alarm systems required to be accessible by Section 11-4.1 shall comply with Section 11-4.28. applicable sections of the Florida Building Code, Accessibility .

[F4712]

Section 908 Emergency Alarm Systems

908.6 Refrigerant detector.  Change to read as shown.

- 908.6 Refrigerant detector.  Machinery rooms shall contain a refrigerant detector with an audible and visual alarm. The detector, or a sampling tube that draws air to the detector, shall be located in an area where refrigerant from a leak will concentrate. The alarm shall be actuated at a value not greater than the corresponding TLV-TWA values for the refrigerant classification indicated in the Florida Building Code, Mechanical. Detectors and alarms shall be placed in approved locations.

Section 909 Smoke Control Systems

909.1  Scope and purpose.  Change to read as shown.

909.1 Scope and purpose.  This section applies to mechanical or passive smoke control systems when they are required by other provisions of this code. The purpose of this section is to establish minimum requirements for the design, installation and acceptance testing of smoke control systems that are intended to provide a tenable environment for the evacuation or relocation of occupants. These provisions are not intended for the preservation of contents, the timely restoration of operations or for assistance in fire suppression or overhaul activities. Smoke control systems regulated by this section serve a different purpose than the smoke- and heat-venting provisions found in Section 910. Mechanical smoke control systems shall not be considered exhaust systems under Chapter 5 of the Florida Building Code, Mechanical.

909.3 Special inspection and test requirements.  Change to read as shown.

909.3 Special inspection and test requirements.  Reserved.

909.3 Special inspection and test requirements. In addition to the ordinary inspection and test requirements which buildings, structures and parts thereof are required to undergo, smoke control systems subject to the provisions of Section 909 shall undergo special inspections and tests sufficient to verify the proper commissioning of the smoke control design in its final installed condition. The design submission accompanying the construction documents shall clearly detail procedures and methods to be used and the items subject to such inspections and tests. Such commissioning shall be in accordance with generally accepted engineering practice and, where possible, based on published standards for the particular testing involved.

[3515]

Section 909.7 Airflow design method, revise text to read as follows:

909.7 Airflow design method When approved by the building official, smoke migration through openings fixed in a permanently open position, which are located between smoke control zones by the use of the airflow method, shall be permitted. The design airflow shall be in accordance with this section. Airflow shall be directed to limit smoke migration from the fire zone. The geometry of openings shall be considered to prevent flow reversal from turbulent effects.

Section 909.8 Exhaust method, revise text to read as follows:

909.8 Exhaust method. When approved by the building official, mechanical smoke control for large enclosed volumes, such as in atriums or malls, shall be permitted to utilize the exhaust method. Smoke control systems using the exhaust method shall be designed in accordance with NFPA 92B.

No change to the remaining text.

Section 909.9 Design fire, revise text to read as follows:

909.9 Design fire. The design fire shall be based on a rational analysis performed by the registered design professional and approved by the building official. The design fire shall be based on the analysis in accordance with Section 909.4 and this section.

No change to the remaining text.

Section 909.10 Equipment, revise text to read as follows:

909.10 Equipment. Equipment including, but not limited to, fans, ducts, automatic dampers and balance dampers, shall be suitable for its intended use, suitable for the probable exposure temperatures that the rational analysis indicates and as approved by the building official.

No change to the remaining text.

909.10.2 Ducts.  Change to read as shown.

- 909.10.2 Ducts.  Duct materials and joints shall be capable of withstanding the probable temperatures and pressures to which they are exposed as determined in accordance with Section 909.10.1. Ducts shall be constructed and supported in accordance with the Florida Building Code, Mechanical. Ducts shall be leak tested to 1.5 times the maximum design pressure in accordance with nationally accepted practices. Measured leakage shall not exceed 5 percent of design flow. Results of such testing shall be a part of the documentation procedure. Ducts shall be supported directly from fire-resistance-rated structural elements of the building by substantial, noncombustible supports.

Exception: Flexible connections (for the purpose of vibration isolation) complying with the Florida Building Code, Mechanical that are constructed of approved fire-resistance-rated materials.

909.12.1 Wiring.  Change to read as shown.

909.12.1 Wiring.  In addition to meeting requirements of the Chapter 27 of the Florida Building Code, Building, all wiring, regardless of voltage, shall be fully enclosed within continuous raceways.

Section 909.15 Control diagrams, revise text to read as follows:

909.15 Control diagrams. Identical control diagrams showing all devices in the system and identifying their location and function shall be maintained current and kept on file with the building official, the fire department and in the fire command center in a format and manner approved by the fire chief.

Section 909.16 Fire-fighter’s smoke control panel.  Change to read as follows:

909.16 Fire-fighter’s smoke control panel. A fire-fighter’s smoke control panel for fire department emergency response purposes only shall be provided and shall include manual control or override of automatic control for mechanical smoke control systems. The panel shall be located in a fire command center complying with Section 911 in high-rise buildings or buildings with smoke protected assembly seating.  In other buildings, the fire-fighter’s smoke control panel shall be installed in an approved location adjacent to the fire alarm control panel.  The fire-fighter’s smoke control panel shall comply with Sections 909.16.1 through 909.16.3.

[Remaining text unchanged.]

909.16.3 Control action and priorities.  Change to read as shown.

- 909.16.3 Control action and priorities.  The fire-fighter’s control panel actions shall be as follows:

- 1.  No change.

- Exception: Power disconnects required by the Chapter 27 of the Florida Building Code, Building.

- No change.

Section 909.18.8.3.1 Report filing, revise text to read as follows:

909.18.8.3.1 Report filing. A copy of the final report shall be filed with the building official and an identical copy shall be maintained in an approved location at the building.

Section 909.19 System acceptance, revise text to read as follows:

909.19 System acceptance. Buildings, or portions thereof, required by this code to comply with this section shall not be issued a certificate of occupancy until such time that the building official determines that the provisions of this section have been fully complied with and that the fire department has received satisfactory instruction on the operation, both automatic

and manual, of the system.

Exception: In buildings of phased construction, a temporary certificate of occupancy, as approved by the building official, shall be allowed provided that those portions of the building to be occupied meet the requirements of this section and that the remainder does not pose a significant hazard to the safety of the proposed occupants or adjacent buildings.

Section 909.20 Smokeproof enclosures, revise text to read as follows:

909.20 Smokeproof enclosures. Where required by Section 1020.1.7, a smokeproof enclosure shall be constructed in accordance with this section. A smokeproof enclosure shall consist of an enclosed interior exit stairway that conforms to Section 1020.1 and an open exterior balcony or ventilated vestibule meeting the requirements of this section. Where access to the roof is required by the Florida Building Code, such access shall be from the smokeproof enclosure where a smokeproof enclosure is required.

No change to remaining text.

Section 909.20.5 Stair pressurization alternative.  Change to read as shown.

909.20.5 Stair pressurization alternative. Where the building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, the vestibule is not required, provided that interior exit stairways are pressurized to a minimum of 0.10 05 inch nches of water (12.3 Pa) and a maximum of 0.35 inches of water (87 Pa) in the shaft relative to the building measured with all stairway doors closed under maximum anticipated conditions of stack effect and wind effect.

[F4763]

Section 910 Smoke and Heat Vents

910.2.2 High-piled combustible storage.  Change to read as shown.

910.2.2 High-piled combustible storage.  Buildings and portions thereof containing high-piled combustible stock or rack storage in any occupancy group in accordance with Section 413 and the Florida Fire Prevention Code.

Section 912 Fire Department Connections

912.3.3 Physical protection.  Change to read as shown.

[F] 912.3.3 Physical protection. Where fire department connections are subject to impact by a motor vehicle, vehicle impact protection shall be provided in accordance with Section 312 of the Florida Fire Prevention Code.

912.5 Backflow protection.  Change to read as shown.

[P] 912.5 Backflow protection. The potable water supply to automatic sprinkler and standpipe systems shall be protected against backflow as required by the Florida Building Code, Plumbing.

SECTION 915 EMERGENCY RESPONDER RADIO COVERAGE

[F] 915.1 General. Emergency responder radio coverage shall be provided in all new buildings in accordance with the Florida Fire Prevention Code.

Section 916 Carbon Monoxide Protection, add text to read as follows:

916 Carbon monoxide protection

916.1 Carbon monoxide protection.  Every separate building or an addition to an existing building for which a permit for new construction is issued and having a fossil-fuel-burning heater or appliance, a fireplace, or an attached garage, or other feature, fixture, or element that emits carbon monoxide as a byproduct of combustion shall have an operational carbon monoxide alarm installed within 10 feet of each room used for sleeping purposes in the new building or addition, or at such other locations as required by this Code..

916.1.1 Carbon monoxide alarm Power Source. In new construction, alarms shall breceive their primary power from the building wiring when such wiring is served from the local power utility. Such alarms shall have battery back up.  The requirements of Section 916.1 shall be satisfied by providing for one of the following alarm installation:

(1) A hard-wired carbon monoxide alarm.

(2) A battery-powered carbon monoxide alarm.

(3) A hard-wired combination carbon monoxide and smoke alarm.

(4) A battery-powered combination carbon monoxide and smoke alarm.

916.1.2 Combination alarms. Combination smoke/carbon monoxide alarms shall be listed and or labeled by a Nationally Recognized Testing Laboratory.

Exceptions:

(1)   An approved operational carbon monoxide detector shall be installed inside or directly outside of each room or area within a hospital, inpatient hospice facility or nursing home facility licensed by the Agency for Health Care Administration, or a new state correctional institution where a fossil-fuel burning heater, engine, or appliance is located. The carbon monoxide detector shall be connected to the fire-alarm system of the hospital, inpatient hospice facility, or nursing home facility as a supervisory signal.

(2)   This section shall not apply to existing buildings that are undergoing alterations or repair unless the alteration is an addition as defined in Section 916.1.3.

916.1.3 Addition shall mean an extension or increase in floor area, number of stories or height of a building or structure. [3853]

Chapter 10, Means of Egress

Section 1001 Administration

1001.3 Maintenance. Means of egress shall be maintained in accordance with the Florida Fire Prevention Code.

1001.4 Alterations.  Add to read as shown.

1001.4 Alterations. A building shall not hereafter be altered to reduce the capacity of the means of egress to less than required by this chapter nor shall any change of occupancy be made in any building unless such building conforms with the requirements of this chapter.

Exception: Existing stairs shall be permitted to remain in use provided they comply with the requirements of the building code in effect at the time of original construction.

Section 1001.5, add text to read as follows:

1001.5 Where approved by the building official, existing stairs shall be permitted to be rebuilt in accordance with the dimensional criteria of the building code in effect at the time of original construction provided:

- Handrails comply with Section 1012, and,

- Guardrails comply with Section 1013, and,

- The elevation of the floor surfaces on both sides of the door complies with Section 1008.1.5

Section 1001.6 Special egress requirements by occupancy, add text to read as follows:

1001.6 Special egress requirements by occupancy. The general requirements of Chapter 10 apply to all occupancies except as modified for specific occupancies in accordance with Section 1028 and Sections 1030 through 1037.

Section 1002 Definitions

1002 Definitions.  Add to read as shown.

CIRCULAR STAIRS. A stairway with steps that result in a sweeping circular or curved pattern, but not spiral stairs.

1002 Definitions.  Change to read as shown.

EXIT DISCHARGE, LEVEL OF. The lowest level having at least 50 percent of the number of exits and capacity of exits discharging to the exterior at grade or story with the least change in elevation to grade, provided no other story has 50 percent of its exits or egress capacity discharging to the exterior at the grade.

1002 Definitions.  Add to read as shown.

Means of escape. As used in Section 1008.1.3.6, A way out of a building or structure that does not conform to the strict definition of means of egress but does provide an alternate way out. A means of escape consists of a door, stairway, passage or hall providing a way of unobstructed travel to the outside at street or ground level. that is independent of and remotely located from the means of egress. It may also consist of a passage through an adjacent nonlockable space, independent of and remotely located from the means of egress, to any approved exit. [4354]

1002.1 Definitions, revise text to read as follows:

MERCHANDISE PAD. A merchandise pad is an area for display of merchandise surrounded by aisles, permanent fixtures or walls. Merchandise pads contain elements such as non-fixed and moveable fixtures, cases, racks, counters and partitions as indicated in Section 105.2 from which customers browse or shop.

Section 1003 General Means of Egress

1003.3.3 Horizontal projections.  Change to read as shown.

1003.3.3 Horizontal projections. Elements cannot project over a walking surface more than 4 inches (102 mm) when they are located between 27 and 80 inches (686 and 2032 mm) above the floor. Handrails can project up to 4½ inches (114 mm) from the wall.

1003.3.3 Horizontal projections. Structural elements, fixtures or furnishings shall not project horizontally from either side more than 4 inches (102 mm) over any walking surface between the heights of 27 inches (686 mm) and 80 inches (2032 mm) above the walking surface.

Exception: Handrails are permitted to protrude 41/2 inches (114 mm) from the wall.

[3967]

1003.3.4 Clear width.  Change to read as shown.

1003.3.4 Clear width. For accessibility provisions related to protruding objects, refer to Section 11-4.4 as provided in Section 1003.3.

1003.3.4 Clear width. Protruding objects shall not reduce the minimum clear width of accessible routes.[3967]

1003.4 Floor surface.  Change to read as shown.

1003.4 Floor surface. Walking surfaces shall be slip resistant under foreseeable conditions.  The walking surface of each element in the means of egress shall be uniformly slip resistant along the natural path of travel.

1003.4 Floor surface.Walking surfaces of the means of egress shall have a slip-resistant surface and be securely attached. [3967, 3965]

1003.5 Elevation change.  Change to read as shown.

1003.5 Elevation change. Change in level in the means of egress shall be either by a ramp or a stair. The presence and location of ramped walkways shall be readily apparent.

1003.5 Elevation change. Where changes in elevation of less than 12 inches (305 mm) exist in the means of egress, sloped surfaces shall be used. Where the slope is greater than one unit vertical in 20 units horizontal (5-percent slope), ramps complying with Section 1010 shall be used. Where the difference in elevation is 6 inches (152 mm) or less, the ramp shall be equipped with either handrails or floor finish materials that contrast with adjacent floor finish materials.

Exceptions:

1. A single step with a maximum riser height of 7 inches (178 mm) is permitted for buildings with occupancies in Groups F, H, R-2, R-3, S and U at exterior doors not required to be accessible by Chapter 11.

2. A stair with a single riser or with two risers and a tread is permitted at locations not required to be accessible by Chapter 11, provided that the risers and treads comply with Section 1009.4, the minimum depth of the tread is 13 inches (330 mm) and at least one handrail complying with Section 1012 is provided within 30 inches (762 mm) of the centerline of the normal path of egress travel on the stair.

3. A step is permitted in aisles serving seating that has a difference in elevation less than 12 inches (305 mm) at locations not required to be accessible by Chapter 11, provided that the risers and treads comply with Section 1028.11 and the aisle is provided with a handrail complying with Section 1028.13.

Throughout a story in a Group I-2 occupancy, any change in elevation in portions of the exit access that serve nonambulatory persons shall be by means of a ramp or sloped walkway.

[3967,3966 ]

1003.5.1 Accessibility.  Add to read as shown.

1003.5.1 Accessibility. For accessibility provisions related to changes in levels, see Section 11-4.3.8. . the Florida Building Code, Accessibility.

[F4713]

Section 1004 Occupant Load

1004.1 Design occupant load.  Change to read as shown.

1004.1 Design occupant load.  In determining means of egress requirements, the number of occupants for whom means of egress facilities shall be provided shall be determined in accordance with this section. Where occupants from accessory areas egress through a primary space, the calculated occupant load for the primary space shall include the total occupant load of the primary space plus the number of occupants egressing through it from the accessory area.

Exceptions:

1.	In a special purpose factory-industrial occupancy, the occupant load shall be the maximum number of persons to occupy the area under any probable conditions.

2.	The occupant load for towers shall be the number of persons expected to occupy the space, with spaces not subject to human occupancy because of machinery or equipment excluded from the gross area calculation.

Table 1004.1.1 Maximum Floor Area Allowances per Occupant.  Change to read as shown.

TABLE 1004.1.1

MAXIMUM FLOOR AREA ALLOWANCES PER OCCUPANT

|  | FLOOR AREA IN SQ. |
| --- | --- |
| FUNCTION OF SPACE | FT. PER OCCUPANT |
| Accessory storage areas, mechanical equipment room | 300 gross |
| Agricultural building | 300 gross |
| Aircraft hangars | 500 gross |
| Airport terminal |  |
| Baggage claim | 20 gross |
| Baggage handling | 300 gross |
| Concourse | 100 gross |
| Waiting areas | 15 gross |
| Assembly |  |
| Gaming floors (keno, slots, etc.) | 11 gross |
| Assembly with fixed seats | See Section 1004.7 |
| Assembly without fixed seats |  |
| Concentrated (chairs only—not fixed) | 7 net |
| Standing space | 5 net |
| Unconcentrated (tables and chairs) | 15 net |
| Bowling centers, allow 5 persons for each |  |
| lane including 15 feet of runway, and for |  |
| additional areas | 7 net |
| Business areas | 100 gross |
| Courtrooms—other than fixed seating areas | 40 net |
| Day care | 20 net |
| Dormitories | 50 gross |
| Educational |  |
| Classroom area | 20 net |
| Shops and other vocational room areas | 50 net |
| Exercise rooms | 50 gross |
| Exercise rooms with equipment | 50 gross |
| Exercise rooms without equipment | 15 gross |
| H-5 Fabrication and manufacturing areas | 200 gross |
| Industrial areas | 100 gross |
| Institutional areas |  |
| Inpatient treatment areas | 240 gross |
| Outpatient areas | 100 gross |
| Sleeping areas | 120 gross |
| Kitchens, commercial | 200 gross |
| Library |  |
| Reading rooms | 50 net |
| Stack area | 100 gross |
| Locker rooms | 50 gross |
| Mercantile |  |
| Areas on other floors | 60 gross |
| Basement and grade floor areas | 30 gross |
| Multiple street floors – each (Note 1) | 40 gross |
| Storage, stock, shipping areas | 300 gross |
| Parking garages | 200 gross |
| Residential | 200 gross |
| Skating rinks, swimming pools |  |
| Rink and pool | 50 gross |
| Swimming pool deck | 30 gross |
| Swimming pool water surface | 50 gross |
| Decks | 15 gross |
| Stages and platforms | 15 net |
| Warehouses | 500 gross |

For SI: 1 square foot = 0.0929 m2.

1. For the purpose of determining occupant load in mercantile occupancies where, due to differences in grade of streets on different sides, two or more floors directly accessible from streets exist, each such floor shall be considered a street floor.  The occupant load factor shall be one person for each 40 square feet (3.7 m2) of gross floor area of sales space.

2.  For any food court or other assembly use areas located in the mall that are not included as a portion of the gross leasable area of the mall buildings, the occupant load is calculated based on the occupant load factor for that use as specified in Table 1004.1.2. The remaining mall area is not required to be assigned an occupant load.

Section 1006 Means of Egress Illumination

1006.1 Means of egress illumination.  Change to read as shown.

1006.1 Means of egress illumination.

1006.1.1  Add to read as shown.

1006.1.1 Illumination of means of egress shall be provided in accordance with this section for every building and structure. For the purposes of this requirement, exit access shall include only designated stairs, aisles, corridors, ramps, escalators and passageways leading to an exit. For the purposes of this requirement, exit discharge shall include only designated stairs, aisles, corridors, ramps, escalators, walkways and exit passageways leading to a public way.

Exceptions:

- When approved by the building official, illumination of means of egress shall not be required in industrial and storage occupancies that are occupied only during daylight hours, with skylights or windows arranged to provide the required level of illumination on all portions of the means of egress during these hours.

2.	Assembly occupancy private party tents of 1,200 square feet (111 m2) or less shall not be required to provide illumination of means of egress.

3.	Open structures shall not be required to provide illumination of means of egress.

4.	Towers occupied by not more than three persons shall not be required to provide illumination of means of egress.

1006.1.2  Add to read as shown.

1006.1.2 Illumination of means of egress shall be continuous during the time that the conditions of occupancy require that the means of egress be available for use. Artificial lighting shall be employed at such places and for such periods of time as required to maintain the illumination to the minimum criteria values herein specified.

Exceptions: Automatic motion sensor-type lighting switches shall be permitted within the means of egress, provided that switch controllers are equipped for fail-safe operation, illumination timers are set for a minimum 15-minute duration and the motion sensor is activated by any occupant movement in the area served by the lighting units.

1006.1.3  Add to read as shown.

1006.1.3 The floors and other walking surfaces within an exit and within the portions of the exit access and exit discharge designated in Section 1006.1.1 shall be illuminated to values of at least 1 footcandle (10 lux) measured at the floor. During conditions of stair use, the minimum illumination for new stairs shall be at least 108 lux (10 foot-candle), measured at the walking surface.

Exception: In assembly occupancies, the illumination of the floors of exit access shall be at least 0.2 footcandle (2 lux) during periods of performances or

1006.1.4  Add to read as shown.

1006.1.4 Required illumination shall be arranged so that the failure of any single lighting unit will not result in an illumination level in any designated area of less than 0.2 footcandle (2 lux).

1006.1.5  Add to read as shown.

1006.1.5 The equipment or units installed to meet the requirements of Section 1006.3 shall be permitted also to serve the function of illumination of means of egress, provided that all requirements of Section 1006.1 for such illumination are met.

1006.1.6  Add to read as shown.

1006.1.6 Sources of illumination.

1006.1.6.1  Add to read as shown.

1006.1.6.1 Illumination of means of egress shall be from a source of reasonably ensured reliability.

1006.1.6.2  Add to read as shown.

1006.1.6.2 Battery-operated electric lights and other types of portable lamps or lanterns shall not be used for primary illumination of means of egress. Battery-operated electric lights shall be permitted to be used as an emergency source to the extent permitted under Section 1006.2.3.4.

1006.2 Emergency lighting and standby power.  Change to read as shown.

1006.2 Emergency lighting and standby power.

1006.2.1  Add to read as shown.

1006.2.1 Emergency lighting facilities for means of egress shall be provided in accordance with this section for the following:

1.	Every building or structure where required in Table 1006.

2.	Windowless and underground structures.

Exception: One- and two-family dwellings.

3.	High-rise structures.

4.	At doors equipped with delayed egress locks.

5.	The stair shaft and vestibule of smokeproof enclosures. A standby generator that is installed for the smokeproof enclosure mechanical ventilation equipment shall be permitted to be used for such stair shaft and vestibule power supply.

For the purposes of this requirement, exit access shall include only designated stairs, aisles, corridors, ramps, escalators and passageways leading to an exit.  For the purposes of this requirement, exit discharge shall include only designated stairs, ramps, aisles, walkways and escalators leading to a public way.

Exceptions:

1.	Towers occupied by three or fewer persons shall be exempt from emergency lighting requirements.

2.	Locations in towers not routinely inhabited by humans shall be exempt from emergency lighting requirements.3.	When approved by the building official, illumination of means of egress shall not be required in towers that are occupied only during daylight hours, with windows arranged to provide the required level of illumination on all portions of the means of egress during these hours.

4.	Water-surrounded structures in locations not routinely inhabited by humans shall be exempt from emergency lighting requirements.

5.	When approved by the building official, illumination of means of egress shall not be required in water-surrounded structures that are occupied only during daylight hours, with windows arranged to provide the required level of illumination on all portions of the means of egress during these hours.

1006.2.2  Add to read as shown.

1006.2.2 Where maintenance of illumination depends upon changing from one energy source to another, a delay of not more than 10 seconds shall be permitted.

1006.2.3  Add to read as shown.

1006.2.3 Performance of system.

1006.2.3.1  Add to read as shown.

1006.2.3.1 Emergency illumination shall be provided for a period of hours 1½ in the event of failure of normal lighting. Emergency lighting facilities shall be arranged to provide initial illumination that is at least an average of 1 footcandle (10 lux) and a minimum at any point of 0.1 footcandle (1 lux) measured along the path of egress at floor level. Illumination levels shall be permitted to decline to 0.6 footcandle (6 lux) average and a minimum at any point of 0.06 footcandle (0.6 lux) at the end of the emergency lighting time duration. A maximum-to-minimum illumination uniformity ratio of 40:1 shall not be exceeded.

1006.2.3.2  Add to read as shown.

1006.2.3.2 The emergency lighting system shall be arranged to provide the required illumination automatically in the event of any interruption of normal lighting, such as any failure of public utility or other outside electrical power supply; opening of a circuit breaker or fuse or any manual act(s), including accidental opening of a switch controlling normal lighting facilities.

1006.2.3.3  Add to read as shown.

1006.2.3.3 Emergency generators providing power to emergency lighting systems shall be installed in accordance with NFPA 110.  Stored electrical energy systems where required in this code shall be installed and tested in accordance with NFPA 111.

1006.2.3.4  Add to read as shown.

1006.2.3.4 Battery-operated emergency lights shall use only reliable types of rechargeable batteries provided with suitable facilities for maintaining them in a properly charged condition. Batteries used in such lights or units shall be approved for their intended use and shall comply with Chapter 27 of the Florida Building Code, Building.

1006.2.3.5  Add to read as shown.

1006.2.3.5 The emergency lighting system shall be either continuously in operation or shall be capable of repeated automatic operation without manual intervention.

1006.2.4  Add to read as shown.

1006.2.4 Standby power.  High-rise buildings shall be provided with Class 1, Type 60 standby power in accordance with Chapter 27 of the Florida Building Code, Building and NFPA 110.  The standby power system shall have a capacity and rating sufficient to supply all required equipment.  Selective load pickup and load shedding shall be permitted in   accordance with Chapter 27 of the Florida Building Code, Building.  The standby power system shall be connected to the following:

1.	Emergency lighting system.

2.	At least one elevator serving all floors and transferable to any elevator.

3.	Mechanical equipment for smokeproof enclosures.

(See Section 403 for additional requirements for standby power in high-rise structures.)

1006.3 Exit signs.  Change to read as shown.

1006.3 Exit signs.

1006.3.1  Add to read as shown.

1006.3.1 Exits shall be marked by an approved sign readily visible from any direction of exit access. Every exit sign shall be suitably illuminated by a reliable light source. Externally and internally illuminated signs shall be visible in both normal and emergency lighting.

Exception: Main exterior exit doors that obviously and clearly are identifiable as exits.

1006.3.2  Add to read as shown.

1006.3.2 New sign placement shall be such that no point in an exit access corridor is in excess of the rated viewing distance or 100 feet (30 m) whichever is less, from the nearest sign.

1006.3.3  Add to read as shown.

1006.3.3 Every required sign shall be located and of such size, distinctive color and design as to be readily visible and shall provide contrast with interior finish or other signs.  No equipment that impairs visibility of an exit sign shall be permitted, nor shall there be any brightly illuminated sign or object in or near the line of vision of the required exit sign of such a character as to detract attention from the exit sign.  Floor proximity signs, where required, shall be in accordance with Section 1006.3.8.2 or 1006.3.8.3.

1006.3.4  Add to read as shown.

1006.3.4 Exit stair door or tactile signage.

Tactile signage stating “EXIT” and complying with ICC/ANSI A117.1, American National Standard for Accessible and Usable Buildings and Facilities, shall be installed adjacent to the latch side of the door 60 inches (1524 mm) above the finished floor to the center line of the sign.

Section 1006.3.5, add text to read as follows:

1006.3.5 Externally illuminated signs shall have the word "EXIT" or other appropriate wording in plainly legible letters not less than 6 inches (15 2 mm) high with the principal strokes of letters not less than 3/4 inches (19 mm) wide. The word "EXIT" shall have letters of a width not less than 2 inches (51 mm), except the letter "I," and the minimum spacing between letters shall be not less than 3/8 inches (10 mm). Signs larger than the minimum established in this paragraph shall have letter widths, strokes and spacing in proportion to their height. Externally illuminated signs shall be illuminated by not less than 5 footcandles (50 lux) at the illuminated surface and shall have a contrast ratio of not less than 0.5.

Exceptions:

1.	Marking required by Section 1009.6.4.

2.	Group R-3 and Group R-4 (small facility) occupancies.

Section 1006.3.6, add text to read as follows:

1006.3.6 Internally illuminated signs shall be listed in accordance with UL 924, Standard for Safety Emergency Lighting Power Equipment. The visibility of an internally illuminated sign shall be the equivalent of an externally illuminated sign that complies with Section 1006.3.5.

Exceptions:

1.	Marking required by Section 1009.5.4.

2.	Signs in compliance with Sections 1006.3.4 and 1006.3.8.2.

1006.3.7  Add to read as shown.

1006.3.7 Where emergency lighting facilities are required by Section 1006.2, the exit signs shall be illuminated by the emergency lighting facilities. The level of illumination of the exit sign shall be at the levels provided in accordance with Section 1006.3.5 for the required emergency lighting time duration as specified in Section 1006.2.3.1, but shall be permitted to decline to 60 percent of the illumination level at the end of the emergency lighting time duration.

1006.3.8  Add to read as shown.

1006.3.8 Where the direction of travel to reach the nearest exit is not apparent, a directional sign complying with Sections 1006.3.5 or 1006.3.6 reading “EXIT,” or a similar designation with a directional indicator showing the direction of travel shall be placed in every location. Directional signs shall be listed.

1006.3.8.1  Add to read as shown.

1006.3.8.1 The directional indicator shall be located outside of the “EXIT” legend, not less than 3/8 inches (10 mm) from any letter.  The directional indicator shall be of a chevron type and shall be identifiable as a directional indicator at a minimum distance of 40 feet (12.2 m). A directional indicator larger than the minimum established in this section shall be proportionately increased in height, width and stroke. The directional indicators shall be located at the end of the sign for the direction indicated.

1006.3.8.2  Add to read as shown.

1006.3.8.2 Where floor proximity exit signs are required, exit signs shall be placed near the floor level in addition to those signs required for doors or corridors. These signs shall be illuminated in accordance with Section 1006.3. Externally illuminated signs shall be sized in accordance with Section 1006.3.5. The bottom of the sign shall be at least 6 inches (152 mm) and no more than 8 inches (203 mm) above the floor. For exit doors, the sign shall be mounted on the door or adjacent to the door with the nearest edge of the sign within 4 inches (102 mm) of the door frame.

1006.3.8.3  Add to read as shown.

1006.3.8.3 Where floor proximity egress path marking is required, a listed and approved floor proximity egress path marking system that is internally illuminated shall be installed within 18 inches (457 mm) of the floor. The system shall provide a visible delineation of the path of travel along the designated exit access and shall be essentially continuous, except as interrupted by doorways, hallways, corridors or other such architectural features. The system shall operate continuously or at any time the building fire alarm system is activated. The activation, duration and continuity of operation of the system shall be in accordance with Section 1006.2.

1006.3.9  Add to read as shown.

1006.3.9 Signs installed as projections from a wall or ceiling within the means of egress shall provide vertical clearance no less than 80 inches (2134 mm) from the walking surface.

1006.4 Performance of system.  Change to read as shown.

1006.4  Performance of system.  Reserved.

Table 1006 Emergency Lighting Requirements.  Add to read as shown.

TABLE 1006

EMERGENCY LIGHTING REQUIREMENTS

| OCCUPANCY | CONDITIONS | EXCEPTIONS |
| --- | --- | --- |
| Assembly |  | Private party tents < 1200 sq ft |
| Educational | For interior stairs and corridors, normally occupied spaces, flexible and open-plan area, interior or windowless portions, shops and labs | Exempted from administrative areas, general classrooms, mechanical rooms and storage rooms |
| Group I-1 and I-2 | If using life-support systems, supply the required power from life safety branch of electricals as required by NFPA 99 | None |
| Outpatient clinics, ambulatory | If using life-support systems for other than emergency purposes, supply the required power essentials electrical system as required by NFPA 99 | None |
| Group I-3 | None | None |
| Hotels and dormitories | > 25 rooms | All rooms direct to grade |
| Apartment buildings | > 12 units or >3 stories | All apartments direct to grade |
| Group R-4, large facilities | > 25 rooms | All rooms direct to grade |
| Mercantile | > 1 story > 3000 sq ft gross sales area and malls | None |
| Business | > 2 stories above LED, or ≥ 50 people above or below LED, or ≥ 300 people total | None |
| Industrial | None | When approved by the building official, special purpose without routine occupancy or daylight operations with windows |
| Storage | None | When approved by the building official, not normally occupied or daylight operations with windows |
| Day care centers | For interior stairs and corridors, normally occupied spaces, flexible and open-plan area, interior or windowless portions, shops and labs | Exempted from administrative areas, general classrooms, mechanical rooms and storage rooms |

Section 1007 Accessible Means of Egress

1007.1 Accessible means of egress.  Change to read as shown.

1007.1 Accessible means of egress.  Accessible means of egress shall be provided in accordance with Sections 11-4.1.3(8), 11-4.1.3(9) and 11-4.3.10. with the applicable sections of the Florida Building Code, Accessibility.

[F4714]

1007.2 Continuity and components.  Change to read as shown.

1007.2 Continuity and components.  Reserved.

1007.3 Stairways.  Change to read as shown.

1007.3 Stairways.  Reserved.

1007.4 Elevators.  Change to read as shown.

1007.4 Elevators.  Reserved.

1007.5 Platform lifts.  Change to read as shown.

1007.5 Platform lifts.  Reserved.

1007.6 Areas of refuge.  Change to read as shown.

1007.6 Areas of refuge.  Reserved.

1007.7Exterior area for assisted rescue.  Change to read as shown.

1007.7Exterior area for assisted rescue.  Reserved.

1007.8 Two-way communication.  Change to read as shown.

1007.8 Two-way communication. Reserved.

1007.9Signage.  Change to read as shown.

1007. 9 Signage.  Reserved.

1007.10 Directional signage.  Change to read as shown.

1007.10 Directional signage. Reserved.

1007.11 Instructions.  Change to read as shown.

1007.11 Instructions.  Reserved.

Section 1008 Doors, Gates and Turnstiles

1008.1 Doors.  Change to read as shown.

1008.1 Doors. Means of egress doors shall meet the requirements of this section. Doors serving a means of egress system shall meet the requirements of this section and Section 1017.2 1020.2. Doors provided for egress purposes in numbers greater than required by this code shall meet the requirements of this section. For accessibility provisions related to doors, refer to Sections 11-4.1.3, 11-4.3.9 and 11-4.13. the Florida Building Code, Accessibility.

[F4715]

Means of egress doors shall be readily distinguishable from the adjacent construction and finishes such that the doors are easily recognizable as doors. Mirrors or similar reflecting materials shall not be used on means of egress doors. Means of egress doors shall not be concealed by curtains, drapes, decorations or similar materials. [3970]

Section 1008.1.1 Size of doors, revise text to read as follows:

1008.1.1 Size of doors.  Revise to reserve exception 7 and 8.

Exceptions:

1 – 6 No change.

7.  Reserved.  In other than Group R-1 occupancies, the minimum widths shall not apply to interior egress doors within a dwelling unit or sleeping unit that is not required to be an Accessible unit, Type A unit or Type B unit.[3968]

8.  Reserved.  Buildings that are 400 square feet or less and that are intended for use in conjunction with one‐ and two‐family residences are not subject to the door height and width requirements of this code.

Comment after Glitch

1008.1.4.1 Revolving doors.  Change to read as shown.

1008.1.4.1 Revolving doors. Revolving doors shall comply with the following:

1- 3 No change.

4.	Each revolving door shall have a side-hinged swinging door which complies with Section 1008.1 in the same wall and within 10 feet (3048 mm) of the revolving door, unless one of the following conditions applies:

a.	Revolving doors shall be permitted without adjacent swinging doors, as required by Section 1008.1.4.1(4) in street floor elevator lobbies, provided that no stairways or doors from other parts of the building discharge through the lobby and the lobby has no occupancy other than as means of travel between the elevators and street.

b.	The requirement of Section 1008.1.4.1(4) shall not apply to existing revolving doors where the number of revolving doors does not exceed the number of swinging doors within 240 inches (6100 mm) of the revolving doors.

5. Reserved.

1008.1.4.2 Power-operated doors.  Change to read as shown.

1008.1.4.2 Power-operated doors. Where means of egress doors are operated by power, such as doors with a photoelectric-actuated mechanism to open the door upon the approach of a person, or doors with power-assisted manual operation, the design shall be such that in the event of power failure, the door is capable of being opened manually to permit means of egress travel or closed where necessary to safeguard means of egress.

The forces required to open these doors manually shall not exceed those specified in Section 1008.1.3, except that the force to set the door in motion shall not exceed 50 pounds (220 N). The door shall be capable of swinging from any position to the full width of the opening in which such door is installed when a force is applied to the door on the side from which egress is made. Full-power-operated doors shall comply with BHMA A156.10. Power-assisted and low-energy doors shall comply with BHMA A156.19. On the egress side of each door, there shall be a readily visible, durable sign that reads: “IN EMERGENCY PUSH TO OPEN.”

The sign shall be in letters not less than 1 inch (25 mm) high on a contrasting background.

Exceptions:

1.	Occupancies in Group I-3.

2.	Horizontal sliding doors complying with Section 1008.1.4.3..

3. 	Sliding, power-operated doors in exit access serving an occupant load of fewer than 50 that manually opens in the direction of door travel with forces not more than required in Section 1008 shall not be required to have a swing-out feature. The required sign shall state, “IN EMERGENCY, SLIDE TO OPEN.”

4.	In the emergency breakout mode, a door leaf located within a two-leaf opening shall be exempt from the minimum 32 inches (813 mm) single-leaf requirement, provided the clear width of the single leaf is at least 30 inches (762 mm).

5.	For a biparting door in the emergency breakout mode, a door leaf located within a multiple-leaf opening shall be exempt from the minimum 32-inch (813 mm) single-leaf requirement of Section 1008.1.1, provided a minimum 32-inch (813 mm) clear opening is provided when the two biparting leaves meeting in the center are broken out.

1008.1. 4.3 Horizontal sliding doors.  Change to read as shown.

1008.1. 4.3 Horizontal sliding doors. In other than Group H occupancies, horizontal sliding doors permitted to be a component of a means of egress in accordance with Exception 6 to Section 1008.1.2 shall comply with all of the following criteria:

1 – 8 No change.

9.	In apartment buildings, hotels and dormitories, horizontal sliding doors shall not be used across corridors.

1008.1. 4.4 Access-controlled egress doors.  Change to read as shown.

1008.1.4.4 Access-controlled egress doors. The entrance doors in a means of egress in buildings with an occupancy in Group A, B, D, E, I-2, M, R-1 or R-2 and entrance doors to tenant spaces in occupancies in Groups A, B, D, E, I-2, M, R-1 and R-2 are permitted to be equipped with an approved entrance and egress access control system which shall be installed in accordance with all of the following criteria:

[No change to remaining text]

1008.1. 4.5 Security grilles.  Change to read as shown.

1008.1. 4.5 Security grilles. In Groups B, F, M, R and S, horizontal sliding or vertical security grilles are permitted at the main exit and shall be openable from the inside without the use of a key or special knowledge or effort during periods that the space is occupied. The grilles shall remain secured in the full-open position during the period of occupancy by the general public. Where two or more means of egress are required, not more than one-half of the exits or exit access doorways shall be equipped with horizontal sliding or vertical security grilles.

1008.1. 4.6  Add to read as shown.

1008.1.4.6 The temporary installation or closure of storm shutters, panels and other approved hurricane protection devices shall be permitted on emergency escape and rescue openings in Group R occupancies during the threat of a storm. Such devices shall not be required to comply with the operational constraints of Section 1029.4. While such protection is provided, at least one means of escape from the dwelling or dwelling unit shall be provided.  The means of escape shall be within the first floor of the dwelling or dwelling unit and shall not be located within a garage without a side hinged door leading directly to the exterior.  Occupants in any part of the dwelling or dwelling unit shall be able to access the means of escape without passing through a lockable door not under their control.

1008.1. 4.7  Add to read as shown.

1008.1.4.7 Self-closing doors. Where doors are required to be self-closing and are operated by power upon the approach of a person or are provided with power-assisted manual operation, they shall be permitted in the means of egress in accordance with the following:

1.	Doors can be opened manually in accordance with Section 1008.1.4.2 to allow egress travel in the event of power failure.

2.	The doors remain in the closed position unless actuated or opened manually.

3.	When actuated, doors remain open for not more than 30 seconds.

4.	Doors held open for any period of time close and the power-assist mechanism ceases to function upon operation of approved smoke detectors installed in such a way as to detect smoke on either side of the door opening in accordance with the provisions of NFPA 72, National Fire Alarm Code.

5.	Doors required to be self-latching are either self-latching or become self-latching upon operation of approved smoke detectors in accordance with Section 1008.1.4.7(4).

6.   Power assisted swinging doors shall comply with ANSI/BHMA A156.19.

Section 1008.1.5  Floor elevation.  Change to read as shown.

1008.1. 5 Floor elevation. There shall be a floor or landing on each side of a door. Such floor or landing shall be at the same elevation on each side of the door. Landings shall be level except for exterior landings, which are permitted to have a slope not to exceed 1 unit vertical in 50 units horizontal (2-percent slope).

Exceptions:  No change to text.

1008.1.7 Thresholds.  Change to read as shown.

1008.1.7 Thresholds.   Thresholds at doorways shall not exceed 0.75 inch (19.1 mm) in height for sliding doors serving dwelling units or 0.5 inch (12.7 mm) for other doors. Raised thresholds and floor level changes greater than 0.25 inch (6.4 mm) at doorways shall be beveled with a slope not greater than one unit vertical in two units horizontal (50-percent slope).

Exceptions:

1.	The threshold height shall be limited to 7¾ inches (197 mm) where the occupancy is Group R-2, the door is an exterior door that is not a component of the required means of egress and the doorway is not on an accessible route. In one- and two-family dwellings where the door discharges to the outside or to an exterior balcony or exterior exit access, the floor level outside the door shall be permitted to be one step lower than the inside, but not more than 8 inches (203 mm) lower.

2.	For exterior doors serving dwelling units, thresholds at doorways shall not exceed the height required to pass the water resistance test of ANSI/AAMA/WDMA 101/I.S.2, or TAS 202 for high-velocity hurricane zones, or the maximum allowable height difference between interior floor level. Exterior floor level shall comply with the following:

[table]

1008.1.9.2 Hardware height.  Change to read as shown.

1008.1.9.2 Hardware height.  A latch or other fastening device on a door shall be provided with a releasing device having an obvious method of operation under all lighting conditions. The releasing mechanism for any latch shall be located at least 34 inches (864 mm) and not more than 48 inches  (1219 mm) above the finished floor. Doors shall be openable with not more than one releasing operation.

Exception: Egress doors from individual living units and guest rooms of residential occupancies shall be permitted to be provided with devices that require not more than one additional releasing operation if such device is operable from the inside without the use of a key or tool and is mounted at a height not more than 48 inches (1219 mm) above the finished floor.

1008.1. 9.4 Bolt locks.  Change to read as shown.

1008.1. 9.4 Bolt locks.  Manually operated flush bolts or surface bolts are not permitted.  All hardware must be direct acting requiring no more than one operation. Double cylinder dead bolts, requiring a key for operation on both sides, are prohibited on required means of egress doors unless the locking device is provided with a key which cannot be removed when the door is locked from the inside. Only one locking or latching device shall be permitted on a door or on one leaf of a pair of doors.

Exceptions: No change.

1008.1.9.6 Special locking arrangements in Group I-2. Change to read as shown.

1008.1.9.6 Special locking arrangements in Group I-2. Approved delayed egress locks shall be permitted in a Group I-2 occupancy where the clinical needs of persons receiving care require such locking. Delayed egress locks shall be permitted in such occupancies where the building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or an approved automatic smoke or heat detection system installed in accordance with Section 907, provided that the doors unlock in accordance with Items 1 through 6 below. A building occupant shall not be required to pass through more than one door equipped with a delayed egress lock before entering an exit.

1. The doors unlock upon actuation of the automatic sprinkler system or automatic fire detection system.

2. The doors unlock upon loss of power controlling the lock or lock mechanism.

3. The door locks shall have the capability of being unlocked by a signal from the fire command center, a nursing station or other approved location.

4. The procedures for the operation(s) of the unlocking system shall be described and approved as part of the emergency planning and preparedness required by Chapter 4 of the International Florida Fire Prevention Code.

5. All clinical staff shall have the keys, codes or other means necessary to operate the locking devices.

6. Emergency lighting shall be provided at the door.

Exception: Items 1 through 3 shall not apply to doors to areas where persons, because of clinical needs, require restraint or containment as part of the function of a mental hospital.

1008.1.9.11  Add to read as shown.

1008.1.9.11  During its swing, any door in a means of egress shall leave unobstructed at least one half of the required width of an aisle, corridor, passageway, or landing, nor project more than 7 inches (178 mm) into the required width of an aisle, corridor, passageway or landing, when fully open. Doors shall not open immediately onto a stair without a landing. The landing shall have a width at least equal to the width of the door. See Section 1031 for door swing in Group E occupancies.

Every door in a stair enclosure serving more than four stories shall permit reentry from the stair enclosure to the interior of the building, or an automatic release shall be provided to unlock all stair enclosure doors to permit reentry.  Such automatic release shall be actuated with the initiation of the building fire alarm, fire detection or fire sprinkler system.

Exception: Doors on stair enclosures shall be permitted to be equipped with hardware that prevents reentry into the interior of the building, provided that the following conditions are met:

1.	There are at least two levels where it is possible to leave the stair enclosure;

2.	There are not more than four stories intervening between stories where it is possible to leave the stair enclosure;

3.	Reentry is possible on the top or next to top story permitting access to another exit;

4. 	Doors permitting reentry are identified as such on the stair side of the door; and

5. 	Doors not permitting reentry shall be provided with a sign on the stair side indicating the location of the nearest door, in each direction of travel, permitting reentry or exit.

1008.1.10  Panic and fire exist hardware, Exception 2,  to read as follows:

Exception:

1. A main exit of a Group A occupancy in compliance with Section 1008.1.9.3, Item 2.

2. Outdoor gates from residential and commercial swimming pools or swimming pool decks, except where the pool deck is accessible to and useable by the occupants of a building and serves as a portion of the means of egress of a building with or has an occupant load of 300 or greater. [4256]

Remaining text unchaged.

Section 1009 Stairways

1009.4.2 Riser height and tread depth.  Change to read as shown.

1009.4.2 Riser height and tread depth.  Change exceptions as follows:

Exceptions:

1 – 4 No change.

5. In occupancies in Group R-3, as applicable in Section 101.2, within dwelling units in occupancies in Group R-2, as applicable in Section 101.2, and in occupancies in Group U, which are accessory to an occupancy in Group R-3, as applicable in Section 101.2, the maximum riser height shall be 7.75 inches (197 mm) and the minimum tread depth, exclusive of nosing, shall be not less than 9 inches (229 mm), the minimum winder tread depth at the walk line shall be 10 inches (254 mm), and the minimum winder tread depth shall be 6 inches (152 mm). Treads and risers of stairs shall be permitted to be so proportioned that the sum of two risers and a tread, exclusive of projection of nosing, is not less than 24 inches (610 mm) nor more than 25 inches (635 mm). Every tread less than 10 inches (254 mm) wide shall have a nosing, or effective projection, of approximately 1 inch (25 mm) over the level immediately below that tread.

5. In Group R-3 occupancies; within dwelling units in Group R-2 occupancies; and in Group U occupancies that are accessory to a Group R-3 occupancy or accessory to individual dwelling units in Group R-2 occupancies; the maximum riser height shall be 73/4 inches (197 mm); the minimum tread depth shall be 10 inches (254 mm); the minimum winder tread depth at the walk line shall be 10 inches (254 mm); and the minimum winder tread depth shall be 6 inches (152 mm).   A nosing not less than 3/4 inch (19.1 mm) but not more than 11/4 inches (32 mm) shall be provided on stairways with solid risers where the tread depth is less than 11 inches (279 mm). [3971]

6. See the Florida Building Code, Existing Building for the replacement of existing stairways.

7.  No change.

8. Industrial equipment access stairs and landings that serve as a component of the means of egress from the involved equipment and do not serve more than 20 people shall be permitted to have a minimum clear width of 22 inches (559 mm), minimum tread depth of 10 inches (254 mm), maximum riser height of 9 inches (229 mm), minimum headroom of 6 feet 8 inches (2032 mm), and a maximum height between landings of 12 feet (36 576 mm).

Section 1009.4.4 Dimensional uniformity.  Change Exceptions as follows:

Exceptions:

1. No change.

2. No change.

Where the bottom or top riser adjoins a sloping public way, walkway or driveway having an established grade and serving as a landing, the bottom or top riser is permitted to be reduced along the slope to less than 4 inches (102 mm) in height, with the variation in height of the bottom or top riser not to exceed one unit vertical in 12 units horizontal (8.333. -percent slope) of stairway width. The nosings or leading edges of treads at such nonuniform height risers shall have a distinctive marking stripe, different from any other nosing marking provided on the stair flight. The distinctive marking stripe shall be visible in descent of the stair and shall have a slip-resistant surface. Marking stripes shall have a width of at least 1 inch (25 mm) but not more than 2 inches (51 mm).

1009.4.4.1 Add to read as shown.

1009.4.4.1 Tread slope shall not be more than ¼ inches per foot (21 mm/m).

1009. 5 Stairway landings.  Change Exceptions as shown.

Exceptions:

1.	Aisle stairs complying with Section 1028.

2.	In one- and two-family dwellings, a door at the top of a stair shall be permitted to open directly at a stair, provided the door does not swing over the stair and the door serves an area with an occupant load of fewer than 50 persons.

Section 1009.6.1 Stairway walking surface.  Change to read as shown.

1009. 6.1 Stairway walking surface. The walking surface of treads and landings of a stairway shall not be sloped steeper than one unit vertical in 48 units horizontal (2-percent slope) in any direction. Stairway treads and landings shall have a solid surface. Finish floor surfaces shall be securely attached.

Exceptions: No change.

1-2 No change

3. See also the Florida Building Code, Accessibility.

[F4716]

1009.6.4 Stair identification.  Add to read as shown.

1009.6.4 Stair identification.  An approved sign shall be located at each floor level landing in all enclosed stairways of buildings four or more stories in height. The sign shall indicate the floor level and the availability of roof access from that stairway and an identification of the stairway. The sign shall also state the floor level of and direction to exit discharge. The sign shall be located approximately 5 feet (1524 mm) above the floor landing in a position which is readily visible when the door is in the open or closed position. The floor level designation shall also be tactile in accordance with Chapter 11. the Florida Building Code, Accessibility.

[F4717]

1009.8 Curved stairways.  Change Exceptions as shown.

Exceptions:

1.	The radius restriction shall not apply to curved stairways for occupancies in Group R-3 and within individual dwelling units in occupancies in Group R-2.

2.	In Group R3 occupancies, circular stairs may have a minimum tread depth of 9 inches (229 mm) with 1 inch (25.4 mm) of nosing, and the smaller radius may be less than twice the width of the stairway.

1009.9 Spiral stairways.  Change to read as shown.

1009.9 Spiral stairways. Where permitted by this section or in specific occupancies in accordance with Sections 1028 and 1030 through 1037, spiral stairs complying with this section shall be permitted as a component in a means of egress.

1009.9.1 Add to read as shown.

1009.9.1 Spiral stairs complying with the following shall be permitted:

1.	Riser heights shall not exceed 7 inches (178 mm).

2.	The stairway shall have a tread depth of not less than 11 inches (279 mm) for a portion of the stairway width sufficient to provide the egress capacity for the occupant load served in accordance with Section 1004.1.

3.	At the outer side of the stairway, an additional 101/2 inches (267 mm) of width shall be provided clear to the other handrail, and this width shall not be included as part of the required egress capacity.

4.	Handrails complying with Section 1009.12 shall be provided on both sides of the spiral stairway.

5.	The inner handrail shall be located within 24 inches (610 mm), measured horizontally, of the point where a tread depth not less than 11 inches (279 mm) is provided.

6.	The turn of the stairway shall be such that descending users have the outer handrail at their right side.

1009.9.2 Add to read as shown.

1009.9.2 Where the occupant load served does not exceed three and from mezzanines not exceeding 250 square feet (23 m2) and an occupant load of three or less, spiral stairs meeting the following conditions shall be permitted:

1.	The clear width of the stairs shall be not less than 26 inches (660 mm).

2.	The height of the risers shall not exceed 9½ inches (241 mm).

3.	Headroom shall be not less than 6 feet 6 inches (1981 mm).

4. 	Treads shall have a depth not less than 7½ inches (191 mm) at a point 12 inches (305 mm) from the narrower edge.

5. 	All treads shall be identical.

6.	Handrails complying with Section 1009.12 shall be provided on both sides of the spiral stairway.

1009.9.3 Add to read as shown.

1009.9.3 Within dwellings and dwelling units, guest rooms and guest suites where the occupant load served does not exceed five, spiral stairs meeting the following conditions shall be permitted:

1.	The minimum stairway width shall be 26 inches (660 mm).

2.	The height of risers shall not be more than 9½ inches (241 mm).

3.	The headroom shall be a minimum of 6 feet 6 inches (1981 mm).

4.	Treads shall have a depth not less than 7½ inches (190 mm) at a point 12 inches (305 mm) from the narrow edge.

5.	All treads shall be identical.

6.	Handrails shall be provided on one side.

1009.10 Alternating tread devices.  Change to read as shown.

1009.10 Alternating tread devices. Alternating tread devices are limited to an element of a means of egress in buildings of Groups F, H and S from a mezzanine not more than 250 square feet (23 m2) in area and which serves not more than three occupants; in buildings of Group I-3 from a guard tower, observation station or control room not more than 250 square feet (23 m2) in area and for access to unoccupied roofs.

1009.12 Handrails.  Change Exceptions as shown.

Exceptions:

1-5 No change.

6. In one- and two-family dwellings and within dwelling units in Group R2 occupancies, stairways having four or more risers above a floor or finished ground level shall be equipped with handrails located not less than 34 inches (864 mm) or more than 38 inches (965 mm) above the leading edge of a tread.

1009.13 Stairway to roof, to read as follows:

1009.13 Access to roof. Buildings four stories or more in height, except those with a roof slope greater than 4:12, shall be provided with a stairway to the roof. Such stairway shall be marked at street and floor levels with a sign indicating that it continues to the roof. Where roofs are used for roof gardens or for other purposes, stairways shall be provided as required for such use or occupancy. Stairway to roof. In buildings four or more stories above grade plane, one stairway shall extend to the roof surface, unless the roof has a slope steeper than four units vertical in 12 units horizontal (33-percent slope). In buildings without an occupied roof, access to the roof from the top story shall be permitted to be by an alternating tread device.[3992]

1009.13.1 Roof access.  Change to read as shown.

1009.13.1 Roof access. Reserved.

1009.13.2 Protection at roof hatch openings [no change to text]

1009.15 Add to read as shown.

1009.15 Interlocking or scissor stairs shall comply with Sections 1009.15.1 and 1009.15.2.

1009.15.1 Add to read as shown.

1009.15.1 New interlocking or scissor stairs shall be permitted to be considered only as a single exit.

1009.15.2  Add to read as shown.

1009.15.2 Existing interlocking or scissor stairs shall be permitted to be considered separate exits if they meet the following criteria:

1.	They are enclosed in accordance with Section 1022.

2.	They are separated from each other by 2-hour fire-resistance-rated noncombustible construction.

3.	No protected or unprotected penetrations or communicating openings exists between the stair enclosures.

1009.16 Accessible stairs. Add to read as shown.

1009.16 Accessible stairs. Stairs required to be accessible by Section 11-4.1 shall comply with Section 11-4.9. Floor surfaces of stairs along accessible routes and in accessible rooms and spaces shall comply with the Florida Building Code, Accessibility.

Section 1010 Ramps

1010.1 Scope.  Change to read as shown.

1010.1 Scope. The provisions of this section shall apply to ramps used as a component of a means of egress.

Exceptions:

1.	Other than ramps that are part of the accessible routes providing access in accordance with Sections the provisions of the Florida Building Code, Accessibility 11-4.7 through 11-4.8, ramped aisles within assembly rooms or spaces shall conform with the provisions in Section 1028.11.

2.	Curb ramps shall comply with ICC A117.1.

3.	Vehicle ramps in parking garages for pedestrian exit access shall not be required to comply with Sections the provisions of the Florida Building Code, Accessibility 11-4.7 through 11.4-8 when they are not an accessible route serving accessible parking spaces, other required accessible elements or part of an accessible means of egress.

[F4718]

Section 1010.2 Slope, revise text to read as follows:

1010.2 Slope. Ramps used as part of a means of egress shall have a running slope not steeper than one unit vertical in 12 units horizontal (8.333-percent slope). The slope of other ramps shall not be steeper than one unit vertical in eight units horizontal (12.5-percent slope).

Exceptions:

1. Aisle ramp slope in occupancies of Group A shall comply with Section 1028.11.

2. Ramps that provide access to vehicles, vessels, mobile structures and aircraft shall not be required to comply with the maximum slope or maximum rise for a single ramp run.

1010.3 Cross slope.  Change to read as shown.

1010.3 Cross slope. The slope measured perpendicular to the direction of travel of a ramp shall not be steeper than one unit vertical in 50 48 units horizontal (2-percent slope).

Exception: See also the Florida Building Code, Accessibility.

1010.5 Minimum dimensions. The minimum dimensions of means of egress ramps shall comply with Sections 1010.5.1 through 1010.5.3.

1010.5.1 Width. The minimum width of a means of egress ramp shall not be less than that required for corridors by Section 1018.2. The clear width of a ramp between handrails, if provided, or other permissible projections shall be

36 inches (914 mm) minimum.

Exception: Ramps that are part of a required means of egress shall not be less than 44 inches (1118 mm) wide.[3993]

1010.6 Landings.  Change to read as shown.

1010.6 Landings. Ramps shall have landings at the bottom and top of each ramp, points of turning, entrance, exits and at doors and in accordance with the Florida Building Code, Accessibility   Section 11- 4.8.4. Landings shall comply with Sections 1010.6.1 through 1010.6.5.

Section 1010.6.1 Slope.  Change to read as shown.

1010.6.1 Slope. Landings shall have a slope not steeper than one unit vertical in 50 48 units horizontal (2-percent slope) in any direction. Changes in level are not permitted.

Exception: see also the Florida Building Code, Accessibility.

[F4721]

1010.6.3 Length.  Change to read as shown.

1010.6.3 Length. The landing length shall be 60 inches (1525 mm) minimum.

Exceptions:

1. In Group R-2 and R-3 individual dwelling and sleeping units that are not required to be Accessible units, landings are permitted to be 36 inches (914 mm) minimum.

2  No change

3.  Accessible landings shall comply with section of the Florida Building Code, Accessibility 11-4.8.4.

[F4722]

1010.6.4 Change in direction.  Change to read as shown.  .

1010.6.4 Change in direction. Where changes in direction of travel occur at landings provided between ramp runs, the landing shall be 60 inches by 60 inches (1524 mm by 1524 mm) minimum.

Exception: In Group R-2 and R-3 individual dwelling or sleeping units that are not required to be Accessible units, Type A units or Type B units in accordance with Section 1107, landings are permitted to be 36 inches by 36 inches (914 mm by 914 mm) minimum.

1010.7.3 Add to read as shown.

1010.7.3 All ramps that serve as required means of egress shall be of permanent fixed construction.

1010.7.4 Add to read as shown.

1010.7.4 The ramp floor and landings shall be solid and without perforations.

Section 1010.8 Handrails, revise text to read as follows:

1010.8 Handrails. Handrails shall be provided along both sides of a ramp run with a rise greater

than 6 inches (152 mm) and shall conform to the requirements in Sections 1012. If handrails

are not continuous, they shall extend at least 18 inches (305 mm) beyond the top and bottom of

the ramp segment and shall be parallel with the floor or ground surface. Ends of handrails shall

be either rounded or returned smoothly to floor, wall or post. Handrails shall not rotate within

their fittings. Top of the handrail gripping surface shall be not less than 34 inches (864 mm) nor

more than 38 inches (965 mm) above the ramp surface.

Exceptions:

1. Handrails are not required when the total ramp run rise is 6 inches (152 mm) or less and

the horizontal projection is 72 inches or less, except where required to be accessible.

2. Aisles in Group A occupancies (see Section 1028.13).

3. In dwelling units not required to be accessible by Chapter 11, fair housing requirements,

handrails are not required to extend beyond the top and bottom of the ramp segment.

4. Handrails are not required on curb ramps.

1010.9 Edge protection.  Change to read as shown.

1010.9 Edge protection. Edge protection complying with Sections 1010.9.1 or 1010.9.2 shall be provided on each side of ramp runs and at each side of ramp landings.

Exceptions:

1.	Edge protection is not required on ramps not required to have handrails, provided they have flared sides that comply with provisions of the Florida Building Code, Accessibility Section 11-4.8.7, curb ramp.

2 – 4 No change.

Section 1011 Exit Signs

1011. Exit Signs. Change to read as shown.

1011. Exit Signs.  See Section 1006.3.

1011.1 Where required. Exits and exit access doors shall be marked by an approved exit sign readily visible from any direction of egress travel. The path of egress travel to exits and within exits shall be marked by readily visible exit signs to clearly indicate the direction of egress travel in cases where the exit or the path of egress travel is not immediately visible to the occupants. Intervening means of egress doors within exits shall be marked by exit signs. Exit sign placement shall be such that no point in an exit access corridor or exit passageway is more than 100 feet (30 480 mm) or the listed viewing distance for the sign, whichever is less, from the nearest visible exit sign.

1011.1 Where required. Exits and exit access doors shall be marked by an approved exit sign readily visible from any direction of egress travel. The path of egress travel to exits and within exits shall be marked by readily visible exit signs to clearly indicate the direction of egress travel in cases where the exit or the path of egress travel is not immediately visible to the occupants. Intervening means of egress doors within exits shall be marked by exit signs. Exit sign placement shall be such that no point in an exit access corridor or exit passageway is more than 100 feet (30 480 mm) or the listed viewing distance for the sign, whichever is less, from the nearest visible exit sign.

Exceptions:

1. Exit signs are not required in rooms or areas that require only one exit or exit access.

2. Main exterior exit doors or gates that are obviously and clearly identifiable as exits need not have exit signs where approved by the building official.

3. Exit signs are not required in occupancies in Group U and individual sleeping units or dwelling units in Group R-1, R-2 or R-3.

4. Exit signs are not required in dayrooms, sleeping rooms or dormitories in occupancies in Group I-3.

5. In occupancies in Groups A-4 and A-5, exit signs are not required on the seating side of vomitories or openings into seating areas where exit signs are provided in

the concourse that are readily apparent from the vomitories. Egress lighting is provided to identify each vomitory or opening within the seating area in an emergency. [3995]

Section 1012 Handrails

1012.2 Height.  Change to add Exception as shown.

Exception: Handrails for stairs not required to be accessible that form part of a guardrail may be 42 inches (1067 mm) high.

Section 1012.3 Handrail graspability.  Change to add Exception as shown.

1012.3 Handrail graspability. All required handrails shall comply with Section 1012.3.1 or shall provide equivalent graspability.

Exceptions:

1.  In Group R-3 occupancies; within dwelling units in Group R-2 occupancies; and in Group U occupancies that are accessory to a Group R-3 occupancy or accessory to individual dwelling units in Group R-2 occupancies; handrails shall be Type I in accordance with Section 1012.3.1, Type II in accordance with Section 1012.3.2 or shall provide equivalent graspability.

2.  Accessible handrails shall meet the requirements of the Florida Building Code, Accessibility Section 11-4.26.2.

[F4725]

1012.4  Continuity.  Change Exceptions as shown.

1012.4 Continuity. Handrail-gripping surfaces shall be continuous, without interruption by newel posts or other obstructions.

Exceptions:

1. Handrails within dwelling units are permitted to be interrupted by a newel post at a turn or landing.

2. Within a dwelling unit, the use of a volute, turnout, starting easing or starting newel is allowed over the lowest tread.

3. Handrail brackets or balusters attached to the bottom surface of the handrail shall not be considered to be obstructions to graspability, provided that the following conditions are met:  that do not project horizontally beyond the sides of the handrail within 11/2 inches (38 mm) of the bottom of the handrail shall not be considered obstructions. For each 1/2 inch (12.7mm) of additional handrail perimeter dimension above 4 inches (102 mm), the vertical clearance dimension of 11/2 inches (38 mm)shall be permitted to be reduced by 1/8 inch (3 mm).

3.1.    They do not project horizontally beyond the sides of the handrail within 11/2 inches (38 mm) of the bottom of the handrail and provided that, for each ½ inch (12.7 mm) of additional handrail perimeter dimension above 4 inches (102 mm), the vertical clearance dimension of 1½ inches (38 mm) can be reduced by 1/8 inch (.3 mm).

3.2.    They have edges with a radius of not less than .01 inch (.25 mm).

3.3.    They obstruct not in excess of 20 percent of the handrail length.

4. Where handrails are provided along walking surfaces with slopes not steeper than 1:20, the bottoms of the handrail gripping surfaces shall be permitted to be obstructed along their entire length where they are integral to crash rails or bumper guards. [3985]

Section 1012.6 Handrail extensions.  Change to read as shown.

1012.6 Handrail extensions. Handrails shall return to a wall, guard or the walking surface or shall be continuous to the handrail of an adjacent stair flight or ramp run. Where handrails are

not continuous between flights, the handrails shall extend horizontally at least 12 inches (305 mm) beyond the top riser and continue to slope for the depth of one tread beyond the bottom

riser. At ramps where handrails are not continuous between runs, the handrails shall extend horizontally above the landing 12 18 inches (305 mm) minimum beyond the top and bottom of

ramp runs. The extensions of handrails shall be in the same direction of the stair flights at stairways and the ramp runs at ramps.

Exceptions:

1 – 3 No change.

4.  Accessible handrail extensions shall be as per Section 11-4.8.5(2). the Florida Building Code, Accessibility.

1012.7  Clearance.  Change to add Exception as shown.

Exception: Accessible handrails shall comply with the provisions of the Florida Building Code, Accessibility Section 11-4.8.5(3).

[F4726]

1012.9 Intermediate handrails.  Change to read as shown.

1012.9 Intermediate handrails.  Handrails shall be provided within 30 inches (762 mm) of all portions of the stair width required for egress capacity in accordance with Table 1005.1. The required egress width shall be along the natural path of travel.  Stairways shall have intermediate handrails located in such a manner that all portions of the stairway width required for egress capacity are within 30 inches (762 mm) of a handrail. On monumental stairs, handrails shall be located along the most direct path of egress travel. [4007]

1012.9.1.   Change to read as shown.

1012.9.1 Where new intermediate handrails are provided in accordance with Section 1009.11.2, the minimum clear width between handrails shall be 20 inches (510 mm).[3996]

1013.3 Opening limitations.  Revise to read as follows:

1013.3 Opening limitations. Required guards shall not have openings which allow passage of a sphere 4 inches (102 mm) in diameter from the walking surface to the required guard height. The High Velocity Hurricane Zone shall comply with section 1618.4.3 and 1618.4.4.[3681]

Section 1014 Exit Access

Section 1014.3 Common path of egress travel.  Change Exceptions as shown.

Exceptions:

1. The length of a common path of egress travel in Group B, F, M and S occupancies shall not be more than 100 feet (30 480 mm), provided that the building is equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1.

2 – 3 No change.

4. The length of a common path of egress travel in a Group R-2 occupancy shall not be more than 125 feet (38 100 mm), within the dwelling unit, provided that the building is protected throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2 otherwise 75 feet.

5. Where a tenant space in Group A occupancy has an occupant load of more than 50, the length of a common path of egress travel shall not be more than 20feet (6098 mm).

6.	The common path of egress travel in Group R1 and R2 occupancies shall not exceed 35 feet (10 668 mm). Travel within a guestroom, guest suite or dwelling unit shall not be included when calculating the common path of travel. The common path of egress travel in occupancy Groups R1 and R2 shall not exceed 50 feet (15 240 mm) provided the building is protected throughout by an approved, automatic sprinkler system in accordance with Section 903.3.1.1.

7.	The common path of egress travel in occupancies in Group F and S shall be 50 feet (15 240 mm) in unsprinklered buildings.

8.	The common path of egress travel in Group S2 Parking Garages shall be 50 feet (15 240 mm).

9.	In occupancy Group S2 common paths of egress travel shall not be limited.

10.	In occupancy Group H common paths of egress travel shall be prohibited.

Section 1015 Exit and Exit Access Doorways

Table 1015.1 Spaces with One Means of Egress, revise text to read as follows:

# Table 1015.1 SPACES WITH ONE Exit or Exit Access Doorway

| Occupancy | Maximum Occupant Load |
| --- | --- |
| A,B, E,F,M,U, R2, R3 | 49 |
| H-1,H-2,H-3 | 3 |
| D,H-4, H-5, I-1, I-3, R-1, R-4 | 10 |
| S | 29 |

1015.2.1 Two exits or exit access doorways.  Revise Exceptions as shown.

.

Exceptions:

1 – 2 No change.

3.	In Group R1 and R2 occupancies, the distance between exits is not applicable to common nonlooped exit access corridors in a building that has corridor doors from the guestroom or guest suite or dwelling unit, which are arranged so that the exits are located in opposite directions from such doors.

1015.5 Refrigerated rooms or spaces.  Change Exception as shown.

Exception: Where using refrigerants in quantities limited to the amounts based on the volume set forth in the Florida Building Code, Mechanical.

Table 1016.1 Exit Access Travel.  Change to read as shown.

| TABLE 1016.1 EXIT ACCESS TRAVEL DISTANCEa |  |  |
| --- | --- | --- |
| OCCUPANCY | WITHOUT SPRINKLER SYSTEM (feet) | WITH SPRINKLER SYSTEM (feet) |
| Rd | 100e | 200b |
| M | 150 | 250c |
| A, F-1 | 200 | 250b |
| I-1 | Not Permitted | 250c |
| B | 200 | 300c |
| S-1 | 200 | 400c |
| F-2, S-2, U | 300 | 400c |
| H-1 | Not Permitted | 75c |
| H-2 | Not Permitted | 100c |
| H-3 | Not Permitted | 150c |
| H-4 | Not Permitted | 175c |
| H-5 | Not Permitted | 200c |
| E, D, S-2f I-2, I-3 | 150 | 200c |
| For SI: 1 foot = 304.8 mm. a. See the following sections for modifications to exit access travel distance |  |  |

For SI: 1 foot = 304.8 mm.

a – c No change.

d. Travel within a guestroom, guest suite or dwelling unit shall not be included when calculating the travel distance. See 1014.3 Exception 4 for common path within.

e. For exterior 200 feet is allowed with out sprinkler.

f.  Enclosed Parking Garage

Section 1018 Corridors

Table 1018.1 Corridor Fire-Resistance Rating.  Change to read as shown.

| Occupancy | Occupant Load Served by Corridor | Required Fire-Resistance Rating (hours) |  |
| --- | --- | --- | --- |
|  |  | Without Sprinkler System | With Sprinkler System b |
| H-1, H-2, H-3 | All | 1 | 1 |
| A, H-4, H-5 | Greater than 30 | 1 | 1 |
| A, B, D, Ec, F, M, S, U | Greater than 30 | 1 | 0 |
| R | Greater than 10 | 1 | 1 |
| I-2a | All | Not permitted | 0 |
| I-1, I-3 | All | Not Permitted | 1 |

a. For requirements for occupancies in Group I-2, see Section 407.3.

b. Buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1.

c. In buildings protected throughout by an approved, supervised automatic sprinkler system in accordance with Section 903, corridor walls shall not be required to be rated, provided that such walls form smoke partitions in accordance with the Florida Fire Prevention Code.[3431]

1018.5.1 Corridor ceiling.  Change to read as shown.

1018.5.1 Corridor ceiling.  Use of the space between the corridor ceiling and the floor or roof structure above as a return air plenum is permitted for one or more of the following conditions:

1 – 2 No change.

3.	The air-handling system serving the corridor is shut down upon activation of the air-handling unit smoke detectors required by the Florida Building Code, Mechanical.

4 – 5 No change.

Section 1021 Number of Exits and Continuity

1021.1 Exits from stories..  Change Exceptions as shown.

Exceptions:

1 – 5 No change

6.  A fenced outdoor assembly occupancy shall have at least two widely separated means of egress from the enclosure. If more than 6,000 persons are to be served by such means of egress, there shall be at least three means of egress; if more than 9,000 persons are to be served, there shall be at least four means of egress.

Table 1021.2 Buildings with One Exit.

Revise the 1st raw under “Occupancy” to add “D”.

Section 1026 Exterior Exit Ramps and Stairways

1026.2 Use in a means of egress.  Change to read as shown.

1026.2 Use in a means of egress.  Exterior exit stairways shall not be used as an element of a required means of egress for Group I-2 occupancies. For occupancies in other than Group

I-2, exterior exit ramps and stairways shall be permitted as an element of a required means of egress for buildings not exceeding four stories above grade plane or having occupied floors

more than 75 feet (22 860 mm) above the lowest level of fire department vehicle access.

1026.3 Open side.  Change to read as shown.

1026.3 Open side.  Exterior exit ramps and stairways serving as an element of a required means of egress shall be not less than 50 percent open on one side. Outside stairs shall be arranged to restrict the accumulation of smoke.

Section 1028 Assembly

1028.1.1 Bleachers.  Change to read as shown.

1028.1.1 Bleachers.  Reserved.

1028.2 Assembly main exit.  Change to read as shown.

1028.2 Assembly main exit.  Every assembly occupancy shall be provided with a main entrance/exit. The minimum aggregate width of the main entrance for Group A occupancies shall be sufficient to accommodate 50 percent of the occupant load and shall be at the level of exit discharge or shall connect to a stairway or ramp leading to a street. Each level of a Group A occupancy shall have access to a main exit and such access shall have sufficient capacity to accommodate 50 percent of the occupant load of such levels.  Where the main exit from an assembly occupancy is through a lobby or foyer, the aggregate capacity of all exits from the lobby or foyer shall be permitted to provide the required capacity of the main exit regardless of whether all such exits serve as entrances to the building.

Exception:

1.	A bowling establishment shall have a main entrance capable of accommodating 50 percent of the total occupant load regardless of the aisles that the entrance serves.

2.	 In assembly occupancies where there is no well-defined entrance/exit, exits may be distributed around the perimeter of the building, provided the total exit width furnishes a minimum of 100 percent of the width needed to accommodate the maximum occupant content.

1028.3  Assembly other exits.  Change to read as follows:

1028.3 Assembly other exits.  Each level of an assembly occupancy shall have access to a main exit and shall be provided with additional exits of sufficient width to accommodate one-half of the total occupant load served by that level. Such additional exits shall be located as far from the main entrance/exit as practicable.  Such exits shall be accessible from a cross aisle or a side aisle.

Exception: In assembly occupancies where there is no well-defined entrance/exit, exits may be distributed around the perimeter of the building, provided the total exit width furnishes a minimum of 100 percent of the width needed to accommodate the maximum occupant content.

Section 1028.6.1  Without smoke protection.  Change to read as shown.

1028.6.1 Without smoke protection. Change Item 4 as shown.

1- 3 No change.

4. Ramped means of egress, where slopes are steeper than one unit vertical in 12 units horizontal (8.333-percent slope), shall have at least 0.22 inch (5.6 mm) of clear width for each occupant served. Level or ramped means of egress, where slopes are not steeper than one unit vertical in 12 units horizontal (8-percent slope), shall have at least 0.20 inch (5.1 mm) of clear width for each occupant served.

Section 1028.6.2 Change to read as follows:

1028.6.2 Smoke-protected seating.  The clear width of the means of egress for smoke-protected assembly seating shall not be less than the occupant load served by the egress element

multiplied by the appropriate factor in Table 1028.6.2.  The total number of seats specified shall be those within the space exposed to the same smoke-protected environment.

Interpolation is permitted between the specific values shown. A life safety evaluation, complying with NFPA 101 as adopted by Florida Fire Prevention Code, shall be done for a facility utilizing the reduced width requirements of Table 1028.6.2 for smoke-protected assembly seating.

Exception:  No change.

Section 1028.7 Travel distance.  Change to read as shown.

1028.7 Travel distance. Exits and aisles shall be so located that the travel distance to an exit door shall not be greater than 200 feet (60 960 mm) measured along the line of travel in nonsprinklered buildings. Travel distance shall not be more than 250 feet (76 200 mm) in sprinklered buildings. Where aisles are provided for seating, the distance shall be measured along the aisles and aisle accessway without travel over or on the seats.

Exceptions:

1 – 2 No change.

3.	The travel distance within an exhibit booth or exhibit enclosure to an exit access aisle shall not be greater than 50 feet (15 240 mm).

1028.8 Common path of travel.  Change to read as shown.

1028.8 Common path of travel.  A common path of travel shall be permitted for the 20 feet (6.1 m) from any point where serving any number of occupants and for the first 75 feet (22 860 mm) from any point where serving not more than 50 occupants.

Exception:

1.	For smoke-protected assembly seating, the common path of travel shall not exceed 50 feet (1524 mm) from any seat to appoint where a person has a choice of two directions of egress travel.

1028.9.1 Minimum aisle width.  Change to read as shown.

1028.9.1 Minimum aisle width.  The minimum clear width of aisles serving seating not at tables shall be as shown:

1.	Forty-eight inches (1219 mm) for aisle stairs having seating on each side.

Exception: Thirty-six inches (914 mm) where the aisle does not serve more than 50 seats.

2.	Thirty-six inches (914 mm) for aisle stairs having seating on only one side.

3.	Twenty-three inches (584 mm) between an aisle stair handrail or guard and seating where the aisle is subdivided by a handrail.

4.	Forty-two inches (1067 mm) for level or ramped aisles having seating on both sides.

Exceptions:

1.	Thirty-six inches (914 mm) where the aisle does not serve more than 50 seats.

.2.	Thirty inches (762 mm) where the aisle does not serve more than 14 seats.

5.  No change.

1028.9.1.1  Add to read as shown.

1028.9.1.1 The minimum width of aisles serving seating at tables shall be 44 inches (1118 mm).

Exception: Thirty-six inches  (914 mm) where serving an occupant load of not more than 50.

1028.9.2 Means of egress capacity.  Change to read as shown.

1028.9.2 Means of egress capacity.  The capacity of means of egress shall be in accordance with Section 1005. The width of aisles and other means of egress serving theater-type seating or similar seating arranged in rows shall provide sufficient capacity in accordance with Sections 1025.9.2.1 and 1025.9.2.2.

1028.9.2.1 Add to read as shown.

1028.9.2.1 Minimum clear widths of aisles and other means of egress serving theater-type seating, or similar seating arranged in rows, shall be in accordance with Table 1025.9.2.1.

Table 1028.9.2.1 Capacity Factors.  Add to read as shown.

TABLE 1028.9.2.1

CAPACITY FACTORS

| No. of Seats | Nominal Flow Time (sec) | Inch of Clear Width per Seat Served |  |
| --- | --- | --- | --- |
|  |  | Stairs | Passageways, Ramps, and Doorways |
| Unlimited | 200 | 0.300 AB | 0.220 C |

1028.9.2.2 Add to read as shown.

1028.9.2.2 The minimum clear widths shown in Table 1025.9.2.1 shall be modified in accordance with all of the following:

1.	If risers exceed 7 inches (178 mm) in height, multiply the stair width in the table by factor A, where

A = 1 + (riser height - 7 inches.)

5

2.	Stairs not having a handrail within a 30-inch (762 mm) horizontal distance shall be 25 percent wider than otherwise calculated (i.e., multiply by factor B = 1.25).

3.	Ramps steeper than 1:10 slope where used in ascent shall have their width increased by 10 percent (i.e., multiply by factor C = 1.10).

Exceptions:

1.	Lighting and access catwalks shall meet the requirements for Group F occupancies.

2.	Grandstands, bleachers and folding and telescopic seating as permitted by Section 1025.6.2.

1028.9.2.3 Add to read as shown.

1028.9.2.3 Clear width shall be measured to walls, edges of seating and tread edges except for permitted projections.

Section 1028.9.3 Converging aisles, add text to read as follows:

1028.9.3 Converging aisles. Where aisles converge to form a single path of egress travel, the required egress capacity of that path shall not be less than the combined required capacity of the converging aisles.

1028.10 Change to read as shown.

1028.10 Aisle accessways.  The aisle accessway between rows of seating shall have a clear width of not less than 12 inches (305 mm), and the minimum width shall be increased in accordance with Sections 1028.10.2 for seating not at tables and Section 1028.10.2.2 for seating at tables. The width of aisle access-ways shall be the clear horizontal distance from the back of the row ahead and the nearest projection of the row behind. Where chairs have automatic or self-rising seats that comply with ASTM F 851, Test Method for Self-Rising Seat Mechanisms, the measurement shall be made with seats in the raised position. Where any chair in the row does not have an automatic or self-rising seat, the measurements shall be made with the seat in the down position. For seats with folding tablet arms, row spacing shall be determined with the tablet in the useable position.

Exception: When not more than four persons are served, there shall be no minimum clear width requirement for the portion of the aisle accessway having a length not exceeding 6 feet (1.8 m) measured from the center of the seat farthest from the aisle.

1028.10.1  Dual access.  Change to read as shown.

1028.10.1  Dual access.  Reserved.

1028.10.2 Single access. Change to read as shown.

1028.10.2 Single access. For rows of seating not at tables served by aisles or doorways at both ends there shall be no more than 100 seats per row and the 12 inches (305 mm) minimum clear width of aisle accessways shall be increased by 0.3 inch (7.6 mm) for every additional seat beyond 14, but the minimum clear width shall not be required to exceed 22 inches (559 mm).

Exception: For smoke-protected assembly seating, the row length limits for a 12-inch-wide (305 mm) aisle accessway, beyond which the aisle accessway minimum clear width shall be increased, are in Table 1025.10.2.

1028.10.2.1 Add to read as shown.

1028.10.2.1  For rows of seating not at tables served by an aisle or doorway at one end only, the 12 inches (305 mm) minimum clear width of aisle accessways shall be increased by 0.6 inch (15.2 mm) for every additional seat beyond seven, but the minimum clear width shall not be required to exceed 22 inches (559 mm).

Exception: For smoke-protected assembly seating, the row length limits for a 12-inch-wide (305 mm) aisle accessway, beyond which the aisle accessway minimum clear width shall be increased, are in Table 1028.10.2.

1028.10.2.1.2 Add to read as shown.

1028.10.2.1.2  For rows of seating not at tables served by an aisle or doorway on one end only, the path of travel shall not exceed 30 feet (9144 mm) from any seat to a point where a person has a choice of two paths of travel to two exits.

1028.10.2.2 Add to read as shown.

1028.10.2.2  Aisle accessways serving seating at tables shall have a minimum clear width of 12 inches (305 mm).

1028.10.2.2.1 Add to read as shown.

1028.10.2.2.1  Where nonfixed seating is located between a table and an aisle accessway, the measurement of required clear width of the aisle accessway shall be made to a line 19 inches (483 mm) away from the edge of the table. The 19 inches (483 mm) distance shall be measured perpendicularly to the edge of the table.

1028.10.2.2.2 Add to read as shown.

1028.10.2.2.2  The minimum 12 inches (305 mm) width required for an aisle accessway shall be increased by 0.5 inches (13 mm) for each additional 12 inches (305 mm) or fraction thereof beyond 12 feet (3.7 m) of aisle accessway length where measured from the center of the seat farthest from an aisle.

1028.10.2.2.3 Add to read as shown.

1028.10.2.2.3  The path of travel along the aisle accessway shall not exceed 36 feet (10.9 m) from any seat to the closest aisle or egress doorway.

1028.11.2 Risers.  Change to read as shown.

1028.11.2 Risers.  Where the gradient of aisle stairs is to be the same as the gradient of adjoining seating areas, the riser height shall not be less than 4 inches (102 mm) nor more than 8 inches (203 mm) and shall be uniform within each flight.

Exceptions:

1.	The riser height of aisle stairs in folding and telescopic seating shall be permitted to be not less than 3½ inches (89 mm) and shall not exceed 11 inches (279 mm).

2.	Riser heights not exceeding 9 inches (229 mm) shall be permitted where they are necessitated by the slope of the adjacent seating areas to maintain sightlines.

1028.12 Seat stability.  Change to read as shown.

1028.12 Seat stability.  In places of assembly, the seats shall be securely fastened to the floor.

Exceptions:

1 – 6 No change.

7.	Restaurants, cafeterias, cafetoriums, gymnasiums, gymnatoriums and similar multipurpose assembly occupancies.

8.	Movable seating in rows with seats fastened together in groups of not less than three nor more than seven.

9.	Seats in balconies, galleries, railed in enclosures, boxes or loges with level floor surfaces and having occupant loads not exceeding 14.

10.	Assembly occupancies in accordance with Exceptions 1 or 3 shall not have more than one seat for 15 square feet (1.4 m2) of net floor area and shall provide adequate aisles to reach exits.

1028.13 Handrails.  Change to read as shown.

1028.13 Handrails.  Ramped aisles having a slope exceeding one unit vertical in 15 units horizontal (6.7-percent slope) and aisle stairs shall be provided with handrails located either at the side or within the aisle width. Handrails shall not be required where otherwise permitted by the following:

1.	Handrails shall not be required for ramped aisles having a gradient not steeper than 1:8 and having seating on both sides where the aisle does not serve as an accessible route.

2.	The requirement for a handrail shall be satisfied by the use of a guard provided with a rail that complies with the graspability requirements for handrails and located at a consistent height between 34 inches and 42 inches (865 mm and 1065 mm), measured using one of the following methods:

a.	Vertically from the top of the rail to the leading edge (nosing) of stair treads.

b.	Vertically from the top of the rail to the adjacent walking surface in the case of a ramp.

3. Handrail extensions are not required at the top and bottom of aisle stairs and aisle ramp runs to permit crossovers within the aisles.

No change to the remaining text.

Section 1029 Emergency Escape and Rescue

1029.1 General.  Change to read as shown.

1029.1 General.  In addition to the means of egress required by this chapter, provisions shall be made for emergency escape and rescue in Group R and I-1 occupancies. Basements and sleeping rooms below the fourth story above grade plane shall have at least one exterior emergency escape and rescue opening in accordance with this section. Where basements contain one or more sleeping rooms, emergency egress and rescue openings shall be required in each sleeping room, but shall not be required in adjoining areas of the basement. Such opening shall open directly into a public way or to a yard or court that open to a public way. The emergency escape and rescue opening shall be permitted to open into a screen enclosure, open to the atmosphere, where a screen door is provided leading away from the residence. Such opening shall be operational from the inside without the use of special knowledge, keys or tools.

Exceptions:

1- 7 No change.

8.	Security and hurricane devices installed in accordance with Section 1008.1.4.6.

1029.4.1 Add to read as shown.

1029.4.1 Every room or space greater than 250 square feet (23.2 m2) in educational occupancies used for classroom or other educational purposes or normally subject to student occupancy and every room or space normally subject to client occupancy, other than bathrooms, in Group D occupancies shall have not less than one outside window for emergency rescue that complies with the following:

1. Such windows shall be openable from the inside without the use of tools and shall provide a clear opening of not less than 20 inches (508 mm) in width, 24 inches (610 mm) in height, and 5.7 square feet (0.53 m2) in area.

2. The bottom of the opening shall be not more than 44 inches (1118 mm) above the floor, and any latching device shall be capable of being operated from not more than 54 inches (1372 mm) above the finished floor.

Exceptions:

- Buildings protected throughout by an approved, supervised automatic sprinkler system in accordance with section 903.3.1.1.

- Where the room or space has a door leading directly to the outside of the building.

Section 1030 Business, add to read as shown.

SECTION 1030 BUSINESS

1030.1 Doors. Egress doors shall conform to the requirements of Section 1008, except doors

serving office areas with an occupant load of 10 or less need not be side-swinging type.

1030.2 Handrails and guardrails.  Handrails and guardrails shall be in accordance with Sections 1012 and 1013.

Exception: In areas not accessible to the public and in fully enclosed stairways in office

buildings not serving a Group A, E or R occupancy, the clear distance between rails or

ornamental pattern shall be such as to prevent the passage of a 21-inch (533 mm) diameter

sphere.

1030.3 Stairs. Spiral stairs complying with Section 1009.9 shall be permitted as a component in a means of egress.

1030.4 Common path of travel. In Group B buildings, which are sprinklered throughout, a

common path of travel not exceeding 100 feet (30 480 mm) shall be permitted.

Section 1031 Educational.  Add to read as shown:

SECTION 1031 EDUCATIONAL

1031.1 Exterior corridors or balconies.

1031.1.1 A corridor roofed over and enclosed on its long sides and open to the atmosphere at the ends may be considered an exterior corridor provided:

1. Clear story openings not less than one-half the height of the corridor walls are provided on both sides of the corridor and above adjacent roofs or buildings, or

2. The corridor roof has unobstructed openings to the sky with the open area not less than 50 percent of the area of the roof. Openings shall be equally distributed with any louvers fixed open. The clear area of openings with fixed louvers shall be based on the actual openings between louver vanes.

1031.1.2 The minimum width of such corridors shall be sufficient to accommodate the occupant load but shall in no case be less than 6 feet (1829 mm).

1031.2 Panic and fire exit hardware.

1031.2.1 Each door in a means of egress from an area of Group E occupancy having an occupant load of 100 or more may be provided with a latch or lock only if it is panic hardware or fire exit hardware, which releases when a force of no more than 15 pounds (67 N) is applied to the releasing devices in the direction of exit travel. Such releasing devices may be bars or panels extending not less than one-half the width of the door and placed at heights suitable for the service required, but not less than 34 inches (864 mm) nor more than 48 inches (1219 mm) above the floor. Whenever panic hardware is used on a labeled fire door, the panic hardware shall be labeled as fire exit hardware.

1031.2.2 If balanced doors are used and panic hardware is required, the panic hardware shall be of the pushpad type and the pad shall not extend more than one-half the width of the door measured from the latch side.

1031.3 Doors that swing into an exit access corridor shall be recessed to prevent interference with corridor traffic; any doors not recessed shall open 180 degrees (3.1 rad) to stop against the wall. Doors in any position shall not reduce the required corridor width by more than one-half.

Section 1032 Factory-Industrial,  Add to read as shown.

SECTION 1032 FACTORY-INDUSTRIAL

1032.1 Handrails and guardrails. Handrails and guardrails shall be installed in accordance with Sections 1009.12 and 1013.

Exception: In areas not accessible to the public in Group F, the clear distance between rails or

ornamental pattern shall be such as to prevent the passage of a 21-inch (533 mm) diameter

sphere.

1032.2 Stairs. Spiral stairs complying with Section 1009.9 shall be permitted as a component in a means of egress.

1032.3 Common path of travel. Common paths of travel in Group F, special purpose occupancies shall not exceed 50 feet (15 m).

Exception: In Group F buildings, which are sprinklered throughout, a common path of travel not exceeding 100 feet (30 m) shall be permitted.

Section 1033 Institutional.  Add to read as shown.

SECTION 1033 INSTITUTIONAL

1033.1 Locks. Patient rooms or tenant space egress doors in Group I occupancies shall not be lockable.

Exceptions:

1. In places of restraint or detention.

2. Door locking arrangements without delayed egress shall be permitted in Groups I-1 and I-2, or portions of such occupancies, where the clinical needs of the patients require specialized security measures for their safety, provided that staff can readily unlock such doors at all times.

3. Key locking devices that restrict access from the corridor and that are operable only by staff from the corridor side shall be permitted. Such devices shall not restrict egress from the room.

1033.2 Arrangement of means of egress.

1033.2.1 Every habitable room shall have an exit access door leading directly to an exit access corridor.

Exceptions:

1. If there is an exit door opening directly to the outside from the room at ground level.

2. Patient sleeping rooms shall be permitted to have one intervening room if the intervening room is not used as an exit access for more than eight patient sleeping beds.

3. Special nursing suites shall be permitted to have one intervening room where the arrangement allows for direct and constant visual supervision by nursing personnel.

4. For rooms other than patients’ sleeping rooms, one or more adjacent rooms shall be permitted to intervene in accordance with Section 1029.8.

1033.3 Any patient sleeping room, or any suite that includes patient sleeping rooms, of more

than 1,000 square feet (93 m2) shall have at least two exit access doors remotely located from

each other.

1033.4 Any room or any suite of rooms, other than patient sleeping rooms, of more than 2,500

square feet (230 m2) shall have at least two exit access doors remotely located from each other.

1033.5 Any suite of rooms that complies with the requirements of Section 1029.3 shall be permitted to be subdivided with nonfire-rated, noncombustible or limited-combustible partitions.

1033.6 Suites of sleeping rooms shall not exceed 5,000 square feet (460 m2).

1033.7 Suites of rooms, other than patient sleeping rooms, shall not exceed 10,000 square feet

(930 m2).

1033.8 Suites of rooms, other than patient sleeping rooms, shall be permitted to have one

intervening room if the travel distance within the suite to the exit access door is not greater than

100 feet (30 m) and shall be permitted to have two intervening rooms where the travel distance

within the suite to the exit access door is not greater than 50 feet (15 m).

1033.9 Every corridor shall provide access to at least two approved exits without passing through any intervening rooms or spaces other than corridors or lobbies.

1033.10 Every exit or exit access shall be arranged so that no corridor, aisle or passageway has a pocket or dead end exceeding 20 feet (6096 mm).

1033.11 Travel distance.

1033.11.1 Travel distance shall not exceed that specified in Table 1016.1.

1033.11.2 Travel distance shall comply with Section 1033.11.2.1 through 1033.11.2.4.

1033.11.2.1 The travel distance between any room door required as an exit access and an exit

shall not exceed 150 feet (45 m).

1033.11.2.2 The travel distance between any point in a room and an exit shall not exceed 200

feet (60 m).

1033.11.2.3 The travel distance between any point in a health care sleeping room and an exit

access door in that room shall not exceed 50 feet (15 m).

1033.11.2.4 The travel distance between any point in a suite of sleeping rooms as permitted by

Section 1029.2 and an exit access door of that suite shall not exceed 100 feet (30 m) and shall meet the requirements of Section 1033.11.2.2.

1033.12 Measurement of travel distance to exits. Travel distance shall be determined in accordance with Section 1016, but shall not exceed:

1. One-hundred feet (30 m) between any room door required as exit access and an exit.

2. One-hundred-and-fifty feet (46 m) between any point in a room and an exit.

3. Fifty feet (15 m) between any point in a sleeping room and the door of that room.

Exceptions:

1. The travel distance above may be increased by 50 feet (15 m) in rooms other than sleeping rooms when the building is protected throughout by an approved automatic sprinkler system or smoke control system.

2. The maximum permitted travel distance shall be increased to 100 feet (30 m) in sprinklered or unsprinklered open dormitories where the enclosing walls of the dormitory space are of smoketight construction. Where travel distance to the exit access door from any point within the dormitory exceeds 50 feet (15 m), a minimum of two exit access doors remotely located from each other shall be provided.

1033.13 Stairs.

1033.13.1 Spiral stairs meeting the requirements of Section 1009.9 are permitted for access to

and between staff locations.

1033.13.2 Alternating tread stairways meeting the requirements of Section 1009.10 are permitted

for access to and between staff locations subject to occupancy by no more than three persons all

capable of using the alternating tread stairway.

1033.13.3 Solid risers, intermediate handrails, latticework or similar facilities required by

Sections 1009.4.5 and 1013.3 which would interfere with visual supervision of residents are not

required.

Section 1034 Mercantile.  Add to read as shown.

SECTION 1034 MERCANTILE

1034.1 Stairs. Spiral stairs complying with Section 1009.8 shall be permitted as a component in

a means of egress.

1034.2 Handrails and guardrails. Handrails and guardrails shall be installed in accordance with Sections 1009.12 and 1013.

Exception: In areas not accessible to the public and in fully enclosed stairways in Group M not

serving a Group A, E or R occupancy, the clear distance between rails or ornamental pattern

shall be such as to prevent the passage of a 21-inch (533 mm) diameter sphere.

1034.3 Common path of travel. In Group M buildings which are sprinklered throughout, a

common path of travel not exceeding 100 feet (30 m) shall be permitted.

Section 1035 Residential. Add to read as shown.

SECTION 1035 RESIDENTIAL

1035.1 Stairways not part of the required means of egress and providing access from the outside

grade level to the basement in Group R3 occupancies shall be exempt from Section 1009 when

the maximum height from the basement finished floor level to grade adjacent to the stair does not

exceed 8 feet (2438 mm) and the grade level opening to the stair is covered by hinged doors or

other approved means.

1035.2 Common path of travel. In Group R1 and R2 occupancies no common path of travel

shall exceed 35 feet (10.7 m). Travel within a guestroom, guest suite or dwelling unit shall not be

included when calculating common path of travel.

Exception: In buildings protected throughout by an approved, automatic sprinkler system a

common path of travel shall not exceed 50 feet (15 m).

1035.3 Travel distance in group R1 and R2 occupancies. In group R1 and R2 occupancies

travel distance within a guest room, guest suite or dwelling unit to a corridor door shall not

exceed 75 feet (23 m) and allowed to be increased to125 feet when the building is protected

throughout by an approved, supervised automatic sprinkler system in accordance with s.

903.3.1.1.

Section 1036 Storage.  Add to read as shown.

SECTION 1036 STORAGE

1036.1 Aircraft servicing hangars.

1036.1.1 Exits from aircraft servicing areas shall be provided at intervals of not more than 150 feet (45 m) on all exterior walls. There shall be a minimum of two means of egress from each aircraft servicing area. Horizontal exits through interior fire walls shall be provided at intervals of not more than 100 feet (30 m) along the wall.

Exception: Dwarf or “smash” doors in doors used for accommodating aircraft shall be permitted for compliance with these requirements.

1036.1.2 Means of egress from mezzanine floors in aircraft servicing areas shall be arranged so that the maximum travel distance to reach the nearest exit from any point on the mezzanine shall not exceed 75 feet (23 m). Such means of egress shall lead directly to a properly enclosed stair discharging directly to the exterior, to a suitable cutoff area or to outside stairs.

1036.2 Stairs. Spiral stairs complying with Section 1009.9 shall be permitted as a component in

a means of egress.

1036.3 Handrails and guardrails. Handrails and guardrails shall be installed in accordance with Sections 1009.12 and 1013.

Exception: In areas not accessible to the public in Group S, the clear distance between rails or ornamental pattern shall be such as to prevent the passage of a 21-inch (533 mm) diameter sphere.

1036.4 Common path of travel.

1036.4.1 In Group S1 storage, occupancies common path of travel shall not exceed 50 feet (15

m).

Exception: Common paths of travel shall not exceed 100 feet (30 m) in buildings protected by

an approved automatic sprinkler system.

1036.4.2 In Group S2 storage, occupancies common paths of travel shall not be limited.

1036.4.3 A common path of travel for the first 50 feet (15 m) from any point shall be permitted

in parking structures.

Section 1037 Day Care.  Add to read as shown.

SECTION 1037 DAY CARE

1037.1 Panic and fire exit hardware.

1037.1.1 Any door in a required means of egress from an area having an occupant load of 100 or more persons shall be permitted to be provided with a latch or lock only if it is panic hardware or fire exit hardware which releases when a force of no more than 15 pounds (67 N) is applied to the releasing devices in the direction of exit travel. Such releasing devices may be bars or panels extending not less than one-half the width of the door and placed at heights suitable for the service required, but not less than 34 inches (864 mm) nor more than 48 inches (1219 mm) above the floor. Whenever panic hardware is used on a labeled fire door, the panic hardware shall be labeled as fire exit hardware.

1037.1.2 If balanced doors are used and panic hardware is required, the panic hardware shall be of the push-pad type and the pad shall not extend more than one-half the width of the door measured from the latch side.

1037.2 Doors and corridors.

1037.2.1 Every room or space with an occupant load of more than 50 persons or an area of more than 1,000 square feet (93 m2) shall have at least two exit access doorways as remotely located from each other as practicable. Such doorways shall provide access to separate exits, but where egress is through corridors, they shall be permitted to open onto a common corridor leading to separate exits located in opposite directions.

1037.2.2 Where the two exit accesses from a day care occupancy in an apartment building enter the same corridor as the apartment occupancy, the exit accesses shall be separated in the corridor by a smoke barrier having not less than a 1-hour fire-resistance rating constructed in accordance with Section 709. The smoke barrier shall be located so that it has an exit on each side.

1037.2.3 Doors designed to be normally closed shall comply with Section 715.4.8.

1037.3 A travel distance of 200 feet (60 960 mm) in unsprinklered buildings and 250 feet (76

200 mm) in buildings protected throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1 and the following.

1. The travel distance between any room door intended as an exit access and an exit shall not exceed 100 feet (30 m); and

2. The travel distance between any point in a room and an exit shall not exceed 150 feet (45

m); and

3. The travel distance between any point in a sleeping room and an exit access door in that room shall not exceed 50 feet (15 m).

Exception: The travel distance in Items 1 and 2 above may be increased by 50 feet (15 m) in buildings protected throughout by an approved supervised automatic sprinkler system.

1037.4 Illumination and marking of means of egress. Illumination and marking of means of

egress shall comply with Section 1006.

1037.5 Emergency lighting. Emergency lighting in accordance with Section 1006.2 shall be provided in the following areas:

1. Interior stairs and corridors.

2. Normally occupied spaces.

Exception: Administrative areas, general classrooms, mechanical rooms and storage areas.

3. Flexible and open plan buildings.

4. Interior or windowless portions of buildings.

5. Shops and laboratories.

1037.6 Special means of egress features. Every room or space normally subject to client occupancy, other than bathrooms, shall have at least one outside window for emergency rescue and ventilation. Such window shall be openable from the inside without the use of tools and shall provide a clear opening of not less than 20 inches (508 mm) width, 24 inches (610 mm) in height, and 5.7 square feet (0.53 m2) in area. The bottom of the opening shall be not more than 44 inches (1118 mm) above the floor. The clear opening shall permit a rectangular solid, with a minimum width and height that provides the required 5.7 square foot (0.53 m2) opening and a minimum depth of 20 inches (8 mm), to pass fully through the opening.

Exceptions:

1. In buildings protected throughout by an approved, automatic sprinkler system.

2. Where the room or space has a door leading directly to the outside of the building.

1037.7 Flexible plan and open plan buildings. In day care occupancies, each room occupied by more than 300 persons shall have two or more means of egress entering into separate atmospheres. If three or more means of egress are required, not more than two of them shall enter into a common atmosphere.

1037.8 Group day care homes means of escape requirements.

1037.8.1 The provisions of Chapter 10 shall be applicable to means of escape in day care homes except as modified in this section.

1037.8.2 In group day care homes, every story occupied by clients shall have not less than two

remotely located means of escape. Maximum travel distance shall be as specified in Section

10374.3.

1037.8.3 In group day care homes, every room used for sleeping, living or dining purposes shall have at least two means of escape, at least one of which shall be a door or stairway that provides a means of nonobstructed travel to the outside of the building at street or ground level. The second means of escape may be a window in accordance with Section 10374.6. No room or space that is accessible only by a ladder or folding stairs or through a trap door shall be occupied for living or sleeping purposes.

1037.8.4 In group day care homes where spaces on the story above the story of exit discharge are used by clients, at least one means of escape shall be an exit discharging directly to the outside. The second means of escape may be a window in accordance with Section 10374.6.

1037.8.5 In group day care homes where clients occupy a story below the level of exit discharge, at least one means of escape shall be an exit discharging directly to the outside. The second means of escape may be a window in accordance with Section 10374.6. No facility shall be located more than one story below the ground. In day care homes, any stairway to the story above shall be cut off by a fire barrier containing a door that has at least a 20-minute fire protection rating and is equipped with a self-closing device.

1037.8.6 In group day care homes, every room or space normally subject to client occupancy, other than bathrooms, shall have at least one outside window for emergency rescue and ventilation complying with Section 10374.6.

Exceptions:

1. In buildings protected throughout by an approved, automatic sprinkler system.

2. Where the room or space has a door leading directly to the outside of the building.

1037.8.7 Where the two exit accesses from a group day care home in an apartment building enter the same corridor as the apartment occupancy, the exit accesses shall be separated in the corridor by a smoke barrier having not less than a 1-hour fire-resistance rating constructed in accordance with Section 710. The smoke barrier shall be located so that it has an exit on each side.

Section 1038 Boiler, Furnace and Mechanical Equipment Rooms.  Add to read as shown.

SECTION 1038 BOILER, FURNACE AND MECHANICAL EQUIPMENT ROOMS

1038.1 Single means of egress. Stories used exclusively for boilers, furnaces or mechanical equipment shall be permitted to have a single means of egress where the travel distance to an exit

on that story does not exceed the common path of travel stipulated in Section 10385.2.

1038.2 Common path of travel. Boiler rooms, furnace rooms, mechanical equipment rooms and similar spaces shall have a common path of travel not exceeding 50 feet (15 m).

Exceptions:

1. In buildings protected throughout with an approved automatic sprinkler system boiler rooms, furnace rooms, mechanical equipment rooms and similar spaces shall be permitted to have a common path of travel not exceeding 100 feet (30 m).

2. Mechanical equipment rooms with no fuel-fired equipment shall be permitted to have a common path of travel not exceeding 100 feet (30 m).

- CHAPTER 11 FLORIDA ACCESSIBILITY CODE FOR BUILDING CONSTRUCTION

See Chapter 11

Chapter 12 Interior Environment

Section 1202 Definitions.  Change to read as shown.

1202.1 General. The following words and terms shall, for the purposes of this chapter and as used elsewhere in this code, have the meanings shown herein.

SUNROOM

1. A room with roof panels that include sloped glazing that is a one-story structure added to an existing dwelling with an open or glazed area in excess of 40 percent of the gross area of the sunroom structure’s exterior walls and roof.

2. A one-story structure added to a dwelling with structural solid roof panels without sloped glazing. The sunroom walls may have any configuration, provided the open area areas with operable or fixed glass or windows or side hinged or sliding glass doors of the longer wall and one additional wall is equal to at least 65 percent of the area below 6 foot 8 inches of each wall, measured from the floor.  For the purposes of this code the term sunroom as used herein shall include conservatories, sunspaces, solariums, and porch or patio covers or enclosures. [4109]

Section 1203 Ventilation

1203.1 General.  Change to read as shown.

1203.1 General.  Buildings shall be provided with natural ventilation in accordance with Section 1203.4, or mechanical ventilation in accordance with the Florida Building Code, Mechanical.

Section 1203.2 Attic spaces.  Change to add Exception as shown.

Exception:

Attic spaces, designed by a Florida licensed engineer or registered architect to eliminate the attic venting.

1203.2.1 Openings into attic.  Change to read as shown.

1203.2.1 Openings into attic. Exterior openings into the attic space of any building intended for human occupancy shall be protected to prevent the entry of birds, squirrels, rodents, snakes and other similar creatures. Openings for ventilation having a least dimension of 1/16 inch (1.6 mm)

minimum and 1/4 inch (6.4 mm) maximum shall be permitted.  Openings for ventilation having a least dimension larger than 1/4 inch (6.4 mm) shall be provided with corrosion- resistant wire cloth screening, hardware cloth, perforated vinyl or similar material with openings having a least

dimension of 1/16 inch (1.6 mm) minimum and 1/4 inch (6.4 mm) maximum. Where combustion air is obtained from an attic area, it shall be in accordance with Chapter 7 of the

International Mechanical Code Florida Building Code, Mechanical.

Revise 1203.3.2 to read as follows:

1203.3.2 Exceptions. The following are exceptions to Sections 1203.3 and 1203.3.1:1. Where warranted by climatic conditions, ventilation openings to the outdoors are not required if ventilation openings to the interior are provided.

2. The total area of ventilation openings is permitted to be reduced to 1/1,500 of the under-floor area where the ground surface is covered with a Class I vapor retarder material and the required openings are placed so as to provide cross ventilation of the space. The installation of operable louvers shall not be prohibited.

3. Ventilation openings are not required where continuously operated mechanical ventilation is provided at a rate of 1.0 cubic foot per minute (cfm) for each 50 square feet (1.02 L/s for each 10 m2) of crawl space floor area and the ground surface is covered with a Class I vapor retarder.

4. Ventilation openings are not required when the ground surface is covered with a Class I vapor retarder, the perimeter walls are insulated and the space is conditioned in accordance with the International Energy Conservation Code the Florida Building Code, Energy Conservation.

5. For buildings in flood hazard areas as established in Section 1612.3, the openings for under-floor ventilation shall be deemed as meeting the flood opening requirements of ASCE 24 provided that the ventilation openings are designed and installed in accordance with ASCE 24.

5 6. Crawl spaces, designed by a Florida-licensed engineer or registered architect to eliminate the venting.  [3986]

1203.4.2 Contaminants exhausted.  Change to read as shown.

- 1203.4.2 Contaminants exhausted.  Contaminant sources in naturally ventilated spaces shall be removed in accordance with the Florida Building Code, Mechanical and the Florida Fire Prevention Code.

1203.4.2.1 Bathrooms.  Change to read as shown.

- 1203.4.2.1 Bathrooms.  Rooms containing bathtubs, showers, spas and similar bathing fixtures shall be mechanically ventilated in accordance with the Florida Building Code, Mechanical.

1203.5 Other ventilation and exhaust systems.  Change to read as shown.

1203.5 Other ventilation and exhaust systems.  Ventilation and exhaust systems for occupancies and operations involving flammable or combustible hazards or other contaminant sources as covered in the Florida Building Code, Mechanical or the Florida Fire Prevention Code shall be provided as required by both codes.

Section 1205 Lighting

1205.4.1 Controls.  Change to read as shown.

1205.4.1 Controls.  The control for activation of the required stairway lighting shall be in accordance with Chapter 27.

Section 1206 Yards or Courts

1206.3.3 Court drainage.  Change to read as shown.

1206.3.3 Court drainage.  The bottom of every court shall be properly graded and drained to a public sewer or other approved disposal system complying with the Florida Building Code, Plumbing.

Section 1208 Interior Space Dimensions

1208.2 Minimum ceiling heights.  Change Exceptions as shown.

1208.2 Minimum ceiling heights. Occupiable spaces, habitable spaces and corridors shall have a ceiling height of not less than 7 feet 6 inches (2286 mm). Bathrooms, toilet rooms, kitchens, storage rooms and laundry rooms shall be permitted to have a ceiling height of not less than 7 feet (2134 mm).

- Exceptions:

- 1.	No change.

- 2.	If any room in a building has a sloped ceiling, the prescribed ceiling height for the room is required in one-half the area thereof. Any portion of the room measuring less than 5 feet (1524 mm) from the finished floor to the ceiling shall not be included in any computation of the minimum area thereof. For accessibility provisions related to vertical clearance of areas adjoining an accessible route, refer to Section 11-4.4.2. [3916]

3.	Mezzanines constructed in accordance with Section 505.1.

Section 1209 Access to Unlocked Spaces

1209.3 Mechanical appliances.  Change to read as shown.

1209.3 Mechanical appliances.  Access to mechanical appliances installed in under-floor areas, in attic spaces and on roofs or elevated structures shall be in accordance with the Florida Building Code, Mechanical.

1210.2 Walls and partitions. Walls and partitions within 2 feet (610 mm) of urinals and water closets shall have a smooth, hard, nonabsorbent surface, to a height of 4 feet (1219 mm) above the floor, and except for structural elements, the materials used in such walls shall be of a type that is not adversely affected by moisture.

Exceptions:

1. Dwelling units and sleeping units.

2. Toilet rooms that are not accessible to the public and which have not more than one water closet.

Accessories such as grab bars, towel bars, paper dispensers and soap dishes, provided on or within walls, shall be installed and sealed to protect structural elements from moisture. For walls and partitions also see Section 2903. [3989 same as the I-code]

Chapter 13 Energy Efficiency

Chapter 13 Energy Efficiency

Revise 1301.1.1 Criteria, to read as follows:

1301.1.1 Criteria. Buildings shall be designed and constructed in accordance with the Florida Building Code, Energy Conservation..

Chapter 14 Exterior Walls

Section 1401 General

1401.1 Scope.  Change to read as shown.

- 1401.1 Scope.  The provisions of this chapter shall establish the minimum requirements for exterior walls, exterior wall coverings, exterior wall openings, exterior windows and doors, architectural trim, balconies and similar projections; and bay and oriel windows.

Exception: Buildings and structures located within the high-velocity hurricane zone shall comply with the provisions of Sections 1403.7 and 1409.

Section 1403 Performance Requirements

1403.2 Weather protection.  Change to read as shown.

1403.2 Weather protection. Exterior walls shall provide the building with a weather-resistant exterior wall envelope. The exterior wall envelope shall include flashing, as described in

Section 1405.4. The exterior wall envelope shall be designed and constructed in such a manner as to prevent the accumulation of water within the wall assembly by providing a

water-resistive barrier behind the exterior veneer, as described in Section 1404.2, and a means for draining water that enters the assembly to the exterior.  All exterior finishes shall be applied in accordance with the manufacturer’s specifications or installation instructions. Protection against condensation in the exterior wall assembly shall be provided in accordance with Section 1405.3.

Exceptions:

1. A weather-resistant exterior wall envelope shall not be required over concrete or non-pourous masonry or masonry walls designed in accordance with Chapters 19 and 21, respectively.

2 – 3 No change. [3909]  This mod put back the I-code text.

- Revise 1403.5 to read as follows:

1403.5 Flood resistance. For buildings in flood hazard areas as established in Section 1612.3, exterior walls extending below the elevation required by Section 1612.4 shall be constructed with flood damage resistant materials design flood elevation shall be resistant to water damage. Wood shall be pressure-preservative treated in accordance with AWPA U1 for the species, product and end use using a preservative listed in Section 4 of APWA U1 or decay-resistant heartwood of redwood, black locust or cedar. [4399]

- 1403.7.  Add to read as shown.

- 1403.7  In order to provide for inspection for termite infestation, clearance between exterior wall coverings and final earth grade on the exterior of a building shall not be less than 6 inches (152 mm).

- Exceptions:

- 1.	Paint or decorative cementitious finish less than 5/8 inch (17.1 mm) thick adhered directly to the masonry foundation sidewall.

- 2.	Access or vehicle ramps which rise to the interior finish floor elevation for the width of such ramps only.

- 3.	A 4-inch (102 mm) inspection space above patio and garage slabs and entry areas.

- 4.	If the patio has been soil treated for termites, the finish elevation may match the building interior finish floor elevations on masonry construction only.

5.	Masonry veneers constructed in accordance with Section 2114.2.. [3998]

[S4656]

1403.8 Drained wall assembly over mass wall assembly.   Add to read as shown.

1403.8 Drained wall assembly over mass wall assembly.   Where wood frame or other types of drained wall assemblies are constructed above mass wall assemblies, flashing or other approved drainage system shall be installed as required by Section 1405.3.

Section 1404 Materials

1404.2 Water-resistive barrier.  Change to read as shown.

1404.2 Water-resistive barrier.  Exterior walls of frame construction receiving a veneer shall be provided with a water-resistive barrier. The water-resistive barrier shall be a minimum of one layer of No. 15 asphalt felt, complying with ASTM D 226 for Type 1 felt or other approved materials, shall be attached to the sheathing, with flashing as described in Section 1405.4, in such a manner as to provide a continuous water-resistive barrier behind the exterior wall veneer.

1404.2 Water-resistive barrier. Exterior walls of frame construction receiving a veneer shall be provided with a water-resistive barrier. The water-resistive barrier shall be a minimum of one layer of No. 15 asphalt felt, complying with ASTM D 226 for Type 1 felt or other approved materials, shall be attached to the sheathing, with flashing as described in Section 1405.4, in such a manner as to provide a continuous water-resistive barrier behind the exterior wall veneer. [3912]

Section 1404.2.1 Add to read as shown:

- 1404.2.1  Where cement plaster (stucco) is to be applied to lath over frame construction, measures shall be taken to prevent bonding between the cement plaster and the water resistive barrier. A bond break shall be provided between the water resistive barrier and the cement plaster (stucco) consisting of one of the following:

- 1. Two layers of an approved water resistant barrier or

- 2. One layer of an approved water resistant barrier over an approved  plastic house wrap, or

- 3.  Other approved methods or materials applied in accordance with the manufacturer’s installation instructions.

Revise 1404.5.1 to read as follows:

1404.5.1 Aluminum siding. Aluminum siding shall conform to the requirements of AAMA 1402.

AAMA 1402, shall be modified to read as follows:

Section 1 Standard Specifications for Aluminum Siding, Soffit, and Fascia, 2.0 Siding Specifications, 2.2 Performance Criteria, 2.2.1 Windload Resistance

2.2.1.1 Static Pressure Test

able to withstand structural loading conditions which occur in 36 m/s (80 mph) wind zone areas for elevations of 10 m (33 ft) and less, which is equivalent to 1040 Pa (21.7 psf) design pressure. All siding products shall be capable of resisting the design pressures specified for walls for components and cladding loads in accordance with Section 1609.1.1. To verify that the siding will perform under these conditions, it shall be tested in accordance with Test Method #1, “Standard for Testing of Aluminum Siding/Fastener for Windload Resistance” or in an approved manner. The static test pressure shall be 780 Pa (16.3 psf). as required to demonstrate compliance with the provisions of 1609.1.

Comment after Glitch

2.2.1.1.2 For applications where the effective design pressure as specified in ASCE 7-88 Section 1609.1.1 is greater than 1040 Pa (21.7 psf) [e.g. wind zone areas greater than 36 m/s (80 mph) or elevations above 10 m (33 ft)] the product shall be tested in accordance with Test Method #1 under a static test pressure determined by the formula:

PT = 0.5 x 1.5 x DP

Where:

PT = Static Test Pressure [Pa (psf)]

DP = Design Pressure [Pa (psf)]

0.5 = Pressure Equalization Factor

1.5 = Safety Factor

NOTE: See Appendix for discussion of windloads on siding and for determination of design pressure.

2.2.1.2 Optional Criteria

In lieu of the test requirements specified in Section 2.2.1.1, siding is acceptable for use in applications where the design pressure is 1040 Pa (21.7 psf) or less and the siding is installed to solid walls with internal or external sheathing, if the metal has a minimum tensile strength of

138 MPa (20,000 psi) and conforms to the following:

Strike Table:

3.0 Soffit and Fascia Specifications, 3.2 Performance Criteria, 3.2.1 Windload Resistance

3.2.1.1 Static Pressure Test

3.2.1.1.1 All soffit products shall be able to withstand structural loading conditions which occur in 36 m/s (80 mph) wind zone areas for elevations of 10 m (33 ft) and less, which is equivalent to 1040 Pa (21.7 psf) design pressure. capable of resisting the design pressures specified for walls for components and cladding loads in accordance with Section 1609.1.1. To verify that the soffit will perform under these conditions, it shall be tested in the maximum unsupported length for which the manufacturer seeks

conformance when tested in accordance with Test Method #4, “Standard for Testing of Soffits and Windload Resistance.”

The static test pressure shall be 780 Pa (16.3 psf). as required to demonstrate compliance with the provisions of Section 1609.1.

NOTE: See Appendix for discussion of windloads on soffits.

3.2.1.1.2 For applications where the effective design pressure as specified in ASCE 7-88 Section 1609.1.1 is greater than 1040 Pa (21.7 psf) [e.g. wind zone areas greater than 36 m/s (80 mph) or elevations above 10 m (33 ft)] the product shall be tested in accordance with Test Method #4 under a static test pressure determined by the formula:

PT = 0.5 x 1.5 x DPp

Where:

PT        = Static Test Pressure [Pa (psf)]

DPp      = Design Pressure [Pa (psf)]

0.5       = Pressure Equalization Factor

1.5       = Safety Factor

NOTE: See Appendix for discussion of wind loads on soffits and for determination of design pressure.

Section 3, Appendix, Windload Criteria is deleted in its entirety. [4466]

1404.9 Vinyl siding.  Change to read as shown.

1404.9 Vinyl siding and Soffit. Vinyl Siding and sofitt shall conform to the requirements of ASTM D 3679, ASTM D 4477 and the manufacturer’s installation instructions. [3913]

1404.9.1 Labeling. Vinyl siding shall be labeled as conforming to the requirements of ASTM D 3679.

1404.9.1  Labeling.  Add to read as shown.

1404.9.1  Labeling. Vinyl siding shall be labeled as conforming to the requirements of ASTM D 3679.

1404.9.2 Manufactured soffit materials and systems shall be labeled in accordance with the provisions of Section 1715.9 of this code. [3856]

1404.10 Fiber cement siding. Fiber cement siding shall conform to the requirements of ASTM C 1186 and shall be so identified on labeling listing an approved quality control agency.

1404.10 Fiber-cement siding. Fiber-cement siding shall conform to the requirements of ASTM C 1186, Type A, and shall be so identified on labeling listing an approved quality control agency.  [3914]  Note:  same text as the I-Code.

Section 1405 Installation of Wall Coverings

1405.4.2 Masonry. Flashing and weep holes in anchored veneer shall be located in the first course of masonry above finished ground level above the foundation wall or slab, and other points of support, including structural floors, shelf angles and lintels where anchored veneers are designed in accordance with Section 1405.5 1405.6. [3999] Note:  same text as the I-Code.

1405.5 Wood veneers. Wood veneers on exterior walls of buildings of Type I, II, III and IV construction shall be not less than 1 inch (25 mm) nominal thickness, 0.438-inch (11.1 mm) exterior hardboard siding or 0.375-inch (9.5 mm) exterior-type wood structural panels or particleboard and shall conform to the following:

1. The veneer shall not exceed 40 feet (1219 mm) in height above grade. Where fire-retardant-treated wood is used, the height shall not exceed 60 feet (1829 mm) in height above grade.

2. The veneer is attached to or furred from a noncombustible backing that is fire-resistance rated as required by other provisions of this code.

3. Where open or spaced wood veneers (without concealed spaces) are used, they shall not project more than 24 inches (610 mm) from the building wall. [4000] Note:  same text as the I-Code.

Revise 1405.6.2 to read as follows:

1405.6.2 Seismic requirements.  Reserved

1405.6.2 Wind requirements. Sections 6.2.2.1 and 6.2.2.11 of TMS 402/ACI 530/ASCE 5 shall be modified as followed

6.2.2.1 Except as provided in Section 6.2.2.11, prescriptive requirements for anchored masonry veneer

shall not be used in areas where the basic wind speed exceeds 130 mph (177 km/hr) as given in ASCE 7.

6.2.2.11 Requirements in areas of high winds — The following requirements apply in areas where the basic wind speed, as given in ASCE 7, exceeds 130 mph (177 km/hr) but does not exceed 150 mph (209 km/hr) and the building’s mean roof height is less than or equal to 60 ft (18.3 m):

(a) Reduce the maximum wall area supported by each anchor to 70 percent of that required in Sections 6.2.2.5.6.1 and 6.2.2.5.6.2.

(b) Space anchors at a maximum 18 in. (457 mm) horizontally and vertically.

(c) Provide additional anchors around openings larger than 16 in. (406 mm) in either direction. Space anchors around perimeter of opening at a maximum of 24 in. (610 mm) on center. Place anchors within 12 in. (305 mm) of openings. [4215]

1405.9 Terra cotta.  Add to read as follows:

1405.9 Terra cotta. Anchored terra cotta or ceramic units not less than 15/8 inches (41 mm) thick shall be anchored directly to masonry, concrete or stud construction. Tied terra cotta or ceramic veneer units shall be not less than 15/8 inches (41 mm) thick with projecting dovetail webs on the back surface spaced approximately 8 inches (203 mm) o.c....these anchors shall be secured to 1/4-inch (6.4 mm) corrosion-resistant pencil rods that pass through the vertical aligned loop anchors in the backing wall. The veneer ties shall have sufficient strength to support the full weight of the veneer in tension. The facing shall be set with not less than a 2-inch (51 mm) space from the backing wall and the space shall be filled solidly with portland cement grout and pea gravel. Immediately prior to setting, the backing wall and the facing shall be drenched with clean water and shall be distinctly damp when the grout is poured. [4001]  Note:  same as the I-Code

1405.10 Adhered masonry veneer.  Add to read as follows:

1405.10 Adhered masonry veneer. Adhered masonry veneer shall comply with the applicable requirements of Section 1405.10.1 and Sections 6.1 and 6.3 of TMS 402/ACI 530/ASCE 5. [4002]  Note:  same as the I-Code

1405.11.4 Grounding.  Change to read as shown.

1405.11.4 Grounding.  Grounding of metal veneers on buildings shall comply with the requirements of Chapter 27 of this code. [4003]

1405.14 Vinyl siding.  Change to read as shown.

1405.14 Vinyl siding. Vinyl siding conforming to the requirements of this section and complying with ASTM D 3679, and ASTM D 4477 in accordance with the manufacturer’s installation instructions shall be permitted on exterior walls of buildings located in areas

where the Vasd as determined in accordance with Section 1609.3.1 basic wind speed specified in Chapter 16 does not exceed 100 miles per hour (45 m/s) and the building height is less than or equal to 40 feet (12 192 mm) in Exposure C. Where construction is located in areas where the  Vasd as determined in accordance with Section 1609.3.1 basic wind speed exceeds 100 miles per hour (45 m/s), or building heights are in excess of 40 feet (12 192 mm), tests or calculations indicating compliance with Chapter 16 shall be submitted. Vinyl siding shall be secured to the building so as to provide weather protection for the exterior walls of the building. [4215]

1405.14.1 Application. The siding shall be applied over sheathing or materials listed in Section 2304.6. Siding shall be applied to conform with the water-resistive barrier requirements in Section 1403. ....Unless otherwise specified in the approved manufacturer's instructions, nails used to fasten the siding and accessories shall have a minimum 0.313-inch (7.9 mm) head diameter and 1/8-inch (3.18 mm) shank diameter. The nails shall be corrosion resistant and shall be long enough to penetrate the studs or nailing strip at least 3/4 inch (19 mm). Where the siding is installed horizontally, the fastener spacing shall not exceed 16 inches (406 mm) horizontally and 12 inches (305 mm) vertically. Where the siding is installed vertically, the fastener spacing shall not exceed 12 inches (305 mm) horizontally and 12 inches (305 mm) vertically. [4004}

Note: same as the I-Code.

Revise 1408.6 as follows:

1408.6 Special inspection. Reserved.

Section 14098 High-Velocity Hurricane Zone Other Materials.  Add to read as shown.

14098.1 Wood.

14098.1.1 Wood and wood products used for wall claddings shall comply with Section 2314 through 2330.

14098.1.2 Wood and wood-products used for wall cladding as non-structural exterior trim, fascia and soffits on buildings of Type I, II-A and IV. Construction may be applied to the outside of exterior walls, cornices, architectural appendages, eaves overhangs and similar projections.

Where an exterior wall is required to be fire resistive, such material shall be separated from the interior of the building by the vertical extension of the exterior wall.

14098.2 Asphalt shingles. Asphalt shingles shall be applied only to solid wood sheathing and shall be in tin-capped and spot-stuck, as set forth in Sections 1512 through 1525.

14098.3 Roll slate or felt. Roll slate or felt shall be applied only to solid wood sheathing and shall be secured by nailing, as set forth in Chapter 15, High-Velocity Hurricane Zones.

14098.4 Metal shingles. Metal shingles shall be applied only to solid wood sheathing and shall be secured as set forth in Chapter 15 (High-Velocity Hurricane Zone).

14098.5 Steel shingles. Steel Siding shall be designed and applied as set forth in Sections 2214 through 2224.

14098.6 Aluminum siding. Aluminum siding shall be designed and applied as set forth in Section 2003.

14098.7 Veneers. Masonry veneers shall be applied as set forth in Sections 2118 through 2122.

14098.8 Combustible materials. Combustible materials and fire resistive characteristics of all materials shall comply with the requirements for the group of occupancy or type of construction, and the required interior finish rating.

14098.9 Other materials. Any cladding materials or assembly not addressed in this code shall be classified by the building official as the one it most nearly resembles, and shall comply with the requirements for loading and fire resistance herein required for such materials and assemblies.

Chapter 15 Roof Assemblies and Rooftop Structures

Section 1501 General.

1501.1 Scope.  Change to read as shown.

1501.1 Scope.  The provisions of this chapter shall govern the design, materials, construction and quality of roof assemblies, and rooftop structures.

Exception: Buildings and structures located within the high-velocity hurricane zone shall comply with the provisions of Section 1503.6 and Sections 1512 through 1525.

Section 1502 Definitions

Section 1502.1 Roof section.  Add to read as shown.

Building Integrated Photovoltaic Roofing.  A roofing product consisting of electricity generating photovoltaic component integrated into a roof covering. (4162)

ROOF SECTION – A separation or division of a roof area by existing joints, parapet walls, flashing (excluding valleys), difference of elevation (excluding hips and ridges), roof type or legal description; not including the roof area required for a proper tie-off with an existing system.

Section 1503 Weather Protection

Table 1503.2 Metal Flashing Material.  Add to read as shown:

### TABLE 1503.2

METAL FLASHING MATERIAL

| MATERIAL | MINIMUM THICKNESS (INCHES) | GAGE | WEIGHT (lbs per sq ft) |
| --- | --- | --- | --- |
| Copper |  |  | 1 (16 oz) |
| Aluminum | 0.024 |  |  |
| Stainless Steel |  | 28 |  |
| Galvanized Steel | 0.0179 | 26 (zinc coated G90) |  |
| Aluminum Zinc Coated Steel | 0.0179 | 26 (AZ50 Alum Zinc) |  |
| Zinc Alloy | 0.027 |  |  |
| Lead |  |  | 2.5 (40 oz) |
| Painted Terne | ----- |  | 1.25 (20 oz) |

1503.2.1 Locations.  Change to read as shown.

1503.2.1 Locations.  Flashing shall be installed at wall and roof intersections, at gutters, wherever there is a change in roof slope or direction, and around roof openings. Where flashing is of metal, the metal shall be corrosion resistant with a thickness not less than provided in Table 1503.2.

Exception:  This requirement does not apply to hip and ridge junctions

Section 1503.3 Coping.  Change text to read as shown:

1503.3 Coping. Parapet walls shall be properly coped or sealed with noncombustible, weatherproof materials of a width no less than the thickness of the parapet wall.  Metal coping shall comply with ANSI/SPRI ES-1 or RAS 111.

Section 1503.4 Roof drainage.  Change text to read as shown:

1503.4 Roof drainage. Unless roofs are sloped to drain over roof edges, design and installation of roof drainage systems shall comply with Section 1503 and the Florida Building Code, Plumbing,  Chapter 11.

1503.4.2 Scupper.  Where required for roof drainage, a scupper shall be placed level with the roof surface in a wall or parapet.  The scupper shall be located as determined by the slope and the contributing area of the roof. The exterior facing or lining of a scupper, if metal, shall be the same as flashing material required by Sections 1503 through 1510 for the particular type of covering specified for the building.  For other type materials, follow manufacturer’s specifications.

1503.4.2.1 Overflow scuppers.  Add to read as shown.

1503.4.2.1  Overflow scuppers.  When other means of drainage of overflow water is not provided, overflow scuppers shall be placed in walls or parapets not less than 2 inches (51 mm) nor more than 4 inches (102 mm) above the finished roof covering and shall be located as close as practical to required vertical leaders or downspouts or wall and parapet scuppers. An overflow scupper shall be sized in accordance with the Florida Building Code, Plumbing.

Section 1503.5 Roof ventilation.  Change to read as shown:

1503.5 Roof ventilation. Attic ventilation shall be provided in accordance with Section 1203.2 and the manufacturer’s installation instructions.

Section 1503.6 Crickets or saddles.  Change to read as shown.

1503.6 Crickets or saddles.  A cricket or saddle shall be installed on the ridge side of any chimney or penetration greater than 30 inches (762 mm) wide as measured perpendicular to the slope.  Cricket or saddle coverings shall be sheet metal or of the same material as the roof covering.

Exception:  Any penetration that allows water to flow around it shall not require a cricket or saddle.

1503.6 Crickets and saddles. A cricket or saddle shall be installed on the ridge side of any chimney or penetration greater than 30 inches (762 mm) wide as measured perpendicular to the slope. Cricket or saddle coverings shall be sheet metal or of the same material as the roof covering. {3983}

1503.7 Protection against decay and termites.  Add to read as shown.

1503.7 Protection against decay and termites.  Condensate lines and roof downspouts shall discharge at least 1 foot (305 mm) away from the structure sidewall, whether by underground piping, tail extensions, or splash blocks. Gutters with downspouts are required on all buildings with eaves of less than 6 inches (152 mm) horizontal projection except for gable end rakes or on a roof above another roof.

Section 1504 Performance Requirements

Section 1504.1.1 Wind resistance of asphalt shingles.  Change text to read as shown:

1504.1.1 Wind resistance of asphalt shingles. Asphalt shingles shall be designed for wind speeds in accordance with Section 1507.2.7.

Section 1504.3.2 Metal panel roof systems.  Change to read as shown.

1504.3.2 Metal panel roof systems. Metal panel roof systems through fastened or standing seam shall be tested in accordance with UL 580 or ASTM E 1592 or TAS 125.

Exception: Metal roofs constructed of cold-formed steel, where the roof deck acts as the roof covering and provides both weather protection and support for structural loads, shall be permitted to be designed and tested in accordance with the applicable referenced structural design standard in Section 2209.1.

Section 1504.5 Edge securement for low-slope roofs.  Change text to read as shown:

1504.5 Edge securement for low-slope roofs. Low-slope membrane roof systems metal edge securement, except gutters, shall be designed and installed for wind loads in accordance with Chapter 16 and tested for resistance accordance with ANSI/SPRI ES-1 or RAS 111 except the basic wind speed shall be determined from Figure 16091609A, 1609B, or 1609C as applicable.

(4217).

1504.6 Physical properties.  Change to read as shown.

1504.6 Physical properties.  Roof coverings installed on low-slope roofs (roof slope < 2:12) in accordance with Section 1507 shall demonstrate physical integrity over the working life of the roof based upon 2,000 hours of exposure to accelerated weathering tests conducted in accordance with ASTM G 152, ASTM G 153, ASTM G 155 or ASTM G 154. Those roof coverings that are subject to cyclical flexural response due to wind loads shall not demonstrate any significant loss of tensile strength for unreinforced membranes or breaking strength for reinforced membranes when tested as herein required.

1504.7 Impact Resistance. Roof coverings installed on low-slope roofs ( roof slope < 2:12 ) in accordance with Section 1507 shall resist impact damage based on the results of tests conducted in accordance with ASTM D 3746, ASTM D 4272, CGSB 37-GP-52M or the “Resistance to Foot Traffic Test” in Section 5.5 of FM 4470. All structural metal roofing systems having a thickness equal to or greater than 22 gage and, all non-structural metal roof systems having a thickness equal to or greater than 26 gage shall be exempt from the tests listed above.

Section 1504.8 Aggregate, revise text to read as follows.

1504.8 Aggregate.  Aggregate shall be permitted as roof surfacing when installed on slopes of 3:12 or less, not less than 400 pound (182 kg) of roofing gravel or 300 pounds (145 kg) of slag per square shall be applied. A minimum of 50 percent of the total aggregate shall be embedded in the flood coat of bitumen or installed in accordance with its product approval. Aggregate shall be dry and free from dirt and shall be in compliance with the sizing requirements set forth in ASTM D 1863. A building official may request a test to confirm compliance with these requirements

Table 1504.8, Maximum Allowable Mean roof Height Permitted for Buildings with Aggregate  on the Roof in Areas outside a Hurricane-Prone Region, change to read as follows:

Table 1504.8, Maximum Allowable Mean roof Height Permitted for Buildings with Aggregate on the Roof in Areas outside a Hurricane-Prone Region.  Reserved.

Section 1504.9 Margin of safety.  Add to read as shown.

1504.9 Margin of Safety. A margin of safety of 2:1 shall be applied to all wind uplift resistance test results except when a margin of safety is specified in the test standard.

Exception: Asphalt shingles testing resulting in a miles per hour rating as required in Section 1507.2.7.

Section 1505 Fire Classification

Section 1505.7 Special purpose roofs.  Change to read as shown:

1505.7 Special purpose roofs.  Reserved.

1505.8 Photovoltaic systems. Rooftop installed photovoltaic systems that are adhered or attached to the roof covering or photovoltaic modules/shingles installed as roof coverings shall be labeled to identify their fire classification in accordance with the testing required in Section 1505.1. {4170}

Section 1506 Materials

Section 1506.5 Add a new section to read as shown:

1506.5 Nails. Nails shall be corrosion resistant nails conforming to ASTM F 1667.  The corrosion resistance shall meet ASTM A 641, Class 1 or an equal corrosion resistance by coating, electro galvanization, mechanical galvanization, hot dipped galvanization, stainless steel, nonferrous metal and alloys or other suitable corrosion resistant material.

Section 1506.6 Screws.  Add a new section to read as shown.

1506.6 Screws.  Wood screws conform to ANSI/ASME B 18.6.1.  Screws shall be corrosion resistant by coating, galvanization, stainless steel, nonferrous metal or other suitable corrosion resistant material.  The corrosion resistance shall be demonstrated through one of the following methods:

1.  Corrosion resistance equivalent to ASTM A 641, Class 1. or

2.  Corrosion resistance in accordance with TAS114, Appendix E. or

3.  Corrosion resistant coating exhibiting not more than 5% red rust after 1000 hours exposure in accordance with ASTM B 117.

Section 1506.7 Clips.  Add to read as shown.

1506.7 Clips.  Clips shall be corrosion resistant clips.  The corrosion resistance shall meet  0.90 oz per sq ft  (0.458 kg/m2) measured according to ASTM A 90/A 90M, TAS 114 Appendix E  or an equal corrosion resistance coating, electro galvanization, mechanical galvanization, hot dipped galvanization, stainless steel, nonferrous metals and alloys or other suitable corrosion resistant material.  Stainless steel clips shall conform to ASTM A167, Type 304.

Section 1507 Requirements for Roof Coverings

Section 1507.2.3 Underlayment, revise text to read as follows.

1507.2.3 Underlayment. Unless otherwise noted, required underlayment shall conform to ASTM D 226, Type I or Type II, or ASTM D 4869 Type I or Type II, or ASTM D 6757.

Revise 1507.2.5 to read as follows:

1507.2.5 Asphalt shingles. Asphalt shingles shall comply with ASTM D 225 or ASTM D 3462.

1507.2.5 Asphalt shingles. Asphalt shingles shall have self-seal strips or be interlocking and comply with ASTM D 225 or ASTM D 3462. Shingles shall also comply with Table 1507.2.7.1. Asphalt shingle packaging shall bear labeling indicating compliance with one of the required classifications as shown in Table 1507.2.7.1 or a listing by an approved testing agency in accordance with the requirements of Section 1609.5.2.

[R4657]

1507.2.6.1  Add to read as shown.

1507.2.6.1  The nail component of plastic cap nails shall meet the corrosion resistance requirements of  section 1507.2.6.

Section 1507.2.7.1, revise as follows:

1507.2.7.1 Wind Resistance of Asphalt Shingles. Asphalt Shingles shall be classified in

accordance with ASTM D3161, TAS 107 or ASTM D7158 in accordance with Table 1507.2.7.1 to resist the basic wind speed per Figure 1609. Shingles classified as ASTM D 3161 Class D or ASTM D 7158 Class G are acceptable for use in the 100‐mph wind zone. Shingles classified as ASTM D3161 Class F, TAS107 or ASTM D 7158 Class H are acceptable for use in all wind zones. Asphalt shingle wrappers shall indicate compliance with one of the required classifications as shown in Table 1507.2.7.1.

Exception: Asphalt shingles not included in the scope of ASTM D 7158 shall be tested and

labeled to indicate compliance with ASTM D 3161 and the required classification in Table

1507.2.7.1(2).

Comment after Glitch

Revise Table 157.2.7.1 to read as follows:

Table 1507.2.7.1

Wind Resistance of Asphalt Shingles

| Classification of Asphalt Shingles |  |  |  |
| --- | --- | --- | --- |
| Maximum Basic Wind Speed, Vult From Figure 1609A, B, C or ASCE-7 | Vasd | ASTM D 7158 | ASTM D 3161 |
| 130 110 | 85 | D, G or H | A, D or F |
| 140 116 | 90 | D, G or H | A, D or F |
| 150 129 | 100 | G or H | A, D or F |
| 160 142 | 110 | G or H | F |
| 170 155 | 120 | G or H | F |
| 180 168 | 130 | H | F |
| 190 181 | 140 | H | F |
| 200 194 | 150 | H | F |

Comment after Glitch, R4657

1507.2.8.2 Ice Barrier .  Change to read as shown.

1507.2.8.2 Ice Barrier .  Reserved.

1507.2.9.1 Base and cap flashing.  Change to read as shown.

1507.2.9.1 Base and counter flashing.  Base and counter flashing shall be installed as follows:

1. In accordance with manufacturer’s installation instructions, or

2. A continuous metal minimum 4” x 54” “L” flashing shall be set in approved flashing cement and set flush to base of wall and over the underlayment. Both horizontal and vertical metal flanges shall be fastened 6 inches (152 mm) on center with approved fasteners. All laps shall be a minimum of 4 inches (102 mm) fully sealed in approved flashing cement. Flashing shall start at the lower portion of roof to insure water-shedding capabilities of all metal laps. The entire edge of the horizontal flange shall be sealed covering all nail penetrations with approved flashing cement and membrane. Shingles will overlap the horizontal flange and shall be set in approved flashing cement.

Base flashing shall be of either corrosion resistant metal with a minimum thickness provided in Table 1503.2 or mineral surface roll roofing weighing a minimum of 77 pounds per 100 square feet (3.76 kg/m2). Counter flashing shall be corrosion resistant metal with a minimum thickness provided in Table 1503.2. {3625}

Section 1507.2.9.2 Change text to read as shown:

1507.2.9.2 Valleys. Valley linings shall be installed in accordance with the manufacturer’s instructions before applying shingles. Valley linings of the following types shall be permitted:

1.	For open valleys (valley lining exposed) lined with metal, the valley lining shall be at least 2416 inches (406610 mm) wide and of any of the corrosion-resistant metals in Table 1503.2. {3809}

2.	For open valleys, valley lining of two plies of mineral-surfaced roll roofing complying with ASTM D 6380 Class M or ASTM D 3909 shall be permitted. The bottom layer shall be 18 inches (457 mm) and the top layer a minimum of 36 inches (914 mm) wide.

3.	For closed valleys, valley lining of one ply of smooth roll roofing complying with ASTM D 6380 Class S and at least 36 inches (914 mm) wide or types as described in Items 1 or 2 above shall be permitted. Specialty underlayment complying with ASTM D 1970 may be used in lieu of the lining material.

Table 1507.2.9.2 Valley Lining Material.  Change to read as shown.

Table 1507.2.9.2 Valley Lining Material.  Reserved.

Section 1507.2.9.3 Drip edge.  Change text to read as shown:

1507.2.9.3 Drip edge. Provide drip edge at eaves and gables of shingle roofs. Overlap to be a minimum of 23 inches (5176 mm). Eave drip edges shall extend ½ inch (13 mm) below sheathing and extend back on the roof a minimum of 2 inches (51 mm). Drip edge at eaves shall be permitted to be installed either over or under the underlayment.  If installed over the underlayment, there shall be a minimum 4 inches (51 mm) width of roof cement installed over the drip edge flange.  Drip edge shall be mechanically fastened a maximum of 12 inches (305 mm) on center. Where the Vasd as determined in accordance with Section 1609.3.1 basic wind speed per Figure 1609 is 110 mph (177 km/h) or greater or the mean roof height exceeds 33 feet (10 058 mm), drip edges shall be mechanically fastened a maximum of 4 inches (102 mm) on center. {3810, 4217}

1507.2.7 Revise to read:

1507.2.7 Attachment. Asphalt shingles shall have the minimum number of fasteners required by the manufacturer and Section 1504.1.  Asphalt shingles shall be secured to the roof with but with not less than four fasteners per strip shingle or two fasteners per individual shingle. Where the roof slope exceeds 21 units vertical in 12 units horizontal (21:12), asphalt shingles shall be installed in accordance with as required by the manufacturer’s printed installation instructions for steep-slope roof applications.

Section 1507.2.7.1 revise to read as shown:

1507.2.7.1 Wind Resistance of Asphalt Shingles.  Asphalt Shingles shall be classified in accordance with ASTM D3161, TAS 107 or ASTM D7158 to resist the basic wind speed per Figure 1609 in accordance with Table 1507.2.7.1. Shingles classified as ASTM D 3161 Class D or ASTM D 7158   Class G are acceptable for use in the 100-mph wind zone. Shingles classified as ASTM D3161 Class F, TAS107 or ASTM D 7158 Class H are acceptable for use in all wind zones.  Asphalt shingle wrappers shall indicate compliance with one of the required classifications as shown in Table 1507.2.7.1.

Table 1507.2.7.1(1) revise table to read as shown:

Table 1507.2.7.1

Wind Resistance of Asphalt Shingles

| Maximum Basic Wind Speed MPH (per Figure 1609) Vasd AS DETERMINED IN ACCORDANCE WITH SECTION 1609.3.1 | Classification |
| --- | --- |
| 100 | ASTM D3161 Class D or ASTM D 7158 Class G or TAS 107 |
| 110 | ASTM D3161 Class F or ASTM D 7158 Class G or TAS 107 |
| 120 | ASTM D3161 Class F or ASTM D 7158 Class G or TAS 107 |
| 130 | ASTM D3161 Class F or ASTM D 7158 Class H or TAS 107 |
| 140 | ASTM D3161 Class F or ASTM D 7158 Class H or TAS 107 |
| 150 | ASTM D3161 Class F or ASTM D 7158 Class H or TAS 107 |

(4217)

Table 1507.2.7.1(2) Classification of Asphalt Shingles per ASTM D 3161, Revise as follows:

Table 1507.2.7.1(2).  Reserved

1507.2.8.1 High wind attachment. Underlayment applied in areas subject to high winds (Vasd greater than 110 mph as determined in accordance with Section 1609.3.1 in accordance with Figure 1609) shall be applied with corrosion-resistant fasteners in accordance with the manufacturer’s instructions. Fasteners are to be applied along the overlap at a maximum spacing of 36 inches (914 mm) on center. (4217)

1507.3.1 Deck requirements.  Change to read as shown.

1507.3.1 Deck requirements.  Concrete and clay tile shall be installed only over solid sheathing except where the roof covering is specifically designed and tested in accordance with Section 1609.5.2 to be applied over structural spaced sheathing boards.

1507.3.2 Deck slope.  Change to read as shown.

1507.3.2 Deck slope. Concrete and clay roof tile shall be installed in accordance with the recommendations of FRSA/RTI 07320 TRI 07320 where the Vasd as determined in accordance with Section 1609.3.1 or the recommendations of RAS 118, 119 or 120.{4183}

Section 1507.3.3 Underlayment.  Change text to read as shown:

1507.3.3 Underlayment. Unless otherwise noted, required underlayment shall conform to: ASTM D 226, Type II; ASTM D 2626; ASTM D 1970 or ASTM D 6380 mineral-surfaced roll roofing.  Underlayment shall be applied according to the tile manufacturer’s installation instructions or the recommendations of the FRSA/TRI 07320 where the basic wind speed, Vasd, is determined in accordance with Section 1609.3.1 or the recommendations of RAS 118, 119 or 120..{3824}

Section 1507.3.3.1 Low slope roofs.  Change to read as shown.

1507.3.3.1  Slope and underlayment requirements.  Refer to FRSA/TRI 07320 manual where the basic wind speed, Vasd, is determined in accordance with Section 1609.3.1 for underlayment and slope requirements for specific roof tile systems. . or the recommendations of RAS 118, 119 or 120.

{3825}

Section 1507.3.3.2 High-slope roofs.  Change the section to read as shown:

1507.3.3.2 High-slope roofs. Reserved.

Section 1507.3.6 Fasteners.  Change to read as shown.

1507.3.6 Fasteners.  Tile fasteners shall be corrosion resistant and not less that 11 gage, 5/16-inch (8.0 mm) head, and of sufficient length to penetrate the deck a minimum of 0.75 inch (19.1 mm) or through the thickness of the deck, which-ever is less or in accordance with the FRSA/TRI 07320 manual . or where the basic wind speed, Vasd, is determined in accordance with Section 1609.3.1 or in accordance with RAS 118, 119 or 120. Attaching wire for clay or concrete tile shall not be smaller than 0.083 inch (2.1 mm).  Perimeter fastening areas include three tile courses but not less that 36 inches (914 mm) from either side of hips or ridges and edges of eaves and gable rakes.   {3826}

1507.3.7 Attachment. Change to read as shown.

1507.3.7 Attachment. Clay and concrete roof tiles shall be fastened in accordance with Section 1609 or in accordance with FRSA/TRI 07320 Installation Manual where the basic wind speed, Vasd, is determined in accordance with Section 1609.3.1

Table 1507.3.7. Reserved.

1507.3.8 Application.  Change to read as shown.

1507.3.8 Application.  Tile shall be applied according to the manufacturer’s installation instructions or recommendations of the FRSA/TRI 07320 where the basic wind speed, Vasd, is determined in accordance with Section 1609.3.1 or the recommendation of or RAS 118, 119 or 120.{3828}

1507.3.9 Flashing.  Change to read as shown.

1507.3.9 Flashing.  At the juncture of the roof vertical surfaces, flashing and counterflashing shall be provided in accordance with the manufacturer’s installation instructions or the recommendations of the FRSA/TRI 07320 Manual . where the basic wind speed, Vasd, is determined in accordance with Section 1609.3.1 or the recommendation of or RAS 118, 119 or 120.{3929}

[R4857]

Table 1507.4.3 Metal Roof Coverings.  Change to read as shown.

TABLE 1507.4.3(1) METAL ROOF COVERINGS

TABLE 1507.4.3(1)

METAL ROOF COVERINGS

| ROOF COVERING TYPE | STANDARD | STANDARD APPLICATION RATE/THICKNESS |
| --- | --- | --- |
| Aluminum | ASTM B 209 | 0.024 inch minimum thickness for roll-formed panels and 0.019 inch minimum thickness for press-formed shingles. |
| Aluminum-zinc coated steel | ASTM A 792 | 0.013 inch minimum thickness, AZ 50 (coated minimum application rate) |
| Cold-rolled copper | ASTM B 370 | Minimum 16 oz/sq. ft. and 12 oz./sq. ft. high yield copper for metal-sheet roof covering systems: 12 oz/sq. ft. for preformed metal shingle systems. |
| Copper | ASTM B 370 | 16 oz./sq. ft. for metal-sheet roof-covering systems; 12 oz./sq. ft. for preformed metal shingle systems. |
| Galvanized steel | ASTM A 653 | 0.013 inch minimum thickness, G-90 zinc-coateda |
| Hard lead |  | 2 lbs./sq. ft. |
| Lead-coated copper | ASTM B 101 |  |
| Prepainted steel | ASTM A 755 |  |
| Soft lead |  | 3 lbs./sq. ft. |
| Stainless steel | ASTM A 240 | 300 Series Alloys |
| Steel | ASTM A 924/ ASTM A 924M |  |
| Terne and terne-coated stainless |  | Terne coating of 40 lbs. per double base box, field painted where applicable in accordance with manufacturer’s installation instructions. |
| Zinc |  | 0.027 inch minimum thickness; 99.995% electrolytic high grade zinc with alloy additives of copper (0.08% - 0.20%), titanium (0.07% - 0.12%) and aluminum (0.015%). |

For SI: 1 ounce per square foot = 0.0026 kg/m2, 1 pound per square foot = 4.882 kg/m2, 1 inch = 25.4 mm, 1 pound = 0.454 kg.

a. For Group U buildings, the minimum coating thickness for ASTM A 653 galvanized steel roofing shall be G.

1507.4.4 Attachment.  Change to read as shown.

1507.4.4 Attachment. Metal roof panels shall be secured to the supports in accordance with the approved manufacturer’s fasteners. In the absence of manufacturer recommendations, the following fasteners shall be used:

1. Galvanized fasteners shall be used for steel roofs.

2. Copper, brass, bronze, copper alloy or 300 series stainless-steel fasteners shall be used for copper roofs.

3.  Aluminum-zinc coated fasteners are acceptable for aluminum-zinc coated roofs.

4. Stainless-steel fasteners are acceptable for all types of metal roofs.

1507.4.5 Underlayment.  Add to read as shown.

1507.4.5 Underlayment.  Underlayment shall be installed as per manufacturer’s installation guidelines.

1507.5.2.1  Add to read as shown.

1507.5.2.1  Underlayment shall be installed as per manufacturer’s installation guidelines.

Section 1507.5.3 Underlayment.  Change to read as shown.

1507.5.3 Underlayment. Underlayment shall comply with ASTM D 226, Type I or Type II or ASTM D 1970 or ASTM D 4869.

1507.5.4 Ice barrier.  Change to read as shown.

1507.5.4 Ice barrier.  Reserved.

Section 1507.5.7 Flashing, revise text to read as follows:

1507.5.7 Flashing. Roof valley flashing shall be of corrosion-resistant metal of the same material as the roof covering or shall comply with the standards in Table 1507.4.3(1). The valley flashing shall extend at least 8 inches (203 mm) from the centerline each way and shall have a splash diverter rib not less than 0.75 inch (19.1 mm) high at the flow line formed as part of the flashing. Sections of flashing shall have an end lap of not less than 4 inches (102 mm).

1507.6.3 Underlayment.  Change to read as shown.  Overlap exists, needs determination.

1507.6.3 Underlayment. Underlayment shall comply with ASTM D 226, Type I or Type II or ASTM D 1970 or ASTM D 4869.

1507.6.4 Ice barrier.  Change to read as shown.

1507.6.4 Ice barrier.  Reserved.

Section 1507.6.5 Material standards.  Change text to read as shown:

1507.6.5 Material standards. Mineral-surfaced roll roofing shall conform to ASTM D 6380 Class M or Class WS or ASTM D 3909.

Section 1507.7.3 Underlayment, revise text to read as follows:

1507.7.3 Underlayment. Underlayment shall comply with ASTM D 226, Type II or ASTM D 4869 Type II.

1507.7.4 Ice barrier.  Change to read as shown.

1507.7.4 Ice barrier.  Reserved.

1507.7.7 Flashing.  Change to read as shown.

1507.7.7 Flashing.  Flashing and counter flashing shall be made with sheet metal. Valley flashing shall be a minimum of 16 inches (381 mm) wide.Valley and flashing metal shall be a minimum thickness provided in Table 1503.2 nonferrous metal or stainless steel.

Table 1507.8 Wood Shingle and Shake Installation.  Change text to read as shown:

WOOD SHINGLE AND SHAKE INSTALLATION

| ROOF ITEM | WOOD SHINGLES | WOOD SHAKES |
| --- | --- | --- |
| 1. Roof slope | Wood shingles shall be installed on slopes of three units vertical in 12 units horizontal (3:12) or greater. | Wood shakes shall be installed on slopes of four units vertical in 12 units horizontal (4:12) or greater. |
| 2. Deck requirement |  |  |
| Temperate climate | Shingles shall be applied to roofs with solid or spaced sheathing. Where spaced sheathing is used, sheathing boards shall not be 4 less than 1" × 4" nominal dimensions and shall be spaced on center equal to the weather exposure to coincide with the placement of fasteners. | Shakes shall be applied to roofs with solid or spaced sheathing. Where spaced sheathing is used, sheathing boards shall not be less than 1" × 4" nominal dimensions and shall be spaced on center equal to the weather exposure to coincide with the placement of fasteners. When 1" × 4" spaced sheathing is installed at 10 inches, boards must be installed between the sheathing boards. |
| 3. Interlayment | No requirements. | Interlayment shall comply with ASTM D 226, Type 1. |
| 4. Underlayment |  |  |
| Temperate climate | Underlayment shall comply with ASTM D 226, Type 1. | Underlayment shall comply with ASTM D 226, Type 1. |
| 5. Application |  |  |
| Attachment | No change | No change |
| No. of fasteners | No change | No change |
| Exposure | No change | No change |
| Method | No change | No change |
| Flashing | In accordance with Section 1507.8.8. | In accordance with Section 1507.9.9. |

1507.8.1.1 Solid sheathing required.  Change to read as shown.

1507.8.1.1 Solid sheathing required.  Reserved.

Section 1507.8.3 Underlayment, revise text to read as follows:

1507.8.3 Underlayment. Underlayment shall comply with ASTM D 226, Type I or ASTM D 4869 Type I.

1507.8.4 Ice barrier.  Change to read as shown.

1507.8.4 Ice barrier.  Reserved.

Section 1507.8. 8 Flashing, revise text to read as follows:

1507.8. 8 Flashing. At the juncture of the roof and vertical surfaces, flashing and counterflashing shall be provided in accordance with the manufacturer’s installation instructions, and where of metal, shall comply with Table 1503.2. The valley flashing shall extend at least 11 inches (279 mm) from the centerline each way and have a splash diverter rib not less than 1 inch (25 mm) high at the flow line formed as part of the flashing. Sections of flashing shall have an end lap of not less than 4 inches (102 mm). For roof slopes of three units vertical in 12 units horizontal (25-percent slope) and over, the valley flashing shall have a 36-inch-wide (914 mm) layer of underlayment running the full length of the valley, in addition to other required underlayment.

1507.9.1.1 Solid sheathing required.  Change to read as shown.

1507.9.1.1 Solid sheathing required.  Reserved.

1507.9.2 Deck slope.  Change to read as shown.

1507.9.2 Deck slope.  Wood shakes shall only be used on slopes of three units vertical in 12 units horizontal (33-percent slope) or greater.

Section 1507.9.3 Underlayment, revise text to read as follows:

1507.9.3 Underlayment. Underlayment shall comply with ASTM D 226, Type I or ASTM D 4869 Type I.

1507.9.4 Ice barrier.  Change to read as shown.

1507.9.4 Ice barrier.  Reserved.

Section 1507.9.9  Flashing, revise text to read as follows:

1507.9.9  Flashing. At the juncture of the roof and vertical surfaces, flashing and counterflashing shall be provided in accordance with the manufacturer’s installation instructions, and where of metal, shall comply with Table 1503.2. The valley flashing shall extend at least 11 inches (279 mm) from the centerline each way and have a splash diverter rib not less than 1 inch (25 mm) high at the flow line formed as part of the flashing. Sections of flashing shall have an end lap of not less than 4 inches (102 mm). For roof slopes of three units vertical in 12 units horizontal (25-percent slope) and over, the valley flashing shall have a 36-inch-wide (914 mm) layer of underlayment running the full length of the valley, in addition to other required underlayment.

Table 1507.10.2 Built-Up Roofing Material Standards, revise text to read as follows:

TABLE 1507.10.2 BUILT-UP ROOFING MATERIAL STANDARDS

| MATERIAL STANDARD | STANDARD |
| --- | --- |
| Acrylic coatings used in roofing | ASTM D 6083 |
| Aggregate surfacing | ASTM D 1863 |
| Asphalt adhesive used in roofing | ASTM D 3747 |
| Asphalt cements used in roofing | ASTM D 3019; D 2822; D 4586 |
| Asphalt-coated glass fiber base sheet | ASTM D 4601 |
| Asphalt coatings used in roofing | ASTM D1227; D 2823; D 4479; ASTM D 2824 |
| Asphalt glass felt | ASTM D 2178 |
| Asphalt primer used in roofing | ASTM D 41 |
| Asphalt-saturated and asphalt-coated organic felt base sheet | ASTM D 2626 |
| Asphalt-saturated organic felt (perforated) | ASTM D 226 |
| Asphalt used in roofing | ASTM D 312 |
| Coal-tar cements used in roofing | ASTM D 4022; D 5643 |
| Coal-tar saturated organic felt | ASTM D 227 |
| Coal-tar pitch used in roofing | ASTM D 450; Type I or II |
| Coal-tar primer used in roofing, dampproofing and waterproofing | ASTM D 43 |
| Glass mat, coal tar | ASTM D 4990 |
| Glass mat, venting type | ASTM D 4897 |
| Mineral-surfaced inorganic cap sheet | ASTM D 3909 |
| Thermoplastic fabrics used in roofing | ASTM D 5665, D 5726 |

1507.10.3 Red rosin paper.  Add to read as shown.

1507.10.3 Red rosin paper.  Red rosin paper shall be used when the membrane is applied directly to a wood deck or cementitious fiber decks.

1507.15.3 Roof Coating.  Move to the FBC, Existing Building:

1507.15.3 Roof Coating.  Application of elastomeric and or maintenance coating systems over existing asphalt shingles shall be in accordance with the shingle manufacturer’s approved installation instructions. {3814}

1507.17 add and new section.

1507.17 Building integrated photovoltaic roofing modules/shingles. The installation of building integrated photovoltaic roofing modules/shingles shall comply with the provisions of this section.

1507.17.1 Material standards. Building integrated photovoltaic roofing modules/shingles shall be listed and labeled in accordance with UL 1703.

1507.17.2 Attachment. Building integrated photovoltaic roofing modules/shingles shall be attached in accordance with the manufacturer’s installation instructions.

1507.17.3 Wind resistance. Building integrated photovoltaic roofing modules/shingles shall be tested in accordance with procedures and acceptance criteria in ASTM D3161 or TAS 107. Building integrated photovoltaic roofing modules/shingles shall comply with the classification requirements of Table

1507.2.7.1 for the appropriate maximum basic wind speed.  Building integrated photovoltaic roofing modules/shingle packaging shall bear a label to indicate compliance with the procedures in ASTM D3161 or TAS 107 and the required classification from Table 1507.2.7.1.

(4163)

Section 1509 Rooftop Structures

1509.6 Equipment and appliances on roofs or elevated structures.  Add to read as shown.

1509.6 Equipment and appliances on roofs or elevated structures.  Where equipment and appliances requiring access are installed on roofs or elevated structures at a height exceeding 16 feet (4877 mm), such access shall be provided by a permanent approved means of access, the extent of which shall be from grade or floor level to the equipment and appliances’ level service space. Such access shall not require climbing over obstructions greater than 30 inches (762 mm) high or walking on roofs having a slope greater than 4 units vertical in 12 units horizontal (33-percent slope).

Permanent ladders installed to provide the required access shall comply with the following minimum design criteria:

1.	The side railing shall extend above the parapet or roof edge not less than 30 inches (762 mm).

2.	Ladders shall have rung spacing not to exceed 14 inches (356 mm) on center.

3.	Ladders shall have a toe spacing not less than 6 inches (152 mm) deep.

4.	There shall be a minimum of 18 inches (457 mm) between rails.

5.	Rungs shall have a minimum 0.75-inch (19 mm) diameter and be capable of withstanding a 300-pound (136.1 kg) load.

6.	Ladders over 30 feet (9144 mm) in height shall be provided with offset sections and landings capable of withstanding 100 pounds (488.2 kg/m2) per square foot.

7.	Ladders shall be protected against corrosion by approved means.

Catwalks installed to provide the required access shall be not less than 24 inches (610 mm) wide and shall have railings as required for service platforms.

Exception: This section shall not apply to Group R-3 occupancies.

1509.7 Mechanical units.  Add to read as shown.

1509.7 Mechanical units.  Roof mounted mechanical units shall be mounted on curbs raised a minimum of 8 inches (203 mm) above the roof surface, or where roofing materials extend beneath the unit, on raised equipment supports providing a minimum clearance height in accordance with Table 1509.7.

Table 1509.7 Clearance below Raised Roof Mounted Mechanical Units.  Add to read as shown.

TABLE 1509.7

CLEARANCE BELOW RAISED ROOF MOUNTED

MECHANICAL UNITS

WIDTH OF MECHANICAL UNIT (inches)	MINIMUM CLEARANCE ABOVE ROOF

SURFACES (inches)

< 24                                                                      14

24 < 36                                                                 18

36 < 48                                                                 24

48 < 60                                                                 30

> 60                                                                      48

For SI: 1 inch = 25.4 mm.

Section 1510 Reroofing

1510.3 Recovering versus replacement.  Change to read as shown.

1510.3 Recovering versus replacement. New roof coverings shall not be installed without first removing all existing layers of roof coverings down to the roof deck where any of the following conditions occur:

1. Where the existing roof or roof covering is water soaked or has deteriorated to the point that the existing roof or roof covering is not adequate as a base for additional roofing.

2. Where the existing roof covering is wood shake, slate, clay, cement or asbestos-cement tile.

3. Where the existing roof has two or more applications of any type of roof covering.

4.	When blisters exist in any roofing, unless blisters are cut or scraped open and remaining materials secured down before applying additional roofing.

5. Where the existing roof is to be used for attachment for a new roof system and compliance with the securement provisions of 1504.1 can not be met.

Exceptions:

1. Complete and separate roofing systems, such as standing-seam metal roof systems, that are designed to transmit the roof loads directly to the building’s structural system and that do not rely on existing roofs and roof coverings for support, shall not require the removal of existing roof coverings.

2.  Reserved

3. The application of a new protective coating over an existing spray polyurethane foam roofing system shall be permitted without tear-off of existing roof coverings.

Section 1511 Reserved to maintain current formatting for the HVHZ

Section 1511 Through Section 1525 Florida Specific for the HVHZ.

Section 1512 Through Section 1525 Florida Specific for the HVHZ

See Chapter 15 - HVHZ

Chapter 16 Structural Design

Section 1601 General

1601.1 Scope.  Change to read as shown.

- 1601.1 Scope.  The provisions of this chapter shall govern the structural design of buildings, structures and portions thereof regulated by this code.

Exception: Buildings and structures located within the high-velocity hurricane zone shall comply with the provisions of Sections 1615 through 1626, and, as applicable in flood hazard areas, Section 1612.  (3885 A2)

Section 1602 Definitions

- 1602.1 Definitions.  Add to read as shown.

- BASE SHEAR. Total design lateral force or shear at the base.

PRODUCTION GREENHOUSE. Greenhouses that are occupied for growing plants on a product or research basis without public access.

RISK OCCUPANCY CATEGORY. A categorization category of buildings and other structures for determination used to determine structural requirements based on occupancy of flood and wind loads based on the risk associated with unacceptable performance.

[S4524]

- 1602.1 Definitions.  Change to read as shown.

NOTATIONS.

D = Dead load.

E = Combined effect of horizontal and vertical earthquake induced forces as defined in Section

12.4.2 of ASCE 7.

F = Load due to fluids with well-defined pressures and maximum heights.

Fa = Flood load in accordance of ASCE 7with Chapter 5.

H = Load due to lateral earth pressures, ground water pressure or pressure of bulk materials.

L = Live load, except roof live load, including any permitted live load reduction.

Lr = Roof live load including any permitted live load reduction.

R = Rain load.

S = Snow load.

T = Self-straining force arising from contraction or expansion resulting from temperature change, shrinkage, moisture change, creep in component materials, movement due to differential settlement or combinations thereof.

W = Load due to wind pressure.

Add the following notations:

Vasd         =              nominal design wind speed (3-sec gust), miles per hour (mph) (km/hr) where applicable.

Vult          =             ultimate design wind speeds (3-sec gust), miles per hour (mph) (km/hr) determined from Figures 1609A, 1609B, or 1609C or ASCE 7. [4214]

Section 1603 Construction Documents

1603.1 General.  Change Exception as shown.

1603.1 General. No change

Exception: Construction documents for buildings constructed in accordance with the conventional light-frame construction provisions of Section 2308 shall indicate the following structural design information:

1. Floor and roof live loads.

2. Ground snow load, Pg. Reserved.

3. Basic Ultimate design wind speed, Vult , (3-second gust), miles per hour (mph) (km/hr) and nominal design wind speed, Vasd, as determined in accordance with Section 1609.3.1 and wind exposure.  [4214]

4. Seismic design category and site class.  Reserved.

5. Flood design data, if located in flood hazard areas established in Section 1612.3.

6. Design load-bearing values of soils.

1603.1.3 Roof snow load.  Change to read as shown.

1603.1.3 Roof snow load.  Reserved.

1603.1.4 Wind design data. Change to read as shown.

1603.1.4 Wind design data.  The following information related to wind loads shall be shown, regardless of whether wind loads govern the design of the lateral-force-resisting system of the building:

1.             Basic Ultimate design wind speed Vult , (3-second gust), miles per hour (km/hr) and nominal design wind speed, Vasd, as determined in accordance with Section 1609.3.1.

2.             Risk Category from Table 1604.5 or Table 1.5-1 of ASCE 7 Wind importance factor, IW, and building classification from Table 1604.5 or Table 6-1, ASCE 7 and building classification in Table 1-1, ASCE 7. [4214]

3.	Wind exposure, if more than one wind exposure is utilized, the wind exposure and applicable wind direction shall be indicated.

4.	The applicable enclosure classifications and, if designing with ASCE 7, internal pressure coefficient.

5.        Components and cladding. The design wind pressures in terms of psf (kN/m2) to be used for the selection of exterior components and cladding materials not specifically designed by the registered design professional.

1603.1.5 Earthquake design data.  Change to read as shown.

1603.1.5 Earthquake design data.  Reserved.

1603.1.9 System and components requiring special inspections for seismic resistance.  Change to read as shown.

1603.1.9 System and components requiring special inspections for seismic resistance.  Reserved.

Section 1604 General Design Requirements

Table 1604.3 Deflection Limits.  Change to read as shown.

- TABLE 1604.3

- DEFLECTION LIMITSa, b, c, h, i

| CONSTRUCTION | L | Wf | D+ Ld,g |
| --- | --- | --- | --- |
| Roof members:e Supporting plaster ceiling Supporting nonplaster ceiling Not supporting ceiling Members supporting screen surface | l/360 l/240 l/180 ------ | l/360 l/240 l/180 ------ | l/240 l/180 l/120 l/60 |
| Floor members | l/360 | — | l/240 |
| Exterior walls and interior partitions: With brittle finishes With flexible finishes | — — | l/240 l/120 | — — |
| Farm buildings | — | — | l/180 |
| Greenhouses | — | — | l/120 |

a. For structural roofing and siding made of formed metal sheets, the total load deflection shall not exceed l/60. For secondary roof structural members supporting formed metal roofing, the live load deflection shall not exceed l/150. For secondary wall members supporting formed metal siding, the design wind load deflection shall not exceed l/90. For roofs, this exception only applies when the metal sheets have no roof covering.

b. Interior partitions not exceeding 6 feet in height and flexible, folding and portable partitions are not governed by the provisions of this section. The deflection criterion for interior partitions is based on the horizontal load defined in Section 1607.13.

c. See Section 2403 for glass supports.

d. For wood structural members having a moisture content of less than 16 percent at time of installation and used under dry conditions, the deflection resulting from L + 0.5D is permitted to be substituted for the deflection resulting from L + D.

e. The above deflections do not ensure against ponding. Roofs that do not have sufficient slope or camber to assure adequate drainage shall be investigated for ponding. See Section 1611 for rain and ponding requirements and Section 1503.4 for roof drainage requirements.

f. The wind load is permitted to be taken as 0.42 0.7 times the “component and cladding” loads for the purpose of determining deflection limits herein. [4214]

g. For steel structural members, the dead load shall be taken as zero.

h. For aluminum structural members or aluminum panels used in skylights and sloped glazing framing, roofs or walls of sunroom additions or patio covers, not supporting edge of glass or aluminum sandwich panels, the total load deflection shall not exceed l/60. For aluminum sandwich panels used in roofs or walls of sunroom additions or patio covers, the total load deflection shall not exceed l/120.

i. For cantilever members, l shall be taken as twice the length of the cantilever.

j. Screen surfaces shall be permitted to include a maximum of 25% solid flexible finishes.

1604.4 Analysis.  Change to read as shown.

1604.4 Analysis. Load effects on structural members and their connections shall be determined by methods of structural analysis that take into account equilibrium, general stability, geometric compatibility and both short- and long-term material properties.

Members that tend to accumulate residual deformations under repeated service loads shall have included in their analysis the added eccentricities expected to occur during their service life.

Any system or method of construction to be used shall be based on a rational analysis in accordance with well-established principles of mechanics. Such analysis shall result in a system that provides a complete load path capable of transferring loads from their point of origin to the load-resisting elements.

The total lateral force shall be distributed to the various vertical elements of the lateral-force-resisting system in proportion to their rigidities, considering the rigidity of the horizontal bracing system or diaphragm. Rigid elements assumed not to be a part of the lateral-force-resisting system are permitted to be incorporated into buildings provided their effect on the action of the system is considered and provided for in the design. Except where diaphragms are flexible, or are permitted to be analyzed as flexible, provisions shall be made for the increased forces induced on resisting elements of the structural system resulting from torsion due to eccentricity between the center of application of the lateral forces and the center of rigidity of the lateral-force-resisting system.

Every structure shall be designed to resist the overturning effects caused by the lateral forces specified in this chapter. See Section 1609 for wind loads, and Section 1610 for lateral soil loads.

1604.5 – 1604.5.1 – Change to read as shown.

1604.5 Risk Occupancy category. Each building and structure shall be assigned an risk occupancy category in accordance with Table 1604.5.

1604.5.1 Multiple occupancies. Where a building or structure is occupied by two or more occupancies not included in the same risk occupancy category, it shall be assigned the classification of the highest risk occupancy category corresponding to the various occupancies. Where buildings or structures have two or more portions that are structurally separated, each portion shall be separately classified. Where a separated portion of a building or structure provides required access to, required egress from or shares life safety components with another portion having a higher risk occupancy category, both portions shall be assigned to the higher risk occupancy category.

Table 1604.5 RISK OCCUPANCY Category of Buildings and Other Structures.

Revise 2nd column of the 2nd raw to add “Screen enclosures”.

Add screen enclosures to Risk Category I:

• Screen enclosures

[S4669]

1604.8.2 Walls. Change to read as shown.

1604.8.2  Walls. Walls shall be anchored to floors, roofs and other structural elements that provide lateral support for the wall. Such anchorage shall provide a positive direct connection capable of resisting the horizontal forces specified in this chapter, unless the lateral force has otherwise been calculated by the Engineer of Record. Concrete and masonry walls shall be designed to resist bending between anchors where the anchor spacing exceeds 4 feet (1219 mm). Required anchors in masonry walls of hollow units or cavity walls shall be embedded in a reinforced grouted structural element of the wall. See Section 1609 for wind design requirements.

1604.9 Counteracting structural actions. – Change to read as shown.

1604.9 Counteracting structural actions. Structural members, systems, components and cladding shall be designed to resist forces due to earthquake and wind, with consideration of overturning, sliding and uplift. Continuous load paths shall be provided for transmitting these forces to the foundation. Where sliding is used to isolate the elements, the effects of friction between sliding elements shall be included as a force.

[S4670]

1604.10 Wind and seismic detailing.  Change to read as shown.

1604.10 Wind and seismic detailing. Reserved.   Lateral-force-resisting systems shall meet seismic detailing requirements and limitations prescribed in this code and ASCE 7, excluding Chapter 14 and Appendix 11A, even when wind load effects are greater than seismic load effects.

Section 1605 Load Combinations

1605.1 General.  Change to read as shown.

1605.1 General. Buildings and other structures and portions thereof shall be designed to resist:

1. The load combinations specified in Section 1605.2, 1605.3.1 or 1605.3.2,

2. The load combinations specified in Chapters 18 through 23, and

3. The load combinations with overstrength factor specified in Section 12.4.3.2 of ASCE 7 where required by Section 12.2.5.2, 12.3.3.3 or 12.10.2.1 of ASCE 7. With the simplified procedure of ASCE 7 Section 12.14, the load combinations with overstrength factor of Section 12.14.3.2 or ASCE 7 shall be used.

Applicable loads shall be considered, including both earthquake and wind, in accordance with the specified load combinations. Each load combination shall also be investigated with one or more of the variable loads set to zero.

Where the load combinations with overstrength factor in Section 12.4.3.2 of ASCE 7 apply, they shall be used as follows:

1. The basic combinations for strength design with overstrength factor in lieu of Equations 16-5 and 16-7 in Section 1605.2.1.

2. The basic combinations for allowable stress design with overstrength factor in lieu of Equations 16-12, 16-13 and 16-15 in Section 1605.3.1.

3. The basic combinations for allowable stress design with overstrength factor in lieu of Equations 16-20 and 16-21 in Section 1605.3.2.

1605.2.1 Basic load combinations.  Change to read as shown.

1605.2.1 Basic load combinations. Where strength design or load and resistance factor design is used, structures and portions thereof shall resist the most critical effects from the following combinations of factored loads:

1.4(D+F) (Equation 16-1)

1.2(D + F + T) + 1.6(L + H) + 0.5(Lr or S or R) (Equation 16-2)

1.2D+ 1.6(Lr or S or R) + (f1L or 0.8W 0.5W) (Equation 16-3)

1.2D+ 1.6 1.0 W+ f1L + 0.5(Lr or S or R) (Equation 16-4)

1.2D+ 1.0E+ f1L + f2S (Equation 16-5)

0.9D+ 1.6 1.0 W+ 1.6H (Equation 16-6)

0.9D+ 1.0E+ 1.6H (Equation 16-7)

where:

f1 = 1 for floors in places of public assembly, for live loads in excess of 100 pounds per square foot (4.79 kN/m2), and for parking garage live load, and

= 0.5 for other live loads.

f2 = 0.7 for roof configurations (such as saw tooth) that do not shed snow off the structure, and

= 0.2 for other roof configurations.

Exception: Where other factored load combinations are specifically required by the provisions of this code, such combinations shall take precedence. [4214]

1605.3.1 Basic load combinations.  Change to read as shown.

1605.3.1 Basic load combinations. Where allowable stress design (working stress design), as permitted by this code, is used, structures and portions thereof shall resist the most critical effects resulting from the following combinations of loads:

D+F (Equation 16-8)

D+H+F+ L + T (Equation 16-9)

D+H+F+ (Lr or S or R) (Equation 16-10)

D + H + F + 0.75(L + T) + 0.75(Lr or S or R) (Equation 16-11)

D+H+F+ ( 0.6W or 0.7E) (Equation 16-12)

D + H + F + 0.75 .45 (W or 0.7E) + 0.75L + 0.75(Lr or S or R) (Equation 16-13)

0.6D+0.6W+H (Equation 16-14)

0.6D+ 0.7E+H (Equation 16-15)

[S4671]

Exceptions:

1. Crane hook loads need not be combined with roof live load or with more than three-fourths of the snow load or one-half of the wind load.

2.   Reserved.  [4214]

Section 1605.3.1.1 Load reduction, revise text to read as follows:

1605.3.1.1 Stress increases Load reduction.

- 1.	Increases in allowable stress specified in the materials, sections of this code or a referenced standard shall not be permitted to be used with load combinations of Sections 1605.3.1. Duration of load increase shall be permitted in accordance with Chapter 23.

Exception: Increases in allowable stress shall be permitted in accordance with ACI 530/ASCE 5/TMS 402 provided the load reduction shall not be applied (see s. 1605.3.1). loads in the load combinations of Equations 16-11 and 16-13 are not reduced.

2. Simultaneous use of both one-third increase in allowable stress and the 25 percent reduction in combined loads shall not be permitted.

[S4672]

2. Simultaneous use of both one-third increase in allowable stress and the 25 percent reduction in combined loads shall not be permitted.

1605.3.2 Alternative basic load combinations. In lieu of the basic load combinations specified in Section 1605.3.1, structures and portions thereof shall be permitted to be designed for the most critical effects resulting from the following combinations. When using these alternative basic load combinations that include wind or seismic loads, allowable stresses are permitted to be increased or load combinations reduced where permitted by the material chapter of this code or the referenced standards. For load combinations that include the counteracting effects of dead and wind loads, only two-thirds of the minimum dead load likely to be in place during a design wind event shall be used. Where wind loads are calculated in accordance with Chapters 26 through 31 Chapter 6 of ASCE 7, the coefficient in the following equations shall be taken as 1.3 0.78. For other wind loads, shall be taken as 1. When using these alternative load combinations to evaluate sliding, overturning and soil bearing at the soil-structure interface, the reduction of foundation overturning from Section 12.13.4 in ASCE 7 shall not be used. When using these alternative basic load combinations for proportioning foundations for loadings, which include seismic loads, the vertical seismic load effect, Ev, in Equation 12.4-4 of ASCE 7 is permitted to be taken equal to zero. [4214]

D+ L + (Lr or S or R) (Equation 16-16)

D+ L + (W) (Equation 16-17)

D+ L +W+ S/2 (Equation 16-18)

D+ L + S +W/2 (Equation 16-19)

D+ L + S +E/1.4 (Equation 16-20)

0.9D+E/1.4 (Equation 16-21)

Exceptions:

1. Crane hook loads need not be combined with roof live loads or with more than three-fourths of the snow load or one-half of the wind load.

2. Reserved.

1605.4 Heliports and helistops. Heliport and helistop landing areas shall be designed for the following loads, combined in accordance with Section 1605:

1. Dead load, D, plus the gross weight of the helicopter, Dh, plus snow load, S.

2 – 3 No change

Exception:  No change

Table 1607.1 Minimum Uniformly Distributed Live Loads and Minimum

Revise Notes to reserve footnote “g”.

g. Reserved.

1607.11 Roof loads.Change to read as shown.

1607.11 Roof loads. The structural supports of roofs and marquees shall be designed to resist wind and, where applicable, snow and earthquake loads, in addition to the dead load of construction and the appropriate live loads as prescribed in this section, or as set forth in Table 1607.1. The live loads acting on a sloping surface shall be assumed to act vertically on the horizontal projection of that surface.

1607.11.1 Distribution of roof loads.  Change to read as shown.

1607.11.1 Distribution of roof loads. Where uniform roof live loads are reduced to less than 20 psf (0.96 kN/m2) in accordance with Section 1607.11.2.1 and are applied to the design of structural members arranged so as to create continuity, the reduced roof live load shall be applied to adjacent spans or to alternate spans, whichever produces the most unfavorable load effect. See Section 1607.11.2 for reductions in minimum roof live loads and Section 7.5 of ASCE 7 for partial snow loading.

1607.11.4 Awnings and canopies.  Change to read as shown.

1607.11.4 Awnings and canopies. Awnings and canopies shall be designed for uniform live loads as required in Table 1607.1 as well as for snowloads and wind loads as specified in Sections 1608 and 1609.

Section 1608 Snow Loads.  Change to read as shown.

Section 1608 Snow Loads.  Reserved.

Section 1609 Wind Loads

Figure 1609 State of Florida Debris Region and Basic Wind Speed.  Change to read as shown.

FIGURE 1609

STATE OF FLORIDA DEBRIS REGION & BASIC WIND SPEED

[4214]

[S4741]

Section 1609.1 Applications.  Change to read as shown.

1609.1 Applications. Buildings, structures and parts thereof shall be designed to withstand the minimum wind loads prescribed herein. Decreases in wind loads shall not be made for the effect of shielding by other structures.

All exterior wall coverings and soffits shall be capable of resisting the design pressures specified for walls for components and cladding loads in accordance with Section 1609.1.1.  Manufactured soffits shall be labeled in accordance with Section 1715.9 of this code.(3857)

Section 1609.1.1 Determination of wind loads, revise text to read as follows:

1609.1.1 Determination of wind loads.  Change to read as shown.

1609.1.1 Determination of wind loads. Wind loads on every building or structure shall be determined in accordance with Chapters 26 through 30 6 of ASCE 7 or the provisions of the alternate all-heights method in Section 1609.6.. The type of opening protection required, the basic wind speed and the exposure category for a site is permitted to be determined in accordance with Section 1609 or ASCE 7.Wind shall be assumed to come from any horizontal direction and wind pressures shall be assumed to act normal to the surface considered. [4214]

Note: Clarification to ASCE 7.  Arrows shown on Figure 6-10 of ASCE 7 indicate that  the pressure coefficients apply specifically to “Direction of MWFRS being designed”.  This means that the longitudinal pressure coefficients are not applicable to trusses that span in the transverse direction and therefore uplift reactions for trusses that span in the transverse direction would be determined by the pressure coefficients associated with those shown for the transverse direction.

[4214, 4177]

Exceptions:

1. Subject to the limitations of Section 1609.1.1.1, the provisions of ICC 600 shall be permitted for applicable Group R-2 and R-3 buildings.

2. Subject to the limitations of Section 1609.1.1.1, 1609.1.4, and 1609.3, provisions of ANSI/AF&PA WFCM, Wood Frame Construction Manual for One- and Two-Family Dwellings shall be permitted for applicable wood frame buildings of Group R3 occupancy where Vasd, determined in accordance with Section 1609.3.1 for a basic wind speed of is150 mph or less in accordance with Figure 1609 and Section 1609.4.

3. Subject to the limitations of Section 1609.1.1.1, residential structures using the provisions of AISI S230.

4. Designs using NAAMM FP 1001. Specification for Design Loads of Metal Flagpoles.

- 5. Designs using TIA-222 for antenna-supporting structures and antennas shall be permitted for communication tower and steel antenna support structures.

6. Wind tunnel tests in accordance with Chapter 31 Section 6.6 of ASCE 7, subject to the limitations in Section 1609.1.1.2.

- 7.	Subject to the limitations of Sections 1609.1.1.1, 1609.1.4, and 1609.3, the provisions of the WPPC Guide to Wood Construction in High Wind Areas shall be permitted for applicable wood- frame buildings of Group R3 occupancy for a basic wind speed of 130 mph (58 m/s) or less in Exposure B and 110 mph (49 m/s) or less in Exposure C in accordance with Figure 1609 and Section 1609.4.

- 8.	Designs using AASHTO LTS-4 Structural Specifications for Highway Signs, Luminaries, and Traffic Signals.

9. Wind loads for screened enclosures shall be determined in accordance with Section 2002.4.

The wind speeds in Figure 1609A, 1609B and 1609C shall be converted to nominal wind speeds, Vasd, in accordance with Section 1609.3.1 when the provisions of the standards referenced in Exceptions 1 through 5 and 7 are used unless the wind provisions in the standards are based on Ultimate Wind Speeds as specified in accordance with Figures 1609A, 1609B, or 1609C or Chapter 26 of ASCE 7.

[S4673]

.  [4214]

Section 1609.1.1.1 Applicability, revise text to read as follows:

1609.1.1.1 Applicability. The provisions of ICC 600, the AF&PA Wood Frame Construction Manual for One- and Two-Family Dwellings, High Wind Areas, the FC & PA Guide to Concrete Masonry Residential Construction in High Wind Areas and the WPPC Guide to Wood Construction in High Wind Areas are applicable only to buildings located within Exposure B or C as defined in Section 1609.4. The provisions of ICC 600, AF&PA WFCM and AISI S230, the FC & PA Guide to Concrete Masonry Residential Construction in High Wind Areas and the WPPC Guide to Wood Construction in High Wind Areas shall not apply to buildings sited on the upper half of an isolated hill, ridge or escarpment meeting the following conditions:

[S4674AM]

1-3 No change to text.

Revise 1609.1.1.2 to read as follows:

1609.1.1.2 Wind tunnel test limitations. The lower limit on pressures for main wind-force-resisting systems and components and cladding shall be in accordance with Sections 1609.1.1.2.1 and 1609.1.1.2.2.

1609.1.1.2.1 Lower limits on main wind-force-resisting system. Base overturning moments determined from wind tunnel testing shall be limited to not less than 80 percent of the design base overturning moments determined in accordance with Section 6.5 of ASCE 7, unless specific testing is performed that demonstrates it is the aerodynamic coefficient of the building, rather than shielding from other structures, that is responsible for the lower values.

The 80-percent limit shall be permitted to be adjusted by the ratio of the frame load at critical wind directions as determined from wind tunnel testing without specific adjacent buildings, but including appropriate upwind roughness, to that determined in Section 6.5 of ASCE 7.

1609.1.1.2.2 Lower limits on components and cladding. The design pressures for components and cladding on walls or roofs shall be selected as the greater of the wind tunnel test results or 80 percent of the pressure obtained for Zone 4 for walls and Zone 1 for roofs as determined in Section 6.5 of ASCE 7, unless specific testing is performed that demonstrates it is the aerodynamic coefficient of the building, rather than shielding from nearby structures, that is responsible for the lower values. Alternatively, limited tests at a few wind directions without specific adjacent buildings, but in the presence of an appropriate upwind roughness, shall be permitted to be used to demonstrate that the lower pressures are due to the shape of the building and not to shielding. [4214]

Section 1609.1.2 is revised to read as follows:  Needs to be resolved.

1609.1.2 Protection of openings. Glazed openings in buildings located in wind-borne debris regions shall be protected from wind-borne debris. Glazed opening protection for wind-borne debris shall meet the requirements SSTD 12, ASTM E 1886 and ASTM E 1996, ANSI/DASMA 115 (for garage doors and rolling doors) or TAS 201, 202 and 203 or AAMA 506 referenced therein.

- 1.	Glazed openings located within 30 feet (9.1 m) of grade shall meet the requirements of the Large Missile Test of ASTM E 1996.

- 2.	Glazed openings located more than 30 feet (9.1 m) above grade shall meet the provisions of the Small Missile Test of ASTM E 1996.

- 3.	Storage sheds that are not designed for human habitation and that have a floor area of 720 square feet (67 m2) or less are not required to comply with the mandatory windborne debris impact standards of this code.

- 4.	Openings in sunrooms, balconies or enclosed porches constructed under existing roofs or decks are not required to be protected provided the spaces are separated from the building interior by a wall and all openings in the separating wall are protected in accordance with Section 1609.1.2 4 above. Such spaces shall be permitted to be designed as either partially enclosed or enclosed structures. [4232]

- Exceptions:

1. Wood structural panels with a minimum thickness of 7/16 inch (11.1 mm) and maximum panel span of 8 feet (2438 mm) shall be permitted for opening protection in one- and two-story buildings classified as Group R-3 or R-4 occupancy. Panels shall be precut so that they shall be attached to the framing surrounding the opening containing the product with the glazed opening. Panels shall be predrilled as required for the anchorage method and shall be secured with the attachment hardware provided. Attachments shall be designed to resist the components and cladding loads determined in accordance with the provisions of ASCE 7, with corrosion-resistant attachment hardware provided and anchors permanently installed on the building. Attachment in accordance with Table 1609.1.2 with corrosion-resistant attachment hardware provided and anchors permanently installed on the building is permitted for buildings with a mean roof height of 45 feet (13 716 mm) or less where Vasd, determined in accordance with Section 1609.3.1 wind speeds do does not exceed 140 mph (63 m/s). [4214]

2. Glazing in Risk Occupancy Category I buildings as defined in Section 1604.5 including greenhouses that are occupied for growing plants on a production or research basis, without public access shall be permitted to be unprotected.

3. Glazing in Risk Occupancy Category II, III or IV buildings located over 60 feet (18 288 mm) above the ground and over 30 feet (9144 mm) above aggregate surface roofs located within 1,500 feet (458 m) of the building shall be permitted to be unprotected

4.         Exterior balconies or porches under existing roofs or decks enclosed with screen or removable vinyl and acrylic panels complying with Section 2002.3.3 shall not be required to be protected and openings in the wall separating the unit from the balcony or porch shall not be required to be protected unless required by other provisions of this code.[4232]

Revise 1609.1.2.1 to read as follows:

1609.1.2.1 Louvers. Louvers protecting intake and exhaust ventilation ducts not assumed to be open that are located within 30 feet (9144 mm) of grade shall meet requirements of an approved impact-resisting standard or the Large Missile Test of ASTM E 1996 AMCA 540 or shall be protected by an impact resistant cover complying  with an approved impact-resistance standard or the large missile test of ASTM E 1996.

[4033 A3handout]

1609.1.2.2.  Reserved.

Table 1609.1.2 – Change to read as shown.

(no change to table values)

Note a:

a. This table is based on a Vasd, determined in accordance with Section 1609.3.1 of 140 mph wind speeds and a 45-foot mean roof height.

[4676]

Section 1609.1.2.3 Impact resistant coverings.  Add text to read as shown.

1609.1.2.3 Impact resistant coverings.

1609.1.2.3.1 Impact resistant coverings shall be tested at 1.5 times the design pressure (positive or negative) expressed in pounds per square feet as determined by the Florida Building Code, Building Section 1609 or ASCE 7 for which the specimen is to be tested.  The design pressures, as determined from ASCE 7, are permitted to be multiplied by 0.6.

[S4677]

1609.1.2.3.2 Impact resistant coverings. Impact resistant coverings shall be labeled in accordance with the provisions of Section 1714.8.

Add Section 1609.1.2.4 as follows:

1609.1.2.3 4 Modifications to ATM E 1996. Section 6.2.2 of ASTM E 1996 shall be modified as follows:

6.2.2 Unless otherwise specified, select the wind zone based on the basic wind speed as follows:

6.2.2.1 Wind Zone 1 - 130 mph <  basic wind speed < 140 mph, and Hawaii.

6.2.2.2 Wind Zone 2 - 140 mph <  basic wind speed < 150 mph at greater than 1.6 km (one mile) from the coastline. The coastline shall be measured from the mean high water mark.

6.2.2.3 Wind Zone 3—150 mph (58 m/s) < basic wind speed < 160 mph (63 m/s), or 140 mph (54 m/s) <  basic wind speed  < 160 mph (63 m/s) and within 1.6 km (one mile) of the coastline. The coastline shall be measured from the mean high water mark.

6.2.2.4 Wind Zone 4—basic wind speed >160 mph (63 m/s). [4214]

1609.1.2.4.1 Table 1 of ASTM E 1886 and ASTM E 1996 shall be modified to read as follows

Air Pressure Cycles

0.2 to 0.5 Ppos1

0.0 to 0.6 Ppos

0.5 to 0.8 Ppos

0.3 to 1.0 Ppos

0.3 to 1.0 Pneg2

0.5 to 0.8 Pneg

0.0 to 0.6 Pneg

0.2 to 0.5 Pneg

Notes:

- Ppos = 0.6 x positive ultimate design load in accordance with ASCE 7.

- Pneg = 0.6 x negative ultimate design load in accordance with ASCE 7.

[S4679, Comment after Glitch]

1609.1.3 Optional exterior door component testing.  Change to read as shown.

1609.1.3 Optional exterior door component testing.  Exterior side-hinged door assemblies shall have the option to have the components of the assembly tested and rated for impact resistance in accordance with the following specification: SDI 250.13.

1609.1.4 add   to read as shown.

1609.1.4 The wind-borne debris regions requirements shall not apply landward of the designated contour line in Figure 1609. A geographical boundary that coincides with the contour line shall be established.

1609.1.3 5 Testing to allowable or nominal loads. Where testing for wind load resistance is based on allowable or nominal wind loads, the design wind loads determined in accordance with ASCE 7 or Section 1609  are permitted to be multiplied by 0.6 for the purposes of the wind load resistance testing. [4214]

1609.2 Definitions. Change the text of the following terms to read as shown:

HURRICANE-PRONE REGIONS. Areas vulnerable to hurricanes defined as:

1. The U. S. Atlantic Ocean and Gulf of Mexico coasts where the basic wind speed for Risk Category II buildings is greater than 115 90 mph (40 m/s) and

2. Hawaii, Puerto Rico, Guam, Virgin Islands and American Samoa.

WIND-BORNE DEBRIS REGION. Areas within Portions of hurricane- prone regions located:that are

- Wwithin 1 mile (1.61 km) of the coastal mean high water line where the basic ultimate design wind speed Vult is 130 110 mph (48 m/s) or greater; or

- In areas  portions of hurricane-prone regionswhere the basic ultimate design wind speed Vult is 140 120 mph (53 m/s) or greater; or Hawaii.

For Risk Category II buildings and structures and Risk occupancy category III buildings and structures, except health care facilities, the windborne debris region shall be based on Figure 1609A. For Risk occupancy category IV buildings and structures and Risk occupancy category III health care facilities, the windborne debris region shall be based on Figure 1609B.

[S4680]

WIND SPEED, Vult. Ultimate design wind speeds.

WIND SPEED, Vasd.Nominal design wind speeds.

[4214]

1609.3 Basic wind speed.   Change to read as shown.

1609.3 Basic wind speed. The basic wind speed in miles per hour, for the development of wind loads, shall be determined from Figure1609.  The exact location of wind speed lines shall be established by local ordinance using recognized physical landmarks such as major roads, canals, rivers and lake shores whenever possible.

1609.3 Basic wind speed. The basic ultimate design wind speed Vult, in miles per hour, for the development of the wind loads shall be determined by Figure 1609 Figures 1609A, 1609B and 1609C. The ultimate design wind speed Vult for use in the design of Risk Category II buildings and structures shall be obtained from Figure 1609A. The ultimate design wind speed Vult for use in the design of Risk Category III and IV buildings and structures shall be obtained from Figure 1609B. The ultimate design wind speed Vult for use in the design of Risk Category I buildings and structures shall be obtained from Figure 1609C. The exact location of wind speed lines shall be established by local ordinance using recognized physical landmarks such as major roads, canals, rivers and lake shores wherever possible. [4214]

1609.3.1 Wind speed conversion. When required, the 3-second gust basic ultimate design wind speeds of Figure 1609A, B and C shall be converted to nominal design wind speeds, Vasd, fastest-mile wind speeds, Vfm, using Table 1609.3.1 or Equation 16-32.

Vfm = (V3s – 10.5)/1.05

where:

V3S = 3-second gust basic wind speed from Figure 1609.

Vasd = Vultv0.6                                                       (Equation 16-32)

Where:

Vasd = nominal design wind speed applicable to methods specified in Exceptions 1 through 5 of Section 1609.1.1

[S4681]

Vult = strength design wind speeds determined from Figures 1609a, 1609b, or 1609c.

[4214]

Delete existing Table 1609.3.1 and replace with the following:

TABLE 1609.3.1

EQUIVALENT BASIC WIND SPEEDS

| V3s | 85 | 90 | 100 | 105 | 110 | 120 | 125 | 130 | 140 | 145 | 150 | 160 | 170 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Vfm | 71 | 76 | 85 | 90 | 95 | 104 | 109 | 114 | 123 | 128 | 133 | 142 | 152 |

- Linear interpolation is permitted

- V3s is the 3-second gust wind speed (mph).

- Vfm is the fastest mile wind speed (mph).

TABLE 1609.3.1

WIND SPEED CONVERSIONSabc

| Vul | 100 | 110 | 120 | 130 | 140 | 150 | 160 | 170 | 180 | 190 | 200 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Vasd | 78 | 85 | 93 | 101 | 108 | 116 | 124 | 132 | 139 | 147 | 155 |

- Linear interpolation is permitted

- Vasd = nominal design wind speed

- Vult = ultimate design wind speed determined from Figures 1609A, 1609B, or 1609C

[4214]

1609.4 Exposure category.  Change to read as shown.

1609.4 Exposure category. For each wind direction considered, an exposure category that adequately reflects the characteristics of ground surface irregularities shall be determined for the site at which the building or structure is to be constructed. Account shall be taken of variations in ground surface roughness that arise from natural topography and vegetation as well as from constructed features.

Exception:  An intermediate exposure between the exposure categories defined is permitted in a transition zone provided that it is determined by a rational analysis method.

1609.4.1 No change.

Section 1609.4.2 Surface roughness categories, revise text to read as follows:

1609.4.2 Surface roughness categories.  A ground surface roughness within each 45-degree (0.79 rad) sector shall be determined for a distance upwind of the site as defined in Section 1609.4.3 from the categories defined below, for the purpose of assigning an exposure category as defined in Section 1609.4.3.

Surface Roughness B. Urban and suburban areas, wooded areas or other terrain with numerous closely spaced obstructions having the size of single-family dwellings or larger.

Surface Roughness C. Open terrain with scattered obstructions having heights generally less than 30 feet (9144 mm). This category includes flat open country, and grasslands, and all water surfaces in hurricane-prone regions. This surface roughness shall also apply to any building located within surface roughness B-type terrain where the building is within 100 feet horizontally in any direction of open areas of surface roughness C or D-type terrain that extends more than 600 feet (182.9 m) and width greater than 150 ft. in the upwind direction. Short-term (less than two year) changes in the pre-existing terrain exposure, for the purposes of development, shall not be considered surface roughness C. Where development buildout will occur within three years and the resultant condition will meet the definition of surface roughness B, surface roughness B shall be regulating for the purpose of permitting. This category includes flat open country, and grasslands and ocean or gulf shorelines and shall extend downwind for a distance of 1500 feet. [4214]

Surface Roughness D. Flat, unobstructed areas and water surfaces. This category includes smooth mud flats, salt flats and unbroken ice. Reserved.

[4214]

Section 1609.4.3 Exposure categories, revise text to read as follows:

1609.4.3 Exposure categories. An exposure category shall be determined in accordance with the following:

Exposure B. For buildings with a mean roof height of less than or equal to 30 ft,Exposure B shall apply where the ground surface roughness condition, as defined by Surface Roughness B, prevails in the upwind direction for a distance of at least 1,500 ft (457 m). For buildings with a mean roof height greater than 30 ft, Exposure B shall apply where Surface Roughness B prevails in the upwind direction for a distance of at least 2,600 feet (792 m) or 20 times the height of the building, whichever is greater.

Exception: For buildings whose mean roof height is less than or equal to 30 feet (9144 mm), the upwind distance is permitted to be reduced to 1,500 feet (457 m). [4214]

Exposure C. Exposure C shall apply for all cases where Exposures B or D do not apply. Buildings located within a distance of 600 feet of inland bodies of water that present a fetch of 1 mile (1.61 km) or more or inland waterways or rivers with a width of 1 mile (1.61 km) or more shall be classified as Exposure C and roof sheathing uplift and roof-to-wall connection uplift loads shall be increased by 20%. [4214, 3665]

Exposure D. Exposure D shall apply where the ground surface roughness, as defined by Surface Roughness D, prevails in the upwind direction for a distance of at least 5,000 feet (1524 m) or 20 times the height of the building, whichever is greater. Exposure D shall also apply where the ground surface roughness immediately upwind of the site is B or C, and the site is within a distance of 600ft (183 m) or 20 times the building height, whichever is greater, from an exposure D condition as defined in the previous sentence. This exposure category is not applicable in Florida. [4214]

Revise 1609.5.3 to read as follows:

1609.5.3 Rigid tile. Wind loads on rigid tile roof coverings shall be determined in accordance with the following equation:

(no change to remainder of section)

GCp= Roof pressure coefficient for each applicable roof zone determined from Chapter 30 6 of ASCE 7. Roof coefficients shall not be adjusted for internal pressure.

qh = Wind velocity pressure, psf (kN/m2) determined from Section 27.3.2 6.5.10 of ASCE 7.

(no change to remainder of section) [4214]

1609.6 Alternate all heights method. – 1609.6.4.2 Determination of Kz – Kzt – Change to read as shown.

1609.6 Alternate all heights method. The alternate design provisions in this section are simplifications of Chapter 27 Part 1 – Directional Procedure of the ASCE 7 Method 2 – Analytical Procedure.

1609.6.1 Scope. As an alternate to ASCE 7 Chapter 27 Part 1 and Chapter 30 Part 3 Section 6.5, the following provisions are permitted to be used to determine the wind effects on regularly shaped buildings, or other structures that are regularly shaped, which meet all of the following conditions:

1-3: (no change)

4. The building shall meet the requirements of a simple

diaphragm building as defined in ASCE 7 Section

26.2, where wind loads are only transmitted to the main

wind-force-resisting system (MWFRS) at the diaphragms.

5. (no change)

1609.6.1.1 Modifications. The following modifications shall be made to certain subsections in ASCE 7: in Section 1609.6.2, symbols and notations that are specific to this section are used in conjunction with the symbols and notations in ASCE 7 Section 26.3.

1609.6.2 Symbols and notations. Coefficients and variables used in the alternate all-heights method equations are as follows:

Cnet = Net-pressure coefficient based on Kd [(G) (Cp) –

(GCpi)], in accordance with Table 1609.6.2(2).

G = Gust effect factor for rigid structures in accordance with ASCE 7 Section 26.9 6.5.8.1.

Kd = Wind directionality factor in accordance with

ASCE 7 Table 26.6-1 6-4.

Pnet = Design wind pressure to be used in determination of wind loads on buildings or other structures or their components and cladding, in psf (kN/m2).

qs = Wind stagnation pressure in psf (kN/m2) in accordance with Table 1609.6.2(1).

1609.6.3 Design equations. When using the alternate all-heights method, the MWFRS and components and cladding of every structure shall be designed to resist the effects of wind pressures on the building envelope in accordance with Equation 16-34.

Pnet = qsKzCnet [IKzt] (Equation 16-34)

Design wind forces for the MWFRS shall not be less than 16 10 psf (0.77 0.48 kN/m2) multiplied by the wall area of the building structure and 8 psf (0.38 kN/m2) multiplied by the roof area of the building projected on a plane normal to the assumed wind

direction (see ASCE 7 Section 27.4.7 6.1.4 for criteria). Design net wind pressure for components and cladding shall not be less than 16 10 psf (0.77 0.48 kN/m2) acting in either direction normal to the surface.

1609.6.4.1 Main wind-force-resisting systems. The MWFRS shall be investigated for the torsional effects identified in ASCE 7 Figure 27.4-8 6-9.

1609.6.4.2 Determination of Kz and Kzt. Velocity pressure exposure coefficient, Kz, shall be determined in accordance with ASCE 7 Sections 27.3 and 30.3 6.5.6.6 and the topographic factor, Kzt, shall be determined in accordance with ASCE 7 Section 26.8 6.5.7.

1. For the windward side of a structure, Kzt and Kz shall be based on height z.

2. For leeward and sidewalls, and for windward and leeward roofs, Kzt and Kz shall be based on mean roof height h.

Replace Table 1609.6.2(1) with the following table:

[S4682]

Table 1609.7(1) Add text to read as shown.

Table 1609.7(1)

GARAGE DOOR AND ROLLING DOOR WIND LOADS FOR A BUILDING WITH A MEAN ROOF HEIGHT OF 30 FEET LOCATED IN EXPOSURE B (psf)

| Effective wind area |  | Vasd determined in accordance with Section 1609.3.1 Basic Wind Speed V (mph – 3 second gust) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Width (ft) | Height (ft) | 85 | 90 | 100 | 110 | 120 | 130 | 140 | 150 |
| Roof Angle 0 – 10 degrees |  |  |  |  |  |  |  |  |  |
| 8 | 8 | 10.5 -11.9 | 11.7 – 13.3 | 14.5 – 16.4 | 17.5 – 19.9 | 20.9 – 23.6 | 24.5 – 27.7 | 28.4 – 32.2 | 32.6 – 36.9 |
| 10 | 10 | 10.1 –11.4 | 11.4 – 12.7 | 14.0 – 15.7 | 17.0 – 19.0 | 20.2 – 22.7 | 23.7 – 26.6 | 27.5 – 30.8 | 31.6 – 35.4 |
| 14 | 14 | 10.0 -10.7 | 10.8 – 12.0 | 13.3 – 14.8 | 16.1 – 17.9 | 19.2 – 21.4 | 22.5 – 25.1 | 26.1 – 29.1 | 30.0 – 33.4 |
| Roof Angle > 10 |  |  |  |  |  |  |  |  |  |
| 9 | 7 | 11.4 – 12.9 | 12.8 – 14.5 | 15.8 – 17.9 | 19.1 – 21.6 | 22.8 – 25.8 | 26.7 – 30.2 | 31.0 – 35.1 | 35.6 – 40.2 |
| 16 | 7 | 10.9 – 12.2 | 12.3 – 13.7 | 15.2 – 16.9 | 18.3 – 20.4 | 21.8 – 24.3 | 25.6 – 28.5 | 29.7 – 33.1 | 34.1 – 38.0 |

For SI: 1 Square foot = 0.929 Sqm, 1 mph = 0.447 mls, 1 psf = 47.88 N/sqm

            - For effective areas or wind speeds between those given above the load may be interpolated, otherwise use the load associated with the lower effective area.

            - Table values shall be adjusted for height and exposure by multiplying by adjustment coefficients in Table 1609.7(2)

            - Plus and minus signs signify pressures acting toward and away from the building surfaces.

            - Negative pressures assume door has 2 feet of width in building’s end zone.

1609.7   Garage doors and rolling doors. Add to read as shown.

1609.7   Garage doors and rolling doors. Pressures from Table 1604.7(1) for wind loading actions on garage doors and rolling doors for buildings designed as enclosed shall be permitted.

Table 1609.7(2) Add text to read as shown.

TABLE 1609.7(2)

ADJUSTMENT FACTOR FOR BUILDING HEIGHT AND EXPOSURE, ( )

For SI: 1 foot = 304.8 mm.

a. All table values shall be adjusted for other exposures and heights by multiplying by the above coefficients.

Section 1609.8.  Add as a new section as follows.

1609.8   Rooftop structures and equipment. The lateral force on rooftop structures and equipment with Af less than(0.1Bh) located on buildings of all heights shall be determined from Equation 29.5-1 of ASCE 7 Eq. 6-28 in which the value of GCf is shall be taken as 3.1. GCf shall be permitted to be reduced linearly from 3.1 to 1.1 as the value of Af is increased from (0.1Bh) to (Bh). The value of G from Section 26.9 of ASCE 7 6.5.8 shall not be used. Additionally, a simultaneous uplift force shall be applied, given by Equation 29.5-1 of ASCE 7Eq. 6-28 in which GCf = 1.5 and Af is replaced by the horizontal projected area, Ar, of the rooftop structure or equipment. For the uplift force GCf shall be permitted to be reduced linearly from 1.5 to 1.0 as the value of Ar is increased from (0.1BL) to (BL).  (4143)

[S4685]

Chapter 1612 Flood Loads

Add Section 12.1.1 as follow:

1612.1.1 Cross references. See Table 1612.1.

| Table 1612.1 CROSS REFERENCES DEFINING FLOOD RESISTANT PROVISIONS OF THE FLORIDA BUILDING CODE |  |  |  |
| --- | --- | --- | --- |
| Florida Building Code – Building |  |  |  |
| Section |  | Section |  |
| Chapter 1 | Administration | Chapter 14 | Exterior Walls |
| 102 | Applicability | 1403 | Performance Requirements |
| 107 | Construction Documents |  |  |
| 110 | Inspections | Chapter 16 | Structural Design |
| 111 | Certificates of Occupancy and Completion | 1601 | General |
|  |  | 1603 | Construction Documents |
| Chapter 2 | Definitions | 1605 | Load Combinations |
| 202 | Definitions | 1612 | Flood Loads |
| Chapter 4 | Special Detailed Requirements Based on Use and Occupancy | Chapter 18 | Soils and Foundations |
| 419 | Hospitals | 1801 | General |
| 420 | Nursing Homes | 18031804 | Excavation, Grading and Fill |
| 424 | Swimming Pools and Bathing Places (Public And Private) | 1807 | Dampproofing and Waterproofing |
| Chapter 8 | Interior Finishes | Chapter 30 | Elevators and Conveying Systems |
| 801 | General | 3001 | General |
| Chapter 12 | Interior Environment | Chapter 31 | Special Construction |
| 1203 | Ventilation | 3102 | Membrane Structures |
| Florida Building Code – Residential |  |  |  |
| Section |  | Section |  |
| Chapter 2 | Definitions | Chapter 22 | Special Piping and Storage Systems |
| 202 | Definitions | M2201 | Oil Tanks |
| Chapter 3 | Building Planning | Chapter 24 | Fuel Gas |
| R301 | Design Criteria | G2404 (301) | General |
| R309 | Garages and Carports |  |  |
| R322 | Flood Resistant Construction | Chapter 26 | General Plumbing Requirements |
|  |  | P2601 | General |
| Chapter 4 | Foundations |  |  |
| R401 | General | Chapter 27 | Plumbing Fixtures |
| R408 | Under-Floor Space | P2705 | Installation |
| Chapter 13 | General Mechanical System Requirements | Chapter 30 | Sanitary Drainage |
| M1301 | General | P3001 | General |
| Chapter 14 | Heating and Cooling Equipment | Chapter 31 | Vents |
| M1401 | General | P3101 | Vent Systems |
| Chapter 16 | Duct Systems | Chapter 41 | Swimming Pools |
| M1601 | Duct Construction | R4101 | Private Swimming Pools |
| Chapter 17 | Combustion Air | Chapter 44 | High-Velocity Hurricane Zones |
| M1701 | General | R4403 | High-Velocity Hurricane Zones – General |
| Chapter 20 | Boilers and Water Heaters |  |  |
| M2001 | Boilers |  |  |
| Florida Building Code – Existing |  |  |  |
| Section |  | Section |  |
| Chapter 1 | Administration | Chapter 10 | Additions |
| 101 | General | 1003 | Structural |
| Chapter 2 202 | Definitions Definitions |  |  |
| Chapter 3 | Prescriptive Compliance Method | Chapter 11 | Historic Buildings |
| 302 | Additions, Alterations or Repairs | 1101 | General |
| 303 | Alterations |  |  |
| 304 | Repairs |  |  |
| Chapter 5 | Repairs | Chapter 12 | Relocated or Moved Buildings |
| 501 | General | 1202 | Requirements |
| 506 | Structural |  |  |
|  |  | Chapter 13 | Performance Compliance Methods |
| Chapter 6 | Alterations – Level I | 1301 | General |
| 601 | General |  |  |
| Florida Building Code – Mechanical |  |  |  |
| Section |  | Section |  |
| Chapter 3 | General Regulations | Chapter 6 | Duct Systems |
| M301 | General | M602 | Plenums |
|  |  | M603 | Duct Construction and Installation |
| Chapter 4 | Ventilation |  |  |
| M401 | General | Chapter 12 | Hydronic Piping |
|  |  | M1206 | Piping Installation |
| Chapter 5 | Exhaust Systems |  |  |
| M501 | General | Chapter 13 | Fuel Oil Piping and Storage |
|  |  | M1305 | Fuel Oil System Installation |
| Florida Building Code – Plumbing |  |  |  |
| Section |  |  |  |
| Chapter 3 | General Regulations |  |  |
| P309 | Flood Hazard Resistance |  |  |
| Florida Building Code – Fuel Gas |  |  |  |
| Section |  |  |  |
| Chapter 3 | General Regulations |  |  |
| FG301 | General |  |  |

[S4506]

[3891]

Section 1612.2 Definitions.

Add new term (Local Floodplain Management Ordinance) as follows:

LOCAL FLOODPLAIN MANAGEMENT ORDINANCE. An ordinance or regulation adopted pursuant to the authority granted to local governments by Title 44 Code of Federal Regulations, Sections 59 and 60 for participation in the National Flood Insurance Program.

[3885 A2]

Revise 1612.3 to read as follows:

1612.3 Establishment of flood hazard areas. To establish flood hazard areas, the applicable governing authority shall, by local floodplain management ordinance, adopt a flood hazard map and supporting data. The flood hazard map shall include, at a minimum, areas of special flood hazard as identified by the Federal Emergency Management Agency in an engineering report entitled “The Flood Insurance Study for [INSERT NAME OF JURISDICTION],” dated [INSERT DATE OF ISSUANCE], as amended or revised with the accompanying Flood Insurance Rate Map (FIRM) and Flood Boundary and Floodway Map (FBFM) and related supporting data along with any revisions thereto. The adopted flood hazard map and supporting data are hereby adopted by reference and declared to be part of this Section.

No change to the remaining text.

(3885 A2)

Revise 1612.5 to read as follows:

1612.5 Flood hazard documentation. The following documentation shall be prepared and sealed by a registered design professional and shall be submitted to the building official:

1.   For construction in flood hazard areas not subject to high-velocity wave action:

1.1.      The elevation of the lowest floor, including basement, as required by the foundation inspection and the final inspection in Section 110.3.lowest floor elevation inspection in Section 109.3.3.

1.2.      For fully enclosed areas below the design flood elevation where provisions to allow for the automatic entry and exit of floodwaters do not meet the minimum requirements in Section 2.6.2.1, ASCE 24, construction documents shall include a statement that the design will provide for equalization of hydrostatic flood forces in accordance with Section 2.6.2.2 of ASCE 24.

1.3.      For dry floodproofed nonresidential buildings, construction documents shall include a statement that the dry floodproofing is designed in accordance with ASCE 24.

2.   For construction in flood hazard areas subject to high-velocity wave action:

2.1.      The elevation of the bottom of the lowest horizontal structural member as required by the foundation inspection and the final inspection in Section 110.3109.3. lowest floor elevation inspection in Section 109.3.3.

[S4512]

2.2.      Construction documents shall include a statement that the building is designed in accordance with ASCE 24, including that the pile or column foundation and building or structure to be attached thereto is designed to be anchored to resist flotation, collapse and lateral movement due to the effects of wind and flood loads acting simultaneously on all building components, and other load requirements of Chapter 16.

2.3.      For breakaway walls designed to resist a nominal load of less that 10 psf (0.48 kN/m2) or more than 20 psf (0.96 kN/m2), construction documents shall include a statement that the breakaway wall is designed in accordance with ASCE 24. (3885)

Section 1613 Earthquake loads.  Reserved

High-Velocity Hurricane Zones

Revise Section 1615 HVHZ Minimum loads in order to add to it sections 1612, 1613, and 1614 for the purpose of maintaining the IBC09 format and at the same time minimize the level of formatting for the HVHZ sections.

See Chapter 16 - HVHZ

Chapter 17 Structural Tests and Special Inspections

Section 1702, add the following definitions.

Special Inspection. Reserved.

Special Inspection, Continuous. Reserved.

Special Inspection, Periodic. Reserved.

Structural Observation. Reserved.

Designated seismic system.  Reserved.

[S4693]

Garage Door Manufacturer.  The party responsible for the completed assembly of the garage door components.

Permanent Label.  A label that cannot be removed without noticeable damage.

Section 1703 Approvals.

1703.6.1 Follow-up inspection.  Change to read as shown.

1703.6.1 Follow-up inspection.  Reserved.

Section 1704 Special Inspections.  Change to read as shown.

Section 1704 Special Inspections.  Reserved

Section 1705 Statement of Special Inspections.  Change to read as shown.

Section 1705 Statement of Special Inspections. Reserved

Section 1706 Special Inspection for Wind Requirements.  Change to read as shown.

Section 1706 Special Inspection for Wind Requirements. Reserved

Section 1707 Special Inspection for Seismic Resistance.  Change to read as shown.

Section 1707 Special Inspection for Seismic Resistance. Reserved

Section 1708 Structural Testing for Seismic Resistance.  Change to read as shown.

Section 1708 Structural Testing for Seismic Resistance. Reserved

Section 1709 Structural Observations.  Change to read as shown.

Section 1709 Structural Observations. Reserved

Section 1715 Preconstruction Load Tests

Section 1715.3.2 Deflection.  Revise to read as follows:

1715.3.2 Deflection. The deflection of structural members under the design load shall not exceed the limitations in Section 1604.3. The HVHZ shall comply with Section 1613.1.

1715.5 Exterior window and door assemblies.  Change to read as shown.

- 1715.5 Exterior window and door assemblies.  This section defines performance and construction requirements for exterior window and door assemblies installed in wall systems. Waterproofing, sealing and flashing systems are not included in the scope of this section.

1715.5.1 Add text to read as shown.

1715.5.1  The design pressure for window and door assemblies shall be calculated in accordance with component and cladding wind loads in 1609.  The design pressures, as determined from ASCE 7, are permitted to be multiplied by 0.6.

1714.5.2 Exterior windows, sliding and patio glass doors.  Change to read as shown.

1715.5.2 Exterior windows, sliding and patio glass doors.

1715.5.2.1 Testing and labeling, add text to read as follows:

1715.5.2.1 Testing and labeling. Exterior windows and glass doors shall be tested by an approved independent testing laboratory, and shall be labeled to indicate compliance with the requirements of one of the following specifications:

ANSI/AAMA/NWWDA 101/I.S. 2 or ANSI/AAMA/WDMA/101/I.S. 2/NAFS or AAMA/WDMA/CSA 101/I.S. 2/A440 or TAS202 (HVHZ shall comply with TAS202 utilizing ASTM E 1300-98 or ASTM E 1300-04 or Section 2404).

Exterior windows and sliding glass doors shall be labeled with a permanent label, marking, or etching providing traceability to the manufacturer and product. The following shall also be required either on a permanent label or on a temporary supplemental label applied by the manufacturer: information identifying the manufacturer, the product model/series number, positive and negative design pressure rating, product maximum size, glazing thickness, impact-resistance rating if applicable, Florida Product Approval number or Miami-Dade Product Approval number, applicable test standard(s), and approved product certification agency, testing laboratory, evaluation entity or Miami-Dade Product Approval.

The labels are limited to one design pressure rating per reference standard. The temporary supplemental label shall remain on the window or door until final approval by the building official.

Exceptions:

1.	Door assemblies installed in nonhabitable areas where the door assembly and area are designed to accept water infiltration need not be tested for water infiltration.

2.	Door assemblies installed where the overhang (OH) ratio is equal to or more than 1 need not be tested for water infiltration. The overhang ratio shall be calculated by the following equation:

OH ratio = OH Length/OH Height

Where:

OH length = The horizontal measure of how far an overhang over a door projects out from door surface.

OH height = The vertical measure of the distance from the door sill to the bottom of the overhang over a door.

3.	Pass-through windows for serving from a single-family kitchen, where protected by a roof overhang of 5 feet (1.5 m) or more shall be exempted from the requirements of the water infiltration test.

Glass Strength: Products tested and labeled as conforming to ANSI/AAMA/NWWDA 101/I.S.2 or ANSI/AAMA/WDMA/101/I.S.2/NAFS or AAMA/WDMA/CSA 101/I.S.2/A440 or TAS 202 shall not be subject to the requirements of Sections 2403.2 or 2403.3 or 2404.1. Determination of load resistance of glass for specific loads of products not tested and certified in accordance with Section 1715.5.2.1 shall be designed to comply with ASTM E 1300 in accordance with Section 2404. The temporary supplemental label shall designate the type and thickness of glass or glazing material.

Section 1715.5.2.1.1 Testing and labeling of skylights is added to read as follows:

1715.5.2.1.1 Testing and labeling of skylights. Exterior skylights shall be tested by an approved independent testing laboratory, and shall be labeled to indicate compliance with the requirements of one of the following specifications:

ANSI/AAMA/WDMA 101/I.S.2/NAFS or AAMA/WDMA/CSA 101/I.S.2/A440, or TAS 202 (HVHZ shall comply with TAS 202).

Exterior skylights shall be labeled with a permanent label, marking, or etching providing traceability to the manufacturer and product. The following shall also be required either on a permanent label or on a temporary supplemental label applied by the manufacturer: information identifying the manufacturer, the product model/series number, positive and negative design pressure rating, product maximum size, type and thickness of glass or glazing material, impact-resistance rating if applicable, Florida Product Approval number or Miami-Dade Product Approval number, applicable test standard(s), and approved product certification agency, testing laboratory, evaluation entity or Miami-Dade Product Approval.

Labels are limited to one design pressure rating per reference standard. The temporary supplemental label shall remain on the skylight until final approval by the building official.

1715.6 5.2.1.2 Skylights and sloped glazing. Unit skylights and tubular daylighting devices (TDDs) shall comply with the requirements of Sections 1715.5.2.1.1 and 2405. All other skylights and sloped glazing shall comply with the requirements of Chapter 24. (4332)

Section 1715.5.2.2 Comparative analysis label, add text to read as follows:

1715.5.2.2 Comparative Analysis Label. A temporary supplemental label conforming to AAMA 203, Procedural Guide for the Window Inspection and Notification System, shall be acceptable for establishing and communicating the calculated allowable design pressures higher than indicated on the label required by Section 1715.5.2.1 for window or door sizes smaller than that required by the ANSI/AAMA/NWWDA 101/I.S.2 or ANSI/AAMA/WDMA 101/I.S.2/NAFS or AAMA/WDMA/CSA 101/I.S.2/A440 test requirements. This temporary supplemental label shall be applied by the manufacturer and remain on the window or door until final approval by the building official.

Exception 1:

Comparative analysis of operative windows and glazed doors may be made, provided the proposed unit complies with the following:

1.	Shall always be compared with a tested and currently approved unit.

2.	Varies only in width, height and/or load requirements.

3.	Shall not exceed 100 percent of the proportional deflection for fiber stress of the intermediate members of the approved unit.

4.	Shall conform as to extruded members, reinforcement and in all other ways with the tested approved unit.

5.	Shall not exceed 100 percent of the concentrated load at the juncture of the intermediate members and the frame of the approved unit.

6.	Shall not permit more air and water infiltration than the approved unit based on the height above grade.

7.	Compared unit shall not exceed the maximum cyclic pressure when tested per TAS 203 or ASTM E 1886 and ASTM E 1996.

Exception 2:

Comparative analysis of fixed glass windows may be made provided the proposed unit complies with the following:

1.	Shall always be compared with a tested and currently approved unit.

2.	Varies only in width, height and/or load requirements.

3.	The design is identical in all respects. e.g., extrusions, glazing system, joinery, fasteners, etc.

4.	Shall not permit more air and water infiltration than the approved unit based on height above grade.

5.	The maximum uniform load distribution (ULD) of any side is equal to the uniform load carried by the side divided by the length of the side.

6.	The ULD of any member must not exceed the ULD of the corresponding member of the tested window.

7.	The uniform load distribution on each member shall be calculated in accordance to Section 2, Engineering Design Rules, of the AAMA 103.3 Procedural Guide.

8.	Compared unit shall not exceed the maximum cyclic pressure when tested per TAS 201,TAS 202 and TAS 203 or ASTM E 1886 and ASTM E 1996.

Section 1715.5.3 Exterior door assemblies, add text to read as follows:

1715.5.3 Exterior door assemblies. Exterior door assemblies not covered by Section 1715.5.2 or Section 1715.5.3.1 shall be tested for structural integrity in accordance with ASTM E 330 Procedure A, at a load of 1.5 times the required design pressure load. The load shall be sustained for 10 seconds with no permanent deformation of any main frame or panel member in excess of 0.4 percent of its span after the load is removed. The design pressures, as determined from ASCE 7, are permitted to be multiplied by 0.6. High-velocity hurricane zones shall comply with TAS 202. After each specified loading, there shall be no glass breakage, permanent damage to fasteners, hardware parts, or any other damage which causes the door to be inoperable.

The minimum test sizes and minimum design pressures shall be as indicated in Table 1715.5.3.

The unit size tested shall qualify all units smaller in width and/or height of the same operation type and be limited to cases where frame, panels and structural members maintain the same profile as tested.

Exceptions:

1.         Door assemblies installed in nonhabitable areas where the door assembly and area are designed to accept water infiltration, need not be tested for water infiltration.

2.         Door assemblies installed where the overhang (OH) ratio is equal to or more than 1 need not be tested for water infiltration. The overhang ratio shall be calculated by the following equation:

OH ratio = OH Length/OH Height

where:

OH Length = The horizontal measure of how far an overhang over a door projects out from door’s surface.

OH Height = The vertical measure of the distance from the door’s sill to the bottom of the overhang over a door.[3631]

- Table 1715.5.3 Minimum Test Sizes, Including Framing.  Add to read as shown.

- TABLE 1715.5.3

MINIMUM TEST SIZES, INCLUDING FRAMING

| Performance Class1 | Width × Height (mm) | Width × Height (in.) | Minimum Performance Grade (Design Pressure) |
| --- | --- | --- | --- |
| Residential (R) | 900 × 2000 | (36 × 79) | 720 Pa (15 psf) |
| Light Commercial (LC) | 900 × 2100 | (36 × 83) | 1200 Pa (25 psf) |
| Commercial (C) | 1000 × 2100 | (40 × 83) | 1440 Pa (30 psf) |
| Heavy Commercial (HC) | 1200 × 2400 | (48 × 95) | 1920 Pa (40 psf) |
| Architectural (AW) | 1200 × 2400 | (48 × 95) | 1920 Pa (40 psf) |

1. Performance Class and Performance Grade per ANSI/AAMA/NWWDA 101/I.S.2.

1715.5.3.1 Add to read as shown.

1715.5.3.1 Sectional garage doors and rolling doors shall be tested for determination of structural performance under uniform static air pressure difference in accordance with ANSI/DASMA 108, ASTM E 330 Procedure A, or TAS 202.  For products tested in accordance with ASTM E 330, testing shall include a load of 1.5 times the required design pressure load sustained for 10 seconds, and acceptance criteria shall be in accordance with ANSI/DASMA 108.  (HVHZ shall comply with TAS 202.)  Design pressures, as determined from  Table 1609.7(1) or ASCE 7. The design pressure as determined from ASCE 7, are permitted to be multiplied by 0.6.

1715.5.3.2 Custom doors. Add to read as shown.

1715.5.3.2 Custom doors. Custom (one of a kind) exterior door assemblies shall be tested by an approved testing laboratory or be engineered in accordance with accepted engineering practices.

1715.5.3.3 Add to read as shown.

1715.5.3.3 Door components evaluated by an approved product evaluation entity, certification agency, testing laboratory or engineer may be interchangeable in exterior door assemblies provided that the door component(s) provide equal or greater structural performance as demonstrated by accepted engineering practices.

1715.5.3.3.1 Add to read as shown.

1715.5.3.3.1 Glazed curtain wall, window wall and storefront systems shall be tested in accordance with the requirements of this section and the Laboratory Test requirements of the American Architectural Manufacturers Association (AAMA) Standard 501, HVHZ shall comply with 2411.3.2.1.1.

- Exceptions:

- 1.	Door assemblies installed in nonhabitable areas where the door assembly and area are designed to accept water infiltration, need not be tested for water infiltration.

- 2.	Door assemblies installed where the overhang (OH) ratio is equal to or more than 1 need not be tested for water infiltration. The overhang ratio shall be calculated by the following equation:

- OH ratio = OH Length/OH Height

- where:

- OH Length = The horizontal measure of how far an overhang over a door projects out from door’s surface.

OH Height = The vertical measure of the distance from the door’s sill to the bottom of the overhang over a door.[3631]

1715.5.3.3.21 Optional exterior door component testing.  Add to read as shown.

- 1715.5.3.3.21 Optional exterior door component testing.  With the exception of HVHZ, exterior side-hinged door assemblies not covered by 1715.5.2 shall have the option to have the components of the assembly tested and rated for structural integrity in accordance with the following specification:

- SDI A250.13

Following the structural testing of exterior door components, there shall be no permanent deformation of any perimeter frame or panel member in excess of 0.4 percent of its span after the load is removed. After each specified loading, there shall be no glass breakage, permanent damage to fasteners, hardware parts, or any other damage that causes the door to be inoperable, as applicable. [3631]

Section 1715.5.3.4 Garage Door Labeling.  Add to read as shown.

1715.5.3.4 Garage Door Labeling.  Garage doors shall be labeled with a permanent label provided by the manufacturer.  The label shall identify the manufacturer, the garage door model/series number, the positive and negative design pressure rating, indicate impact rated if applicable, the installation instruction drawing reference number, the Florida Product Approval or Miami-Dade Product Approval number if applicable, and the applicable test standards.

The required garage door components for an approved garage door assembly may be indicated using a checklist format on the label.  If a checklist format is used on the label, the installer or manufacturer shall mark the selected components on the checklist that are required to assemble an approved garage door system.

The installation instructions shall be provided and available on the job site.

1715.5.4 Anchorage methods.  Add to read as shown.

1715.5.4 Anchorage methods.  The methods cited in this section apply only to anchorage of window and door assemblies to the main wind force resisting system.

1715.5.4.1 Anchoring requirements.  Add to read as shown.

1715.5.4.1 Anchoring requirements. Window and door assemblies shall be anchored in accordance with the published manufacturer’s recommendations to achieve the design pressure specified. Substitute anchoring systems used for substrates not specified by the fenestration manufacturer shall provide equal or greater anchoring performance as demonstrated by accepted engineering practice.

1715.5.4.2 Masonry, concrete or other structural substrate.  Add to read as shown.

1715.5.4.2 Masonry, concrete or other structural substrate.  Where the wood shim or buck thickness is less than 11/2 inches (38 mm), window and door assemblies shall be anchored through the main frame or by jamb clip or subframe system, in accordance with the manufacturer’s published installation instructions. Anchors shall be securely fastened directly into the masonry, concrete or other structural substrate material. Unless otherwise tested, bucks shall extend beyond the interior face of the window or door frame such that full support of the frame is provided. Shims shall be made from materials capable of sustaining applicable loads, located and applied in a thickness capable of sustaining applicable loads. Anchors shall be provided to transfer load from the window or door frame to the rough opening substrate.

Where the wood buck thickness is 11/2 inches (38 mm) or greater, the buck shall be securely fastened to transfer load to the masonry, concrete or other structural subtrate and the buck shall extend beyond the interior face of the window or door frame.  Window and door assemblies shall be anchored through the main frame or by jamb clip or subframe system or through the flange to the secured wood buck in accordance with the manufacturer’s published installation instructions. Unless otherwise tested, bucks shall extend beyond the interior face of the window or door frame such that full support of the frame is provided. Shims shall be made from materials capable of sustaining applicable loads, located and applied in a thickness capable of sustaining applicable loads. Anchors shall be provided to transfer load from the window or door frame assembly to the secured wood buck.

1715.5.4.3 Wood or other approved framing materials.  Add to read as shown.

1715.5.4.3 Wood or other approved framing materials.  Where the framing material is wood or other approved framing material, window and glass door assemblies shall be anchored through the main frame or by jamb clip or subframe system or through the flange in accordance with the manufacturer’s published installation instructions. Shims shall be made from materials capable of sustaining applicable loads, located and applied in a thickness capable of sustaining applicable loads.  Anchors shall be provided to transfer load from the window or door frame to the rough opening substrate.

1715.5.5 Mullions occurring between individual window and glass door assemblies.  Add to read as shown.

1715.5.5 Mullions occurring between individual window and glass door assemblies.

1715.5.5.1 Mullions.   Add to read as shown.

1715.5.5.1 Mullions. Mullions or mulled fenestration assemblies shall be tested by an approved testing laboratory in accordance with either AAMA 450, ASTM E 330, or TAS 202 (HVHZ shall comply with TAS 202), or shall be engineered in accordance with AAMA 450 using accepted engineering practice.  Mullions tested as stand-alone units or qualified by engineering shall use performance criteria cited in Sections 1715.5.5.2, 1715.5.5.3 and 1715.5.5.4.  Mullions qualified by an actual test of an entire assembly shall comply with Section 1715.5.5.4, except that mullions in assemblies requiring a deflection limitation, as defined in AAMA/WDMA/CSA 101/I.S.2/A440, shall meet 1715.5.5.2 and 1715.5.5.3.  Products not included within the scope of Section 1715.5.5.1 shall comply with Sections 1715.5.5.3 and 1715.5.5.4.

1715.5.5.2 Load transfer. Mullions shall be designed to transfer the design pressure loads applied by the window and door assemblies to the rough opening substrate.

1715.5.5.3 Deflection. Mullions shall be capable of resisting the design pressure loads applied by the window and door assemblies to be supported without deflecting more than L/175, where L is the span of the mullion in inches.

1715.5.5.4 Structural safety factor. Mullions that are tested by an approved testing laboratory shall be capable of resisting a load of 1.5 times the design pressure loads applied by the window and door assemblies to be supported. The design pressures, as determined from ASCE 7, are permitted to be multiplied by 0.6. The 1.5 times the design pressure load shall be sustained for 10 seconds, and the permanent deformation shall not exceed 0.2 percent of the mullion span for assemblies requiring deflection limitations, as defined in AAMA/WDMA/CSA 101/I.S.2/A440 and 0.4 percent of the mullion span for all other assemblies after the 1.5 times design pressure load is removed. Mullions that are qualified by engineering shall be capable of resisting the design pressure loads applied by the window and door assemblies to be supported without exceeding the allowable stress of the mullion elements.

1715.5.6 Glazed curtain wall, window wall and storefront systems shall be tested in accordance with the requirements of this section and the Laboratory Test requirements of the American Architectural Manufacturers Association (AAMA) Standard 501, HVHZ shall comply with 2411.3.2.1.1. [3631]

1715.6 Test specimens.  Add to read as shown.

1715.6 Test specimens. Test specimens and construction shall be representative of the materials, workmanship and details normally used in practice. The properties of the materials used to construct the test assembly shall be determined on the basis of tests on samples taken from the load assembly or on representative samples (when TAS 202 is used a minimum of three specimens) of the materials used to construct the load test assembly. Required tests shall be conducted or witnessed by an approved agency.

1715.7 Installation instruction for exterior windows and doors.  Add to read as shown.

1715.7 Installation instruction for exterior windows and doors.  Windows and doors shall be installed in accordance with the manufacturer’s installation instruction.

Section 1715.8 Impact resistant coverings.  Add to read as shown.

1715.8 Impact resistant coverings.

1715.8.1 Labels. A permanent label shall be provided by the product approval holder on all impact resistant coverings.

1715.8.2 The following information shall be included on the labels on impact resistant coverings:

- Product approval holder name and address.

- All applicable methods of approval. Methods of approval include, but are not limited to Miami-Dade NOA; Florida Building Commission, TDI Product Evaluation; ICC-ES.

- The test standard or standards specified at Section 1609.1.2 1609.1.4, including standards referenced within the test standards specified at Section 1609.1.2 1609.1.4 used to demonstrate code compliance.

- For products with a Florida Product Approval Number or a Miami-Dade County Building and NeighborhoodCode Compliance Office Department Notice of Acceptance Number (NOA), such numbers shall be included on the label.

[S4530]

1715.8.3 Location of label. The location of the label on the impact resistant covering shall be as follows:

- Accordions: Bottom of the locking bar or center mate facing the exterior or outside.

- Rollup: On the bottom of the hood facing the exterior or outside or on the bottom slat facing the exterior or outside.

- Bahama Awning or Colonial Hinged: On the bottom, placed on the back of the shutter.

- Panels: For metal and plastic panels the label may be embossed or printed spaced not more than every three (3) lineal feet on each panel. The label shall be applied by the holder of the product approval and shall face the exterior or outside.

- Framed products: The label shall be on the side or bottom facing the exterior or outside.

- Labels on all other products shall face the exterior or outside.

1715.8.4 Installation. All impact resistant coverings shall be installed in accordance with the manufacturer’s installation instructions and in accordance with the product approval. Installation instructions shall be provided and shall be available to inspection personnel on the job site. Opening protection components, fasteners, and other parts evaluated by an approved product evaluation entity, certification agency, testing laboratory, architect, or engineer and approved by the holder of the product approval may be interchangeable in opening protection assemblies provided that the opening protection component(s) provide equal or greater structural performance and durability as demonstrated by testing in accordance with approved test standards.

1715.9 Soffit.

1715.9.1 Product Approval. Manufactured soffit materials and systems shall be subject to statewide or local product approval as specified in FAC Rule 9N--3. The net free area of the manufactured soffit material or system shall be included in the product approval submittal documents.

1715.9.2 Labels. Individual manufactured soffit pieces shall be permanently marked at not more than four feet on center with a number or marking that ties the product back to the manufacturer.

1715.9.23 The following information shall be included on the manufactured soffit material packaging or on the individual manufactured soffit material or system pieces:

1.    Product approval holder and/or manufacturer name and city and state of manufacturing plant.

2.    Product model number or name.

3.    Method of approval and approval numbers as applicable. Methods of approval include, but are not limited to: Florida Building Commission FL #; Miami-Dade NOA; TDI Product Evaluation; and,  ICC-ES.

4.    The test standard or standards specified in Chapter 14 used to demonstrate code compliance.

5.    The net free area shall be included on the packaging or label. [3855]

1715.9.4 Installation. All manufactured soffit materials shall be installed in accordance with the manufacturer’s installation instructions and in accordance with the product approval. Installation instructions shall be provided and shall be available to inspection personnel on the job site. Soffit pieces, components, fasteners, and other parts evaluated by an approved product evaluation entity, certification agency, testing laboratory, architect, or engineer and approved by the holder of the product approval may be interchangeable in manufactured soffit systems provided that the soffit system component or components provide equal or greater structural performance and durability as demonstrated by testing in accordance with approved test standards.

All exterior wall coverings and soffits shall be capable of resisting the design pressures specified for walls for components and cladding loads in accordance with Section 1609.1. Manufactured soffits shall be tested at 1.5 times the design pressure. The design pressures, as determined from ASCE 7, are permitted to be multiplied by 0.6.

[S4694]

[3231]

Section 1716 Material and Test Standards

1716.1 Test standards for joist hangers and connectors. The vertical load-bearing capacity, torsional moment capacity and deflection characteristics of joist hangers and similar connectors shall be determined in accordance with either 1716.1.1 or 1716.1.2

1716.1.1 Test procedure using ASTM D 7147.  The load capacity of joist hangers and similar connectors shall be permitted to be determined using ASTM D 7147.

1716.1.12 Test procedure using ASTM D 1761 standards for joist hangers. The vertical load-bearing capacity, torsional moment capacity and deflection characteristics of joist hangers and similar connectors shall be permitted to be determined in accordance with ASTM D 1761 using lumber having a specific gravity of 0.49 or greater, but not greater than 0.55, as determined in accordance with AF&PA NDS for the joist and headers. 

Exception: The joist length shall not be required to exceed 24 inches (610 mm).

1716.1.2.1 Vertical load capacity for joist hangers. The vertical load capacity for the joist hanger shall be determined by testing a minimum of three joist hanger assemblies as specified in ASTM D 1761. If the ultimate vertical load for any one of the tests varies more than 20 percent from the average ultimate vertical load, at least three additional tests shall be conducted. The allowable vertical load of the joist hanger shall be the lowest value determined from the following:

1. The lowest ultimate vertical load for a single hanger from any test divided by three (where three tests are conducted and each ultimate vertical load does not vary more than 20 percent from the average ultimate vertical load).

2. The average ultimate vertical load for a single hanger from all tests divided by three (where six or more tests are conducted).

3. The average from all tests of the vertical loads that produce a vertical movement of the joist with respect to the header of 0.125 inch (3.2 mm).

4. The sum of the allowable design loads for nails or other fasteners utilized to secure the joist hanger to the wood members and allowable bearing loads that contribute to the capacity of the hanger.

5. The allowable design load for the wood members forming the connection.

1716.1.32.2 Torsional moment capacity for joist hangers. The torsional moment capacity for the joist hanger shall be determined by testing at least three joist hanger assemblies as specified in ASTM D 1761. The allowable torsional moment of the joist hanger shall be the average torsional moment at which the lateral movement of the top or bottom of the joist with respect to the original position of the joist is 0.125 inch (3.2 mm). [4411]

1716.1.42.3 Design value modifications for joist hangers. Allowable design values for joist hangers that are determined by Item 4 or 5 in Section 1715.1.2 shall be permitted to be modified by the appropriate duration of loading factors as specified in AF&PA NDS but shall not exceed the direct loads as determined by Item 1, 2 or 3 in Section 1715.1.2. Allowable design values determined by Item 1, 2 or 3 in Section 1715.1.2 and 2305.1 shall not be modified by duration of loading factors. [4411]

1716.2.1 Overturning resistance.  Change to read as shown.

1716.2.1 Overturning resistance.  Concrete and clay roof tiles shall be tested to determine their resistance to overturning due to wind in accordance with SBCCI SSTD 11 or TAS 108 (high-velocity hurricane zones shall comply with TAS 108) and Chapter 15.

1716.2.2 Wind tunnel testing.  Change to read as shown.

1716.2.2 Wind tunnel testing.  When roof tiles do not satisfy the limitations in Chapter 16 for rigid tile, a wind tunnel test shall be used to determine the wind characteristics of the concrete or clay tile roof covering in accordance with SBCCI SSTD 11 or TAS 108 (high-velocity hurricane zones shall comply with TAS 108) and Chapter 15.

Chapter 18 Soils and Foundations

Section 1801 General

1801.1 Scope.  Change to read as shown.

- 1801.1 Scope.  The provisions of this chapter shall apply to building and foundation systems in those areas not subject to scour or water pressure by wind and wave action. Buildings and foundations subject to such scour or water pressure loads shall be designed in accordance with Chapter 16.

Exception: Buildings and structures located within the high-velocity hurricane zone shall comply with the provisions of Section 1805, Sections 1816 through 1834, and as applicable in flood hazard areas, Section 1612. . [3457, 3887]

Section 1803 Geotechnical Investigations

1803.5.11 Seismic Design Categories C through F.  Reserved.

1803.5.12 Seismic Design Categories D through F.  Reserved.

Revise 1804.4 to read as follows:

1804.4 Grading and fill in flood hazard areas. In flood hazard areas established in Section 1612.3, grading and/or fill shall not be approved:

1. Unless fill is placed, compacted and sloped to minimize shifting, slumping and erosion during the rise and fall of flood water and, as applicable, wave action; and

2. In floodways, unless it has been demonstrated through hydrologic and hydraulic analyses performed by a registered design professional in accordance with standard engineering practice that the proposed grading or fill, or both, will not result in any increase in flood levels during the occurrence of the design flood.

3. In flood hazard areas subject to high-velocity wave action, unless such fill is conducted and/or placed to avoid diversion of water and waves toward any building or structure.

4. Where design flood elevations are specified but floodways have not been designated, unless it has been demonstrated that the cumulative effect of the proposed flood hazard area encroachment, when combined with all other existing and anticipated flood hazard area encroachment, will not increase the design flood elevation more than one foot (305mm) at any point. [3887]

Change Section 1805 Dampproofing and Waterproofing to read as follows:

Section 1805 Dampproofing and Waterproofing

1805.4.3 Drainage discharge.  Change to read as shown.

- 1805.4.3 Drainage discharge.  The floor base and foundation perimeter drain shall discharge by gravity or mechanical means into an approved drainage system that complies with the Florida Building Code, Plumbing.

Exception: Where a site is located in well-drained gravel or sand/gravel mixture soils, a dedicated drainage system is not required.

1807.1.3 Rubble stone foundation walls.  Revise as follows:

1807.1.3 Rubble stone foundation walls.  Foundation walls of rough or random rubble stone shall not be less than 16 inches (406 mm) thick.

1807.1.6.2.1 Seismic requirements.  Change to read as shown.

1807.1.6.2.1 Seismic requirements. Reserved.

1807.1.6.3.2 Seismic requirements.  Change to read as shown.

1807.1.6.3.2 Seismic requirements. Reserved.

Revise 1807.2 Retaining walls to read as follows:

1807.2 Retaining walls 1807.1 General.  Walls built to retain or support the lateral pressure of earth or water or other superimposed loads shall be designed and constructed of masonry, concrete, steel sheet piling or other approved materials.

1807.2 Design.  Add to read as shown.

1807.2.1 Design.  Retaining walls shall be designed to resist the design lateral soil loads in Section 1610, including both dead and live load surcharges to which such walls are subjected, and to ensure stability against overturning, sliding, excessive foundation pressure and water uplift.

1807.3 Hydrostatic pressure.  Add to read as shown.

1807.2.2 1807.3 Hydrostatic pressure.  Unless drainage is provided, the hydrostatic head of the water pressure shall be assumed to be equal to the height of the wall.

1807.4 Reinforced masonry retaining walls.  Add to read as shown.

1807.2.3 1807.4 Reinforced masonry retaining walls.  Vertical reinforcement for masonry retaining walls shall comply with Table 1806.4 or shall be designed in accordance with ACI 530/ASCE 5/TMS 402. Masonry shall be fully grouted with a minimum f’m of 1,500 psi (10 343 kPa). Mortar for masonry shall be Type M or S and laid in running bond. The specified location of the reinforcement shall equal or exceed the effective depth distance, d, noted in Table 1807.2.3 1806.4 and shall be measured from the exposed side of the wall to the center of the vertical reinforcement. Footings for reinforced masonry retaining walls shall be designed in accordance with ACI 318.

1807.5 Segmental retaining walls.  Add to read as shown.

1807.2.4 1807.5 Segmental retaining walls.  Segmental retaining walls shall be designed in accordance with NCMA Design Manual for Segmental Retaining Walls.

Table 1807.4 Reinforcement for Masonry Retaining Walls.  Add to read as shown.

TABLE 1807.2.3 1807.4

REINFORCEMENT FOR MASONRY RETAINING WALLSa

| Nominal Wall thickness in. (mm) | Wall depth, H, ft (m) | Reinforcement size & spacing for equivalent fluid weight of soil, pcf (kN/m3), of: |  |  |
| --- | --- | --- | --- | --- |
|  |  | 30 (4.7) | 45 (7.1) | 60 (9.4) |
| 8 (203) | 4.0 (1.2) 4.7 (1.4) 5.3 (1.6) 6.0 (1.8) 6.7 (2.0) | #4 at 64 in. #4 at 40 in. #4 at 24 in. #5 at 24 in. #5 at 16 in. | #4 at 40 in. #4 at 24 in. #4 at 16 in. #6 at 16 in. #6 at 8 in. | #4 at 32 in. #4 at 16 in. #5 at 16 in. #8 at 16 in. = |
| 10 (254) | 4.0 (1.2) 4.7 (1.4) 5.3 (1.6) 6.0 (1.8) 6.7 (2.0) 7.3 (2.2) 8.0 (2.4) | #4 at 72 in. #4 at 56 in. #4 at 40 in. #4 at 24 in. #4 at 16 in. #5 at 24 in. #5 at 16 in. | #4 at 64 in. #4 at 40 in. #4 at 24 in. #4 at 16 in. #5 at 16 in. #6 at 16 in. #6 at 8 in. | #4 at 48 in. #4 at 24 in. #4 at 16 in. #5 at 16 in. #6 at 16 in. #6 at 8 in. = |
| 12 (305) | 4.0 (1.2) 4.7 (1.4) 5.3 (1.6) 6.0 (1.8) 6.7 (2.0) 7.3 (2.2) 8.0 (2.4) 8.7 (2.7) 9.3 (2.8) | #4 at 72 in. #4 at 72 in. #4 at 48 in. #4 at 32 in. #4 at 24 in. #4 at 16 in. #5 at 24 in. #5 at 16 in. #6 at 16 in. | #4 at 72 in. #4 at 48 in. #4 at 32 in. #4 at 24 in. #4 at 16 in. #5 at 16 in. #5 at 16 in. #7 at 16 in. #7 at 8 in. | #4 at 64 in. #4 at 40 in. #4 at 24 in. #4 at 16 in. #5 at 16 in. #6 at 16 in. #7 at 16 in. #7 at 8 in. = |

a. Based on fully grouted masonry; f ‘m = 1500 psi (10.3 MPa); d = 5 in., 7 in. and 9 in. (127, 178 and 229 mm) for wall thicknesses of 8, 10, and 12 in. (203, 254, and 305 mm), respectively; level backfill to top of wall.

[S4696]

Section 1808  Foundations

1808.3.1 Seismic overturning.  Change to read as shown.

1808.3.1 Seismic overturning.  Reserved.

1808.8.6 Seismic requirements.  Change to read as shown.

1808.8.6 Seismic requirements.  Reserved.

Table 1808.8.1 Minimum specified Compressive Strength f’c of Concrete or Grout.   Change to read as shown.  [Remove seismic language.]

1. Foundations for structures assigned to Seismic Design Category A, B or C

2a. Reserved Foundations for Group R or U occupancies of light-frame construction, two stories or less in height,

assigned to Seismic Design Category D, E or F                                            2,500 psi

2b. Reserved Foundations for other structures assigned to Seismic Design Category D, E, or F                               3,000 psi

[S4698]

For SI: 1 pound per square inch = 0.00689MPa.

1809.5 Fire Protection – Change to read as shown.

1809.5 Frost protection. Except where otherwise protected from frost, foundations and other permanent supports of buildings and structures shall be protected from frost by one or more of the following methods:

1. Extending below the frost line of the locality;

2. Constructing in accordance with ASCE 32; or

3. Erecting on solid rock.

Exception: Free-standing buildings meeting all of the following

conditions shall not be required to be protected:

1. Assigned to Risk Occupancy Category I, in accordance with Section 1604.5;

2. Area of 600 square feet (56m2) or less for light-frame construction or 400 square feet (37 m2) or less for

other than light-frame construction; and

3. Eave height of 10 feet (3048 mm) or less.

Shallow foundations shall not bear on frozen soil unless such frozen condition is of a permanent character.

[S4700]

TABLE 1809.7

FOOTINGS SUPPORTING WALLS OF LIGHT-FRAME CONSTRUCTIONa, b, c, d, e

Revise footnotes to reserve footnote “d”.

1809.10 Pier and curtain wall foundations. – Change to read as shown.

Reserved. Except in Seismic Design Categories D, E and F, pier and curtain wall foundations shall be permitted to be used to support light-frame construction not more than two stories above grade plane, provided the following requirements are met:
1. All load-bearing walls shall be placed on continuous concrete footings bonded integrally with the exterior
wall footings.
2. The minimum actual thickness of a load-bearing masonry wall shall not be less than 4 inches (102 mm)nominal or 35/8 inches (92 mm) actual thickness, and shall be bonded integrally with piers spaced 6 feet (1829
mm) on center (o.c.).

3. Piers shall be constructed in accordance with Chapter 21 and the following:
3.1. The unsupported height of the masonry piers shall not exceed 10 times their least dimension.
3.2. Where structural clay tile or hollow concrete masonry units are used for piers supporting beams and girders, the cellular spaces shall be filled solidly with concrete or Type M or S mortar.
Exception: Unfilled hollow piers shall be permitted where the unsupported height of the pier is not more
than four times its least dimension.

3.3. Hollow piers shall be capped with 4 inches (102 mm) of solid masonry or concrete or the cavities of the top course shall be filled with concrete or
grout.
4. The maximum height of a 4-inch (102 mm) load-bearing masonry foundation wall supporting wood frame walls and floors shall not be more than 4 feet (1219 mm) in height.
5. The unbalanced fill for 4-inch (102 mm) foundation walls shall not exceed 24 inches (610 mm) for solid masonry, nor 12 inches (305 mm) for hollow masonry.

[S4702]

1810.2.4.1  Seismic Design Categories D through F.  Reserved.

1809.13 Footing seismic ties.  Change to read as shown.

1809.13 Footing seismic ties. Reserved.

1810.2.4.1 Seismic Design Categories D through F.  Change to read as shown.

1810.2.4.1 Seismic Design Categories D through F.  Reserved.

1810.3.2.1.1 Seismic hooks.  Change to read as shown.

1810.3.2.1.1 Seismic hooks.  Reserved.

1810.3.3.1.5 Uplift capacity of a single deep foundation element. Change to read as shown.

1810.3.3.1.5 Uplift capacity of a single deep foundation element. Where required by the design, the uplift capacity of a single deep foundation element shall be determined by an approved method of analysis based on a minimum factor of safety of three or by load tests conducted in accordance with ASTM D 3689. The maximum allowable uplift load shall not exceed the ultimate load capacity as determined in Section 1810.3.3.1.2, using the results of load tests conducted in accordance with ASTM D 3689, divided by a factor of safety of two.

Exception: Where uplift is due to wind or seismic loading, the minimum factor of safety shall be two where capacity is determined by an analysis and one and one-half where capacity is determined by load tests.

1810.3.5.3.2 Steel pipes and tubes. Change to read as shown.

1810.3.5.3.2 Steel pipes and tubes. Steel pipes and tubes used as deep foundation elements shall have a nominal outside diameter of not less than 8 inches (203 mm). Where steel pipes or tubes are driven open ended, they shall have a minimum of 0.34 square inch (219mm2) of steel in cross section to resist each 1,000 foot-pounds (1356 Nm) of pile hammer energy, or shall have the equivalent strength for steels having a yield strength greater than 35,000 psi (241 MPa) or the wave equation analysis shall be permitted to be used to assess compression stresses induced by driving to evaluate if the pile section is appropriate for the selected hammer. Where a pipe or tube with wall thickness less than 0.179 inch (4.6 mm) is driven open ended, a suitable cutting shoe shall be provided. Concrete-filled steel pipes or tubes in structures assigned to Seismic Design Category C, D, E or F shall have a wall thickness of not less than 3/16 inch (5 mm). The pipe or tube casing for socketed drilled shafts shall have a nominal outside diameter of not less than 18 inches (457 mm), a wall thickness of not less than 3/8 inch (9.5 mm)and a suitable steel driving shoe welded to the bottom; the diameter of the rock socket shall be approximately equal to the inside diameter of the casing.

Exceptions:

1. There is no minimum diameter for steel pipes or tubes used in micropiles.

2. For mandrel-driven pipes or tubes, the minimum wall thickness shall be 1/10 inch (2.5 mm).

1810.3.6.1 Seismic Design Categories C through F.  Change to read as shown.

1810.3.6.1 Seismic Design Categories C through F.  Reserved.

1810.3.8.2.2 Seismic reinforcement in Seismic Design Categories C through F.  Change to read as shown.

1810.3.8.2.2 Seismic reinforcement in Seismic Design Categories C through F.  Reserved.

1810.3.8.2.3 Additional seismic reinforcement in Seismic Design Categories D through F.  Change to read as shown.

1810.3.8.2.3 Additional seismic reinforcement in Seismic Design Categories D through F.  Reserved.

1810.3.8.3.2 Seismic reinforcement in Seismic Design Category C.  Change to read as shown.

1810.3.8.3.2 Seismic reinforcement in Seismic Design Category C.  Reserved.

1810.3.8.3.3 Seismic reinforcement in Seismic Design Categories D through F.  Change to read as shown.

1810.3.8.3.3 Seismic reinforcement in Seismic Design Categories D through F.  Reserved.

1810.3.9.4 Seismic reinforcement.  Change to read as shown.

1810.3.9.4 Seismic reinforcement.  Reserved.

1810.3.9.4.1 Seismic reinforcement in Seismic Design Category C.  Change to read as shown.

1810.3.9.4.1 Seismic reinforcement in Seismic Design Category C.  Reserved.

1810.3.9.4.2 Seismic reinforcement in Seismic Design Categories D through F.  Change to read as shown.

1810.3.9.4.2 Seismic reinforcement in Seismic Design Categories D through F.  Reserved.

1810.3.10.4 Seismic reinforcement.  Change to read as shown.

1810.3.10.4 Seismic reinforcement.  Reserved.

1810.3.11.1 Seismic Design Categories C through F.  Change to read as shown.

1810.3.11.1 Seismic Design Categories C through F.  Reserved.

1810.3.11.2 Seismic Design Categories D through F.  Change to read as shown.

1810.3.11.2 Seismic Design Categories D through F.  Reserved.

1810.3.12 Grade beams.   Change to read as shown.

1810.3.12 Grade beams.   Reserved.

1810.3.13 Seismic ties.  Change to read as shown.

1810.3.13 Seismic ties.   Reserved.

1810.4.12 Special Inspection. Change to read as shown.

1810.4.12 Special Inspection.  Reserved.

Sections 1811 – 1815 Reserved.  Add to read as shown.

Sections 1811 – 1815 Reserved.

Section 1816 Termite Protection.  Add to read as shown.

Section 1816 Termite Protection

1816.1 Termite protection.  Add to read as shown.

1816.1 Termite protection.  Termite protection shall be provided by registered termiticides, including soil applied pesticides, baiting systems, and pesticides applied to wood, or other approved methods of termite protection labeled for use as a preventative treatment to new construction. See Section 202, Registered Termiticide. Upon completion of the application of the termite protective treatment, a certificate of compliance shall be issued to the building department by the licensed pest control company that contains the following statement: “The building has received a complete treatment for the prevention of subterranean termites. Treatment is in accordance with rules and laws established by the Florida Department of Agriculture and Consumer Services.”

1816.1.1 Add to read as shown.

1816.1.1 If soil treatment is used for subterranean termite prevention, the initial chemical soil treatment inside the foundation perimeter shall be done after all excavation, backfilling and compaction is complete.

1816.1.2 Add to read as shown.

1816.1.2 If soil treatment is used for subterranean termite prevention, soil area disturbed after initial chemical soil treatment shall be retreated with a chemical soil treatment, including spaces boxed or formed.

1816.1.3 Add to read as shown.

1816.1.3 If soil treatment is used for subterranean termite prevention, space in concrete floors boxed out or formed for the subsequent installation of plumbing traps, drains or any other purpose shall be created by using plastic or metal permanently placed forms of sufficient depth to eliminate any planned soil disturbance after initial chemical soil treatment.

1816.1.4 Add to read as shown.

1816.1.4 If soil treatment is used for subterranean termite prevention, chemically treated soil shall be protected with a minimum 6 millimeter vapor retarder to protect against rainfall dilution. If rainfall occurs before vapor retarder placement, retreatment is required. Any work, including placement of reinforcing steel, done after chemical treatment until the concrete floor is poured, shall be done in such manner as to avoid penetrating or disturbing treated soil.

1816.1.5 Add to read as shown.

1816.1.5 If soil treatment is used for subterranean termite prevention, concrete overpour or mortar accumulated along the exterior foundation perimeter shall be removed prior to exterior chemical soil treatment, to enhance vertical penetration of the chemicals.

1816.1.6 Add to read as shown.

1816.1.6 If soil treatment is used for subterranean termite prevention, chemical soil treatments shall also be applied under all exterior concrete or grade within 1 foot (305 mm) of the primary structure sidewalls. Also, a vertical chemical barrier shall be applied promptly after construction is completed, including initial landscaping and irrigation/sprinkler installation. Any soil disturbed after the chemical vertical barrier is applied shall be promptly retreated.

1816.1.7 Add to read as shown.

1816.1.7 If a registered termiticide formulated and registered as a bait system is used for subterranean termite prevention, Sections 1816.1.1 through 1816.1.6 do not apply; however, a signed contract assuring the installation, maintenance and monitoring of the baiting system for a minimum of five years from the issue of the certificate of occupancy shall be provided to the building official prior to the pouring of the slab, and the system must be installed prior to final building approval. If the baiting system directions for use require a monitoring phase prior to installation of the pesticide active ingredient, the installation of the monitoring phase components shall be deemed to constitute installation of the system.

Section 1816.1.8, add to read as shown.

1816.1.8   If a registered termiticide formulated and registered as a wood treatment is used for subterranean termite prevention, Sections 1816.1.1 through 1816.1.6 do not apply.  Application of a wood treatment termiticide shall be as required by label directions for use, and must be completed prior to final building approval.  Changes in framing or additions to  framing in areas of the structure requiring treatment that occur after the initial wood treatment must be treated prior to final building approval.

Section 1816.2 Penetration, add text to read as follows:

1816.2 Penetration. Protective sleeves around piping penetrating concrete slab-on-grade floors shall not be of cellulose-containing materials. If soil treatment is used for subterranean termite protection, the sleeve shall have a maximum wall thickness of 0.010 inch, and be sealed within the slab using a non-corrosive clamping device to eliminate the annular space between the pipe and the sleeve. No termiticides shall be applied inside the sleeve.

Section 1817 through Section 1834, HVHZ.  See the 2007 Florida Building Code.

Section 1817 through Section 1834, HVHZ

Also, see Chapter 18 - HVHZ

Chapter 19 Concrete

Section 1901 General

1901.1 Scope.  Change to read as shown.

- 1901.1 Scope.  The provisions of this chapter shall govern the materials, quality control, design and construction of concrete used in structures.

Exception: Buildings and structures located within the high-velocity hurricane zone shall comply with the provisions of Sections 1917 and 1919 through 1929.

1901.5 Special inspection.  Change to read as shown.

1901.5 Special inspection.  Reserved.

Section 1908 Modifications to ACI 318.  Change to read as shown.

Section 1908 Modifications to ACI 318.  Reserved.

Section 1910 Minimum Slab Provisions

- 1910.2 Joints.  Add to read as shown.

- 1910.2 Joints.  Concrete slabs on ground shall be provided with joints in accordance with ACI 224.3R or other approved methods. Joints shall be designed by an architect or engineer.

- Exception: Joints are not required in unreinforced plain concrete slabs on ground or in slabs for one- and two-family dwellings complying with one of the following:

- 1.	Concrete slabs on ground containing synthetic fiber reinforcement. Fiber lengths and dosage amounts shall comply with one of the following

- (1)	Fiber lengths shall be 1/2 inch to 2 inches (13 to 51 mm) in length. Dosage amounts shall be from 0.75 to 1.5 pounds per cubic yard (0.45 to 0.89 kg/m3) in accordance with the manufacturer’s recommendations. Synthetic fibers shall comply with ASTM C 1116. The manufacturer or supplier shall provide certification of compliance with ASTM C 1116 when requested by the building official; or,

(2)	Fiber length shall be from 1/2 inch to 2 inches (13 mm to 51 mm) in length, monofilament or fibrillated. Dosage amounts shall be from 0.5 to 1.5 pounds per cubic yard (0.30 to 0.89 kg/m3) to achieve minimum 40 percent reduction of plastic shrinkage cracking of concrete versus a control mix in accordance with ICBO AC32. Independent test results using minimum six (6) test specimens shall be provided to the building official showing compliance with ICBO A32. Synthetic fiber shall comply with ASTM C1116, Paragraph 4.1.3, Type III. The manufacturer or supplier shall provide certification of compliance with ASTM C1116 when requested by building official.

2.	Concrete slabs on ground containing 6x6 W1.4 × W1.4 welded wire reinforcement fabric located in the middle to the upper one-third of the slab. Welded wire reinforcement fabric shall be supported with approved materials or supports at spacings not to exceed 3 feet (914 mm) or in accordance with the manufacturer’s specifications. Welded plain wire reinforcement fabric for concrete shall conform to ASTM A 185, Standard Specification for Steel Welded Wire Reinforcement Fabric, Plain, for Concrete Reinforcement.

Section 1911 Anchorage to Concrete—Allowable Stress Design

1911.1 Scope.  Change to read as shown.

1911.1 Scope. The provisions of this section shall govern the allowable stress design of headed bolts and headed stud anchors cast in normal-weight concrete for purposes of transmitting structural loads from one connected element to the other. These provisions do not apply to anchors installed in hardened concrete or where load combinations include earthquake loads or effects. The bearing area of headed anchors shall be not less than one and one-half times the shank area. Where strength design is used, or where load combinations include earthquake loads or effects, the design strength of anchors shall be determined in accordance with Section 1912. Bolts shall conform to ASTM A 307 or an approved equivalent.

Section 1912 Anchorage to Concrete—Strength Design

1912.1 Scope.  Change to read as shown.

1912.1 Scope. The provisions of this section shall govern the strength design of anchors installed in concrete for purposes of transmitting structural loads from one connected element to the other. Headed bolts, headed studs and hooked (J- or L-) bolts cast in concrete and expansion anchors and undercut anchors installed in hardened concrete shall be designed in accordance with Appendix D of ACI 318 as modified by Sections 1908.1.9 and 1908.1.10, provided they are within the scope of Appendix D. The strength design of anchors that are not within the scope of Appendix D of ACI 318, and as amended in Sections 1908.1.9 and 1908.1.10, shall be in accordance with an approved procedure.

Sections 1916-1929 Add per the 2007 Florida Building Code.

Section 1916 Reserved

Section 1917 Lightweight Insulating Concrete Roof Deck

SECTION 1917

LIGHTWEIGHT INSULATING CONCRETE ROOF DECK

1917.1 Lightweight insulating concrete. Material produced with or without aggregate additions to portland cement, water and air to form a hardened material possessing insulating qualities, which, when oven dried shall have a unit weight no greater than 50 pcf (801 kg/m3).

1917.1.1 Aggregate lightweight insulating concrete. Insulating concrete formulated predominantly with perlite or vermiculite aggregate having a minimum compressive strength of 125 psi (861.8 kPa) when tested in compliance with ASTM C 495.

1917.1.2 Cellular lightweight insulating concrete. Insulating concrete formulated by mixing a hydrated cementitious matrix around noninterconnecting air cells created by the addition of preformed foam formed from hydrolyzed proteins or synthetic surfactants. The cured cellular lightweight insulating concrete shall have minimum compressive strength of 160 psi (1103 kPa) when tested in compliance with ASTM C 495 and C 796.

1917.1.3 Cellular/aggregate (hybrid) lightweight insulating concrete. Insulated concrete formulated by combining preformed foam with low density aggregates to impart properties of both aggregate and cellular lightweight insulating concrete. It shall have a minimum compressive strength of 200 psi (1379 kPa) when tested in compliance with ASTM C 495 and C 796.

1917.1.4 Walkability. A term defining the ability of lightweight insulating concrete to withstand anticipated construction foot traffic during the roof membrane application without significant indentations in the lightweight insulating concrete surface.

1917.2 Inspection.

1917.2.1 Application of all lightweight insulating concrete roof decks shall be by applicators approved by the lightweight insulating concrete deck manufacturer. Product Approval shall be required for all lightweight insulating concrete systems.

1917.2.2 The permit holder shall notify the building official 48 hours prior to the pouring of lightweight insulating concrete.

1917.2.3 The permit holder shall make available to the building official a job log with the following minimum items.

1.	Cast density recordings/hour.

2.	Product evaluation for application.

3.	Date and job locations identified.

4.	Results of any field test conducted.

1917.2.4 Once the roof deck system can support foot traffic, the building official shall have clear access and clear path at his option for inspection of lightweight insulating concrete.

1917.3 Testing. The building official may require tests of the lightweight insulating concrete to confirm the fastener withdrawal resistance, compressive strength or drainage ability.

1917.3.1 Existing roof assemblies to receive lightweight insulating concrete other than galvanized G-90 steel deck or structural concrete deck shall be tested for uplift for adhesion to the substrate to confirm compliance with design pressure.

1917.4 Materials and limitations of use. Lightweight insulating concrete, in conjunction with galvanized formed steel sheets, shall not be used as a roof deck in areas where highly corrosive chemicals are used or stored.

1917.4.1 Lightweight insulating concrete shall be poured over bottom slotted galvanized (G-90) steel decking as follows; cellular, 0.5 percent open; hybrid, 0.75 percent open, aggregate 1.5 percent open. No lightweight insulating concrete shall be poured over a painted or non-galvanized steel deck.

1.	Lightweight insulating concrete over structural concrete slabs, twin tees, precast units or other non venting substrates shall be vented to allow the escape of excess moisture.

1917.4.2 Minimum thickness of lightweight insulating concrete shall be 2 inches (51 mm) over the top plane of the substrate unless otherwise specified in the Product Approval. Lightweight insulating concrete shall be of sufficient thickness to receive the specified base ply fastener length.

1917.4.3 Reserved.

1917.4.4 Galvanized coatings of formed steel sheets shall be in accordance with ASTM A 525 with a minimum coating designation of G-90. Base steel shall conform to ASTM A 446, Grade A, B, C, D or greater and ASTM A 611 C, D or E.

1917.4.5 Chemical admixtures shall be in compliance with ASTM C 494. Calcium chloride or any admixture containing chloride salts shall not be used in insulating concrete. Fiber reinforcement may be used to control cracking. Mineral admixtures shall conform to ASTM C618.

1917.4.6 Vermiculite or perlite shall be in compliance with ASTM C332, Group I. Foam concentrates shall be in compliance with ASTM C796 and ASTM C869.

1917.4.7 Mixing, placing and finishing shall be in compliance with the deck system Product Approval. Slurry coating, two-density casting and double casting shall be acceptable per the specific manufacturer's recommendations.

1917.4.8 If the lightweight insulating concrete deck is to receive Product Approval for a direct-adhered roofing system, the deck surface shall be prepared to the requirements set forth in the roof system Product Approval.

1917.4.9 All base ply fasteners for use in lightweight insulating concrete roof decks shall have a Product Approval for use with the specific lightweight insulating concrete roof system in compliance with manufacturer's recommendations and the design pressure of Section 1609.

1917.4.10 The lightweight insulating concrete fastener withdrawal shall have a minimum resistance for new pours of

1.	60 pounds (267 N) in 28 days when the fastener is installed and allowed to age in the concrete.

2.	40 pounds (178 N) at time of roofing.

1917.4.11 Lightweight insulating concrete system expansion joints shall be provided at the following locations:

1.	Where expansion joints are provided in the structural assembly.

2.	Where steel framing, structural steel or decking change direction

3.	Where separate wings of "L," "U," "T" or similar configurations exist

4.	Where the type of decking changes (for example, where a precast concrete deck and a steel deck abut)

5.	Whenever additions are connected to existing buildings.

6.	At junctions where interior heating conditions change

7.	Wherever differential movement between vertical walls and the roof deck may occur.

1917.4.12 Insulation board with lightweight insulating concrete shall conform to Type I expanded polystyrene insulation as defined in ASTM C578.

1.	Packaged insulation board delivered to the job site shall comply with the provisions of Section 2603.2 or Section 2612.1.3.

2.	Installation of insulating board in conjunction with lightweight insulating concrete shall comply with uplift requirements set forth in Section 1609. Insulation panels shall be placed in a minimum 1/8-inch (3.2 mm) slurry bed of insulating concrete while the material is still in a plastic state. The insulating concrete shall be cast over the insulation boards according to the insulating concrete manufacturer's Product Approval. Insulation panels shall be provided with holes and/or slots for keying and venting.

1917.4.13 Reinforcing mesh shall be provided as required to meet fire-rating and/or special structural design requirements. Refer to a specific Product Approval for the specific requirements applicable to the product being installed.

Section 1918 Special Wind Provisions For Concrete

SECTION 1918

SPECIAL WIND PROVISIONS FOR CONCRETE

1918.1 Reinforced concrete components. The design and construction of reinforced concrete components for buildings sited in areas where the ultimate design wind speed, Vult, is with a basic wind speed greater than 115 100 mph (45 m/s) in accordance with Figure 1609 shall conform to the requirements of ACI 318 or with Section 1609.1.1, Exception 13, as applicable, except as modified in this section.

1918.2 Insulated concrete form wall. Insulated concrete form (ICF) wall construction for buildings shall be in accordance with ACI 318 or with Section 1609.1.1, Exception 12, as applicable.

Comment after Glitch

1918.3 Gable endwalls.

1918.3.1 General. Gable endwalls shall be structurally continuous between points of lateral support.

1918.3.2 Cathedral endwalls. Gable endwalls adjacent to cathedral ceilings shall be structurally continuous from the uppermost floor to ceiling diaphragm or to the roof diaphragm.

Section 1919 through Section 1929, HVHZ

See Chapter 19 – HVHZ.

Chapter 20, Aluminum.  Add per the 2007 Florida Building Code.

Chapter 20, Aluminum.

[Note: for text of this Chapter see the 2007 Florida Building Code, Building available on-line from www.Floridabuilding.org]

2001.1 Scope. Provisions of this chapter shall govern the quality, design, fabrication and erection of aluminum alloys used in building construction.

Exception: Buildings and structures located within the high-velocity hurricane zone shall comply with the provisions of Section 2003.

SECTION 2002

MATERIALS

2002.1 General. The quality, design, fabrication and erection of aluminum used structurally in buildings or structures shall conform to good engineering practice, the provisions of this chapter and other applicable requirements of this code.

Exception: All buildings located within the high-velocity hurricane zone shall comply with the requirements of Section 2003.

2002.2 Structural aluminum construction. The design, fabrication and assembly of structural aluminum for buildings or structures shall conform to AA ASM 35 and Specifications for Aluminum Structures, Aluminum Design Manual, Part 1-A and 1-B, of the Aluminum Association. The use of aluminum alloys not listed in the manual shall be permitted provided their standard of performance is not less than those required in the manual and the performance is substantiated to the satisfaction of the building official.

2002.2.1 Definitions

PRIMARY MEMBER. Structural framing members providing structural support to other members and/or surfaces of a structure including, but not limited to beams, posts, columns, joists, structural gutters, headers, eave rail, purlins, roof brace.

SECONDARY MEMBERS. Structural framing members which do not provide basic support for the entire structure, generally including, but not limited to, such members as kickplate rails, chair rails, roof or wall panels, wall brace.

STRUCTURAL MEMBERS. Members or sections that provide support to an assembly and/or resist applied loads.

2002.3 Screen enclosures.

2002.3.1 Actual wall thickness of extruded aluminum members shall be not less than 0.040 inch (1 mm).

2002.3.2 Reserved.

2002.3.3 Vinyl and acrylic panels shall be removable. Removable panels shall be identified as removable by a decal. The identification decal shall essentially state "Removable panel SHALL be removed when wind speeds exceed 75 mph (34 m/s)." Decals shall be placed such that the decal is visible when the panel is installed.

2002.4 Loads. Structural members supporting screened enclosures shall be designed for wind in both of two orthogonal directions using the pressures given in Table 2002.4. Each primary member shall also be designed for a 300 pound (1.33 kN) load applied vertically downward along any 1 foot (305 Mm) of any member, not occurring simultaneously with wind load.

Exception: In addition to wind pressures, purlins shall also be designed for a 200 pound (0.89 kN) load applied vertically downward along any 1 foot (305 mm) of any member, not occurring simultaneously with wind load. [4216]

2002.4 – Change to read as shown (below).

[S4628]

2002.4.1 The following design guides shall be accepted as conforming to accepted engineering practices:

AAF Guide to Aluminum Construction in High Wind Areas.

2002.5 Wall panels. The minimum thickness for formed sheet aluminum structural wall panels shall be not less than 0.024 inch (0.6 mm), subject to approved tolerances.

2002.6 Sunrooms. Sunrooms shall comply with AAMA/NPEA/NSA 2100 with and the structural requirements and testing provisions of Chapter 5.  modified to incorporate ASCE 7.

AAMA 2100, Section 5.2.1 Wind Loads: Modify Section 5.2.1 as follows:

5.2.1 Wind Loads: Basic wind speed in miles per hour (mph) or kilometer per hour (kph) shall be determined by the local or regional building authority in accordance with Section 1609.3. Sunrooms including exposed structures, components, cladding and roof covering shall be designed to resist the wind loads as established in Section 1609.1.1 ASCE 7-98 or local wind load criteria.

For the purpose of applying the criteria of the AAMA Standard for sunrooms based on the intended use, S sunrooms shall be categorized in one of the following categories.

[4279]

Category I: A roof or a covering of an outdoor space. The openings shall be permitted to be enclosed with insect screening or 0.5 mm (20 mil) maximum thickness plastic film. The space is defined as nonhabitable and unconditioned.

Category II: A roof or a covering of an outdoor space with enclosed walls. The openings are permitted to be enclosed with translucent or transparent plastic or glass. The space is defined as nonhabitable and unconditioned.

Category III: A roof or a covering of an outdoor space with enclosed walls. The openings are permitted to be enclosed with translucent or transparent plastic or glass. The sunroom complies with additional requirements for forced-entry resistance, air-leakage resistance and water-penetration resistance. The space is defined as nonhabitable and unconditioned.

Category IV: A roof or a covering of an outdoor space with enclosed walls. The sunroom is designed to be heated and/or cooled by a separate temperature control or system and is thermally isolated from the primary structure. The sunroom complies with additional requirements for forced-entry resistance, water-penetration resistance, air-leakage resistance, and thermal performance. The space is defined as habitable and conditioned.

Category V: A roof or a covering of an outdoor space with enclosed walls. The sunroom is designed to be heated and/or cooled and is open to the main structure. The sunroom complies with additional requirements for forced-entry resistance, water-penetration resistance, air-leakage resistance, and thermal performance. The space is defined as habitable and conditioned.

SECTION 2003

HIGH-VELOCITY HURRICANE ZONES—ALUMINUM

2003.1 Design. Aluminum members shall be designed by methods admitting of rational analysis according to established principles of mechanics.

2003.2 Standards. The design, fabrication, and erection of structural aluminum shall conform to the Aluminum Design Manual.

2003.3 Workmanship. Aluminum construction shall be in conformance with the tolerances, quality and methods of construction as set forth in Section 2003.2 and the American Welding Society's Structural Welding Code-Aluminum (D1.2).

2003.4 Definitions. Members shall be defined as in Section 2002.2.1.

2003.5 Identification. Aluminum for structural elements shall at all times be segregated or otherwise handled in the fabricator's plant so that the separate alloys and tempers are positively identified and, after completion of fabrication, shall be marked to identify the alloy and temper. Such markings shall be affixed to complete members and assemblies or to boxed or bundled shipments of multiple units prior to shipment from the fabricator's plant.

Exception: Certification by the fabricator and or contractor shall be provided attesting to the alloy and temper of the material.

TABLE 2002.4A

HEIGHT ADJUSTMENT FACTORS

MEAN ROOF

HEIGHT 	EXPOSURE

B 	C

15 	1 	0.86

20 	1 	0.92

25 	1 	0.96

30 	1 	1.00

35 	1.05 	1.03

40 	1.09 	1.06

45 	1.12 	1.09

50 	1.16 	1.11

55 	1.19 	1.14

60 	1.22 	1.16

| Table 2002.4A |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Height Adjustment Factors |  |  |  |  |  |
| B |  | C |  | D |  |
| 0-15 | 1 |  | 0.86 |  | 0.89 |
| 20 | 1 |  | 0.92 |  | 0.93 |
| 25 | 1 |  | 0.96 |  | 0.97 |
| 30 | 1 |  | 1 |  | 1 |
| 35 | 1.05 |  | 1.03 |  | 1.03 |
| 40 | 1.09 |  | 1.06 |  | 1.05 |
| 45 | 1.12 |  | 1.09 |  | 1.07 |
| 50 | 1.16 |  | 1.11 |  | 1.09 |
| 55 | 1.19 |  | 1.14 |  | 1.11 |
| 60 | 1.22 |  | 1.16 |  | 1.13 |

(4285 A2)

2003.6 Allowable unit stresses.

2003.6.1 The design, fabrication and assembly of aluminum members for building and other structures shall conform to the standard set forth in Section 2003.2 and as otherwise set forth herein.

2003.6.2 The use of aluminum alloys, other than those listed in the standard shall provide performance not less than those required by the standard and as set forth herein.

2003.6.3 Aluminum members shall be limited by the deflections set forth in Section 1615.3.

2003.7 The building official may require that any structure using aluminum primary or secondary members be designed by a Florida-registered professional engineer.

2003.7.1 Reserved.

2003.7.2 In addition to flexural and shearing stresses, the critical factors of buckling, fatigue, stress raisers such as notches or holes or shape re-entrant corners, deflection and connections shall be considered and provided for by proper design.

2003.7.3 All solid roof systems shall be designed for a minimum 30 psf (1436 Pa) live load.

2003.7.4 All buildings and structures shall be designed to resist uplift. In the case of placement on existing slabs and foundations, sufficient information and calculations shall be provided by the professional engineer and/or architect to verify the ability of the slab or foundation to resist uplift loads.

2003.7.5 All connection devices shall be rated by load testing by an approved testing laboratory.

2003.7.5.1 All expansion anchors shall not be installed less than 3 inches (76 mm) from the edge of concrete slab and/or footings. All expansion anchors shall develop an ultimate withdrawal resisting force equal to four times the imposed load, with no stress increase for duration of load.

2003.8 Fabrication and construction details.

2003.8.1 Connections. Aluminum members shall be designed as set forth in the standards in Section 2003.2.

2003.8.1.1 Fasteners. Bolts and other fasteners shall be aluminum, stainless steel, hot-dip or electro-galvanized steel. Double cadmium plated steel bolts may also be used.

2003.8.1.2 Painting. Except as prescribed in Section 2003.8.4, painting or coating of aluminum alloy parts shall be required only when called for on the plans.

2003.8.1.3 Welding. Aluminum parts shall be welded with an inert-gas-shielded arc or resistance welding process. No welding process that requires a welding flux shall be used. Filler alloys complying with the requirements of the standard in this chapter shall be used.

2003.8.1.4 Welder qualifications. All welding of structural aluminum member shall be performed by certified welders.

2003.8.1.5 Erection. During erection, structural aluminum shall be adequately braced and fastened to resist dead, wind and erection loads.

2003.8.2 Structural aluminum decking and siding.

2003.8.2.1 Aluminum sections spanning between supports shall be limited in span to satisfactorily support the positive and negative loads set forth in Chapter 16 (High- Velocity Hurricane Zones). The deflection of decking shall not exceed that set forth in Section 1613.

2003.8.2.2 Aluminum sheet used for roof decking or siding shall be not less than 0.032 inch (0.8 mm) in thickness.

2003.8.2.3 Aluminum sheets shall be secured to the supports to adequately resist positive and negative loads. Attachments shall be at intervals not exceeding 8 inches (203 mm) o.c. and shall be secured to each other at side laps at intervals as required by rational analysis and/or tests, but shall not exceed 12 inches (305 mm) o.c.

2003.8.2.4 Fasteners shall have a head, and/or be provided with washers not less than 1/2 inch (13 mm) in diameter.

2003.8.2.5 Fasteners located at end laps shall be placed not more than 2 inches (51 mm) nor less than 1 inch (25 mm) from the end of overlapping sheets.

2003.8.2.6 Where roof or wall cladding is of aluminum, an approved membrane to protect against water intrusion to the interior shall be provided or the aluminum cladding shall be designed and constructed with an approved continuous edge-interlock, overlap or seam to prevent water intrusion.

2003.8.3 Nonstructural aluminum decking and siding.

2003.8.3.1 Nonstructural aluminum sheets shall be backed with cladding as set forth in Chapter 23 and Chapter 24 (High-Velocity Hurricane Zones).

2003.8.3.2 Nonstructural aluminum sheets shall have a minimum thickness of 0.032 inches (0.8 mm).

2003.8.3.3 An approved membrane to protect against water intrusion shall be provided or the aluminum cladding shall be designed and constructed with an approved continuous edge-interlock, overlap or seam to prevent water intrusion.

2003.8.3.4 Nonstructural decking and siding shall be attached as set forth in Section 2003.8.2 except that the attachment of aluminum residential siding shall be by rational analysis and/or tests using a minimum 0.120-inch (3 mm) diameter aluminum nails of sufficient length to penetrate studs a minimum of 2 inches (51 mm). Nails at wood studs shall be as required by rational analysis and/or tests, but spaced not greater than 24 inches (610 mm) o.c. horizontally and no greater than 8 inches (203 mm) o.c. vertically.

2003.8.4 Dissimilar materials.

2003.8.4.1 Aluminum may contact compatible metals such as, but not limited to:

1.	Nonmagnetic stainless steel provided the contacting surfaces and any attachments are enclosed for protection from the weather.

2.	Zinc.

3.	White bronze.

2003.8.4.2 Aluminum contacting metals not considered compatible shall be protected as follows:

1.	Painting the dissimilar metal with a prime coat of zinc-chromate primer or other suitable primer, followed by one or two coats of aluminum metal-and-masonry paint or other suitable protective coating, excluding those containing lead pigmentation.

2.	Painting the dissimilar metal with a coating of a heavy-bodied bituminous paint.

3.	Placing a good quality caulking material between the aluminum and the dissimilar metal.

4.	Applying a nonabsorptive tape or gasket.

5.	Hot-dip galvanizing or zinc-plating steel members after fabrication.

2003.8.4.3 Dissimilar metals shall be painted if used in locations where drainage from them passes over aluminum.

2003.8.4.4 Aluminum surfaces in contact with lime-mortar, concrete, or other masonry materials, shall be protected with alkali-resistant coatings, such as heavy-bodied bituminous paint or water-white methacrylate lacquer.

2003.8.4.5 Aluminum in contact with wood or other absorbing materials which may become repeatedly wet shall be painted with two coats of aluminum metal-and-masonry paint or a coat of heavy-bodied bituminous paint, or the wood or other absorbing material shall be painted with two coats of aluminum house paint and the joints sealed with a good quality caulking compound.

2003.8.4.6 Where aluminum is in contact with treated wood, wood shall be treated with pentachlorophenol, 5 percent minimum concentration, creosote, or zinc naphthanate, following the protective measures outlined in Section 2003.8.4.5.

2003.8.5 Expansion and contraction. Aluminum work shall be designed and anchored so the work will not be distorted nor t

2003.9 Sunrooms

2003.9.1 Wind Loads: Basic wind speed in miles per hour (mph) shall be determined in accordance with Section 1620.2. Sunrooms including exposed structures, components, cladding, and roof covering shall be designed to resist the wind loads as established in Section 1620.1.

2003.9.2 Sunroom Categories. For the purpose of applying the criteria of the AAMA Standard for sunrooms based on the intended use, sSunrooms shall be categorized in one of the following categories by the permit applicant, design professional, or the property owner where the sunroom is being constructed

[S4629]

Category I: A roof or a covering of an outdoor space. The openings shall be permitted to be enclosed with insect screening or 0.5 mm (20 mil) maximum thickness plastic film. The space is defined as nonhabitable and unconditioned.

Category II: A roof or a covering of an outdoor space with enclosed walls. The openings are permitted to be enclosed with translucent or transparent plastic or glass. The space is defined as nonhabitable and uunconditioned.

Category III: A roof or a covering of an outdoor space with enclosed walls. The openings are permitted to be enclosed with translucent or transparent plastic or glass. The sunroom complies with additional requirements for forced-entry resistance, air-leakage resistance and water-penetration resistance. The space is defined as nonhabitable and unconditioned.

Category IV: A roof or a covering of an outdoor space with enclosed walls. The sunroom is designed to be heated and/or cooled by a separate temperature control or system and is thermally isolated from the primary structure. The sunroom complies with additional requirements for forced-entry resistance, water penetration resistance, air-leakage resistance, and thermal performance. The space is defined as habitable and conditioned.

Category V: A roof or a covering of an outdoor space with enclosed walls. The sunroom is designed to be heated and/or cooled and is open to the main structure. The sunroom complies with additional requirements for forced-entry resistance, water-penetration resistance, air-leakage resistance, and thermal performance. The space is defines as habitable and conditioned.

[4345]

Chapter 21 Masonry

Section 2101 General

2101.1 Scope.  Change to read as shown.

2101.1 Scope.  This chapter shall govern the materials, design, construction and quality of masonry.

Exception: Buildings and structures located within the high-velocity hurricane zone shall comply with the provisions of Sections 2114 and Sections 2118 through 2122.

2101.2.1  Allowable stress design.  Change to read as shown.

2101.2.1  Allowable stress design. Masonry designed by the allowable stress design method shall comply with the provisions of Sections 2106 and 2107

2101.2.2  Strength design.  Change to read as shown.

2101.2.2  Strength design. Masonry designed by the strength design method shall comply with the provisions of Sections 2106 and 2108, except that autoclaved aerated concrete (AAC) masonry shall comply with the provisions of Section 2106 and Chapter 1 and Appendix A of ACI 530/ASCE 5/TMS 402. AAC masonry shall not be used in the seismic-force-resisting system of structures classified as Seismic Design Category B, C, D, E or F.

.

2101.2.3 Prestressed masonry.  Change to read as shown.

2101.2.3 Prestressed masonry.  Prestressed masonry shall be designed in accordance with Chapters 1 and 4 of ACI 530/ASCE 5/TMS 402. and Section 2106. Special inspection during construction shall be provided as set forth in Section 1704.5.

2101.2.4 Empirical design   Change to read as shown.

2101.2.4 Empirical design. Masonry designed by the empirical design method shall comply with the provisions of Sections 2106 and 2109 or Chapter 5 of ACI 530/ASCE 5/TMS 402.

2101.2.7 Prescriptive methods.  Add to read as shown.

2101.2.7 Prescriptive methods.  Masonry construction is permitted in accordance with applicable standards reference in Section 1609.1.1.

Section 2102 Definitions and Notations

2102.1 General.  Revise to read as shown.

GLASS UNIT MASONRY. Masonry composed of glass units bonded by mortar.

Comment after Glitch

SHEAR WALL. A wall designed to resist lateral forces parallel to the plane of the wall.

Section 2104 Construction

2104.1.7 Bracing of masonry.  Add to read as shown.

2104.1.7 Bracing of masonry.  Bracing that will ensure stability of masonry during construction shall be provided and installed.  Bracing shall be in accordance with the Standard Practice for Bracing Masonry Walls Under Construction.

- Exceptions:

- 1.	Bracing shall not be required for the unsupported wall heights specified in the Standard Practice for Bracing Masonry Walls Under Construction, Appendix A, when an evacuation system complying with the Standard Practice for Bracing Masonry Walls Under Construction with Commentary is provided.

2.Walls 8 feet (2438 mm) and less in height above grade shall not require bracing.

Section 2105 Quality Assurance.

2105.1 General. Change to read as shown.

2105.1 General.  A quality assurance program shall be used to ensure that the constructed masonry is in compliance with the construction documents.

The quality assurance program shall comply with the inspection and testing requirements of Chapter 17.

Section 2106 Seismic Design.  Change to read as shown.

Section 2106 Seismic Design.  Reserved

Revise Section 2107, Allowable Stress Design, as follows:

Section 2107.1 General, revise to read as follows:

2107.1 General. The design of masonry structures using allowable stress design shall comply with Section 2106 and the requirements of Chapters 1 and 2 of TMS 402/ACI 530/ASCE 5/TMS 402  except as modified by Section 2107.2 through 2107.5.  Lap splices shall be in accordance with ACI 530/ ASC5/ TMS 402 or in accordance with 2107.3 or 2107.4  as specified by the architect or engineer.  Development of bars in tension and compression shall be in accordance with ACI 530/ASCE 5/TMS 402 or in accordance with 2107.5 as specified by the architect or engineer.

Exception: Where inspections are performed by a local building department in accordance with Section 105, the provisions of ACI 530/ASCE 5/TMS 402, Chapter 1, Section 1-15 and ACI 530.1/ASCE 6/TMS 602 1.6 shall not apply unless specified by the architect or engineer.

2107.1 General. The design of masonry structures using allowable stress design shall comply with Section 2106 and the requirements of Chapters 1 and 2 of TMS 402/ACI 530/ASCE 5/TMS 402  except as modified by Section 2107.2 through 2107.5. Lap splices shall be in accordance with TMS 402/ ACI 530/ ASC5/ TMS 402 or in accordance with 2107.3 or 2107.4  as specified by the architect or engineer. Development of bars in tension and compression shall be in accordance with TMS 402/ACI 530/ASCE 5/ TMS 402  or in accordance with 2107.5 as specified by the architect or engineer.

Exception: Where plan review and inspections are performed by a local building department in accordance with Sections 105 106 and 109, the provisions of TMS 402/ ACI 530/ASCE 5/TMS 402, Chapter 1, Section 1-15 1.18 and TMS 602/ ACI 530.1/ASCE 6/ TMS 602 Sections 1.5 and 1.6 shall not apply unless specified by the architect or engineer. [4063]

2107.2 ACI 530/ASCE 5/TMS 402, Section 2.1.2, load combinations. Delete Section 2.1.2.1. Rereved.

2107.3 TMS 402/ACI 530/ASCE 5, Section 2.1.9.7.1.1, lap splices.   No change.

2107.4 TMS 402/ACI 530/ASCE 5, Section 2.1.9.7, Splices of reinforcement.  No change.

Change Section 2107.5 as shown:

2107.5 ACI 530/ASCE 5/TMS 402, Section 2.1.10.3, Development of bars in tension and compression.  Modify Section 2.1.10.3 as follows:

2.1.10.3  The required development length of reinforcing bars shall be determined by Equation (2-9), but shall not be less than 12 in. (305 mm), but need not be greater than 72 db.

EQUATION 2-9 from ACI 530/ASCE 5/TMS 402    [UNCHANGED]

K shall not exceed the lesser of the masonry cover, clear spacing between adjacent reinforcement, nor 5  times db .

γ = 1.0 for No. 3 (M#10) through No. 5 (M#16) bars;

# γ = 1.04 for No. 6 (M#19) through No. 7 (M#22) bars; and

γ = 1.2 for No. 8 (M#25) through No. 11 (M#36) bars

Where epoxy coated bars are used, lap length shall be increased by 50 percent.

2107.5 TMS 402/ ACI 530/ASCE 5/TMS 402, Section 2.1.10 9.3, Development of bars in tension and compression.  Modify Section 2.1.10 9.3 as follows:

2.1.10 9.3 The required development length of reinforcing bars shall be determined by Equation (2- 9 12), but shall not be less than 12 in. (305 mm), but need not be greater than 72 db.

EQUATION 2- 9 12 from TMS 402/ ACI 530/ASCE 5/ [UNCHANGED]

K shall not exceed the lesser of the masonry cover, clear spacing between adjacent reinforcement, nor 5 times db .

yg  = 1.0 for No. 3 (M#10) through No. 5 (M#16) bars;

yg  = 1.04 for No. 6 (M#19) through No. 7 (M#22) bars; and

yg  = 1.2 for No. 8 (M#25) through No. 11 (M#36) bars

[S4630]

g – Reinforcement size factor “Lamda”

Where epoxy coated bars are used, lap length shall be increased by 50 percent. [4064]

- Section 2108, Strength Design of Masonry, revise to read as follows:

2108.1 General. The design of masonry structures using strength design shall comply with Section 2106 and the requirements of Chapters 1 and 3 of TMS 402/ACI 530/ASCE 5/TMS 402, except as modified by Section 2108.2 through 2108.3.

Exceptions:

1.  AAC masonry shall comply with the requirements of Chapter 1 and Appendix A of TMS 402/ACI 530/ASCE 5/TMS 402.

# 2 Where inspections are performed by a local building department in accordance with Section 105, the provisions of ACI 530/ASCE 5/TMS 402, Chapter 1, Section 1-15 and ACI 530.1/ASCE 6/TMS 602 Section 1.6 shall not apply unless specified by the architect or engineer.

2108.1 General. The design of masonry structures using strength design shall comply with Section 2106 and the requirements of Chapters 1 and 3 of TMS 402/ACI 530/ASCE 5 /TMS 402, except as modified by Section 2108.2 through 2108.3.

Exceptions:

1. AAC masonry shall comply with the requirements of Chapter 1 and Appendix A of TMS 402/ACI 530/ASCE 5/TMS 402.

2. Where plan review and inspections are performed by a local building department in accordance with Sections 105 106 and 109 , the provisions of TMS 402/ACI 530/ASCE 5 /TMS 402, Chapter 1, Section 1-15 1.18 and TMS 602/ ACI 530.1/ASCE 6/TMS 602 Sections 1.5 and 1.6 shall not apply unless specified by the architect or engineer. [4065]

2108. 2 TMS 402/ACI 530/ASCE 5/TMS 402, Section 3.3.3.3 development. Modify the second paragraph of Section 3.3.3.3 as follows:

3.3.3.3 Development.  The required development length of reinforcement shall be determined by Equation (3-165), but shall not be less than 12 inches (305 mm) and need not be greater than 72db.

EQUATION 3-165 UNCHANGED

K shall not exceed the lesser of the masonry cover, clear spacing between adjacent reinforcement, nor 5 times db.

γ = 1.0 for No. 3 (M#10) through No. 5 (M#16) bars;

# γ = 1.04 for No. 6 (M#19) through No. 7 (M#22) bars; and

γ = 1.2 for No. 8 (M#25) through No. 11 (M#36) bars

Where epoxy coated bars are used, lap length shall be increased by 50 percent.

- 2108.3  TMS 402/ACI 530/ASCE 5, Section 3.3.3.4, splices.  Change to read as shown.

2108.3ACI530/ASCE5/TMS402, Section3.3.3.4, splices.   Reserved.

Section 2109 Empirical Design of Masonry

2109.1.1 Limitations.  Change to read as shown.

2109.1.1 Limitations. The use of empirical design of masonry shall be limited as noted in Section 5.1.2 of TMS 402/ACI 530/ASCE 5. The use of dry-stacked, surface bonded masonry shall be prohibited in Risk Occupancy Category IV structures. In buildings that exceed one or more of the limitations of Section 5.1.2 of TMS 402/ACI 530/ASCE 5, masonry shall be designed in accordance with the engineered design provisions of Section 2101.2.1, 2101.2.2 or 2101.2.3 or the foundation wall provisions of Section 1807.1.5.

Exception: Empirical design shall not be used where the basic ultimate design wind speed, Vult, exceeds 115 100 mph (45 m/s). [4218]

Section 2110 Glass Unit Masonry

2110.1.1 Limitations.  Change Exceptions to read as shown.

- Exceptions:

- 1.	- 2 no change.

3.   Fire tested and listed glass unit masonry shall be permitted for use in accordance with its listing.

Section 2111 Masonry Fireplaces

2111.3 Seismic reinforcing.  Add to read as shown.

2111.3 Seismic reinforcing. Reserved

2111.4 Seismic anchorage.   Add to read as shown.

2111.4 Seismic anchorage. Reserved

2112 Masonry Heaters

2112.4 Seismic reinforcing.  Add to read as shown.

2112.4 Seismic reinforcing.  Reserved

Section 2113 Masonry Chimneys

2113.3 Seismic reinforcing.  Change to read as shown.

2113.3 Seismic reinforcing.  Reserved.

2113.3.1 Vertical reinforcing.  Change to read as shown.

2113.3.1 Vertical reinforcing. Reserved.

2113.3.2 Horizontal reinforcing.  Change to read as shown.

2113.3.2 Horizontal reinforcing. Reserved.

2113.4 Seismic anchorage.  Change to read as shown.

2113.4 Seismic anchorage. Reserved.

2113.4.1 Anchorage.  Change to read as shown.

2113.4.1 Anchorage. Reserved.

2113.11.1.2 Gas appliances.  Change to read as shown.

2113.11.1.2 Gas appliances. Flue lining systems for gas appliances shall be in accordance with the Florida Building Code, Fuel Gas.

2113.15 Flue area (appliance).  Change to read as shown.

2113.15 Flue area (appliance). Chimney flues shall not be smaller in area than the area of the connector from the appliance. Chimney flues connected to more than one appliance shall not be less than the area of the largest connector plus 50 percent of the areas of additional chimney connectors.

Exceptions:

1. Chimney flues serving oil-fired appliances sized in accordance with NFPA 31.

2. Chimney flues serving gas-fired appliances sized in accordance with the Florida Building Code, Fuel Gas..

- Section 2114 TERMITE INSPECTION.  Add to read as shown.

- Section 2114 TERMITE INSPECTION

- 2114.1 Cleaning.   Add to read as shown.

- 2114.1 Cleaning.  Cells and cavities in masonry units and air gaps between brick, stone or masonry veneers and the structure shall be cleaned of all nonpreservative treated or nonnaturally durable wood, or other cellulose-containing material prior to concrete placement.

- Exception: Inorganic material manufactured for closing cells in foundation concrete masonry unit construction or clean earth fill placed in concrete masonry unit voids below slab level before termite treatment is performed.

- 2114.2 Concrete bearing ledge.  Add to read as shown.

- 2114.2 Concrete bearing ledge.  Brick, stone or other veneer shall be supported by a concrete bearing ledge at least equal to the total thickness of the brick, stone or other veneer, which is poured integrally with the concrete foundation. No supplemental concrete foundation pours which will create a hidden cold joint shall be used without supplemental treatment in the foundation unless there is an approved physical barrier. An approved physical barrier shall also be installed from below the wall sill plate or first block course horizontally to embed in a mortar joint. If masonry veneer extends below grade, a termite protective treatment must be applied to the cavity created between the veneer and the foundation, in lieu of a physical barrier.

Exception: Veneer supported by a shelf, angle or lintel secured to the foundation sidewall in accordance with TMS 402/ ACI 530/ASCE 5 /TMS 402, provided at least a 6-inch (152 mm) clear inspection space of the foundation sidewall exterior exist between the veneer and the top of any soil, sod, mulch or other organic landscaping component, deck, apron, porch, walk or any other work immediately adjacent to or adjoining the structure. [4066]

- SECTION 2115 Special Wind Provisions for Masonry.  Add to read as shown.

Section 2115 Special Wind Provisions for Masonry.

- 2115.1 Gable endwalls.  Add to read as shown.

- 2115.1 Gable endwalls.

- 2115.1.1 General.   Add to read as shown.

- 2115.1.1 General.  Gable endwalls shall be structurally continuous between points of lateral support.

2115.1.2 Cathedral endwalls.    Add to read as shown.

2115.1.2 Cathedral endwalls.  Gable endwalls adjacent to cathedral ceilings shall be structurally continuous from the uppermost floor to the ceiling diaphragm or to the roof diaphragm.

- Sections 2116-2117 Reserved.  Add to read as shown.

- SECTIONS 2116 – 2117 RESERVED

Section 2118-2122 High-Velocity Hurricane Zones—Design.  Florida specific, add from the 2007 Florida Building Code.

Section 2118-2122 High-Velocity Hurricane Zones—Design

See Chapter 21 - HVHZ

Chapter 22 Steel

Section 2201 General

2201.1 Scope.  Change to read as shown.

2201.1 Scope.  The provisions of this chapter govern the quality, design, fabrication and erection of steel used structurally in buildings or structures.

Exception: Buildings and structures located within the high-velocity hurricane zone shall comply with the provision of 2214 through 2224.

Section 2204 Connections

2204.1 Welding.  Change to read as shown.

2204.1 Welding.  The details of design, workmanship and technique for welding, inspection of welding and qualification of welding operators shall conform to the requirements of the specifications listed in Sections 2205, 2206, 2207, 2209 and 2210.

2204.2 Bolting.  Change to read as shown.

2204.2 Bolting.  The design, installation and inspection of bolts shall be in accordance with the requirements of the specifications listed in Sections 2205, 2206, 2209 and 2210.

Section 2205 Structural Steel

2205.3.1 Seismic Design Categories D, E and F. – Change to read as shown.

2205.3.1 Seismic Design Categories D, E and F. Reserved. Composite structures are permitted in Seismic Design Categories D , E and F, subject to the limitations in Section 12.2.1 of ASCE 7, where substantiating evidence is provided to demonstrate that the proposed system will perform as intended by AISC 341, Part II. The substantiating evidence shall be subject to building official approval. Where composite elements or connections are required to sustain inelastic deformations, the substantiating evidence shall be based on cyclic testing.

[S4703]

2205.2 Seismic requirements for steel structures.  Change to read as shown.

2205.2 Seismic requirements for steel structures.  Reserved.

2205.3 Seismic requirements for composite construction.  Change to read as shown.

2205.3 Seismic requirements for composite construction.  Reserved.

Section 2206 Steel Joists

2206.1 General.  Change to read as shown.

2206.1 General. The design, manufacture and use of open web steel joists and joist girders shall be in accordance with one of the following Steel Joist Institute (SJI) specifications:

1.  SJI CJ-1.0

2. SJI K-1.1

3. SJI LH/DLH-1.1

4. SJI JG-1.1

Where required, the seismic design of buildings shall be in accordance with the additional provisions of Section 2205.2 or 2210.5.

2206.5 Certification. – Change to read as shown.

2206.5 Certification. At completion of manufacture, the steel joist manufacturer shall submit a certificate of compliance in accordance with Section 1704.2.2 stating that work was performed in accordance with approved construction documents and with SJI standard specifications.

[S4704]

Section 2207 Steel Cable Structures

2207.2 Seismic requirements for steel cable. Change to read as shown.

2207.2 Seismic requirements for steel cable. Reserved.

Section 2208 Steel Storage Racks

2208.1 Storage racks.  Change to read as shown.

2208.1 Storage racks. The design, testing and utilization of industrial steel storage racks made of cold-formed or hot-rolled steel structural members, shall be in accordance with the RMI/ANSI MH 16.1. Where required by ASCE 7, the seismic design of storage racks shall be in accordance with the provisions of Section 15.5.3 of ASCE 7, except that items (1), (2) and (3) of Section 15.5.3 of ASCE 7 do not apply when the rack design satisfies RMI/ANSI MH 16.1.

Section 2210 Cold-Formed Steel Light-Frame Construction

2210.3.4 Trussses spanning 60 feet or greater.  Change to read as shown.

2210.3.4 Trussses spanning 60 feet or greater. The owner shall contract with a registered design professional for the design of the temporary installation restraint/bracing and the permanent individual truss member restraint/bracing for trusses with clear spans 60 feet (18 288 mm) or greater. Special inspection of trusses over 60 feet (18 288 mm) in length shall conform to Section 1704.

2210.6 Lateral design.  Change to read as shown.

2210.6 Lateral design. Light-frame shear walls, diagonal strap bracing that is part of a structural wall and diaphragms used to resist wind, seismic and other in-plane lateral loads shall be designed in accordance with AISI S213.

Section 2211 Gable End Walls

2211.1 Gable end walls.  Add to read as shown.

- 2211.1 Gable end walls.  Gable endwalls shall be structurally continuous between points of lateral support.

- 2211.2 Catherdral end walls.  Add to read as shown.

- 2211.2 Catherdral end walls.  Gable endwalls adjacent to cathederal ceilings shall be continuous from the uppermost floor to ceilings shall be continuous from the uppermost floor to ceiling diaphragm or to the roof diaphragm.

Section 2213.  Add to read as shown.

# SECTION 2213 Reserved.

Section 2214 through Section 2224.  Add per the 2007 Florida Building Code.

# SECTION 2214 –SECTION 2224

HIGH-VELOCITY HURRICANE ZONES—

See Chapter 22 – HVHZ

Chapter 23 Wood

Section 2301 General

2301.1 Scope.  Change to read as shown.

# 2301.1 Scope.  The provisions of this chapter shall govern the materials, design, construction and quality of wood members and their fasteners.

Exception: Buildings and structures located within the high-velocity hurricane zone shall comply with the provisions of Sections 2314 through 2330.

Section 2303 Minimum Standards and Quality

2303.4.1.1 Truss design drawings. Revise Item 5(5.6) as follows:

5.6. Environmental design criteria and loads (wind, rain, snow, seismic, etc.).

Section 2304 General Construction Requirements

2304.3.4 Gable endwalls.  Add to read as shown.

2304.3.4 Gable endwalls.

- 2304.3.4.1 General.  Add to read as shown.

- 2304.3.4.1 General.  Gable endwalls shall be structurally continuous between points of lateral support.

- 2304.3.4.2 Cathedral endwalls.  Add to read as shown.

- 2304.3.4.2 Cathedral endwalls.  Gable endwalls adjacent to cathedral ceilings shall be structurally continuous from the uppermost floor to the ceiling diaphragm or to the roof diaphragm.

2304.3.4.3 Full height studs.  Add to read as shown.

2304.3.4.3 Full height studs.  Full height studs may be sized using the bracing at a ceiling diaphragm for determining stud length requirements.

Table 2304.9.1 Fastening Schedule.  Change Item 31 to read as shown.

TABLE 2304.9.1

FASTENING SCHEDULE

| CONNECTION |  | FASTENINGa,m |  | LOCATION |  |
| --- | --- | --- | --- | --- | --- |
| 31. | Wood structural panels and particleboardb | 1/2 ″ and less | 6dc,1 |  |  |
|  | Subfloor, roof and wall sheathing (to framing) |  | 2 3/8″ × 0.113″ nailn |  |  |
|  |  |  | 1 3/4 ″ 16 gageo |  |  |
|  |  | 15/32 in to 19/32 | 8d common (roofs in 110-140 mph (Exp. B)) |  | 6 inch o.c. edges and intermediate, 4 inch o.c. at component and cladding edge strip #3 [refer to Figure 6-3 of ASCE 7] |
|  |  | 19/32 ″ to 3/4 ″ | 8dd or 6de |  |  |
|  |  |  | 2 3/8″ × 0.113″ nailp |  |  |
|  |  |  | 2″ 16 gagep |  |  |
|  |  | 7/8 ″ to 1″ | 8dc |  |  |
|  | Single Floor (combination subfloor-underlayment | 1 1/8 ″ to 1 1/4 ″ | 10dd or 8dd |  |  |
|  | to framing) | 3/4 ″ and less | 6de |  |  |
|  |  | 7/8 ″ to 1″ | 8de |  |  |
|  |  | 1 1/8 ″ to 1 1/4 ″ | 10dd or 8de |  |  |

For SI: 1 inch = 25.4 mm.

Notes: No change.

Table 2304.9.1 Fastening Schedule. Change Item 31 to read as shown.

TABLE 2304.9.1

FASTENING SCHEDULE

| CONNECTION |  | FASTENINGa,m |  | LOCATION |  |
| --- | --- | --- | --- | --- | --- |
| 31. | Wood structural panels and particleboardb | 1/2 “ and less | 6dc,1 |  |  |
|  | Subfloor, roof and wall sheathing (to framing) |  | 2 3/8" × 0.113” nailn |  |  |
|  |  |  | 1 ¾” 16 gageo |  |  |
|  |  | 15/32 in to 19/32 | 8d common (roofs in 110-140 mph (Exp. B)) |  | 6 inch o.c. edges and intermediate, 4 inch o.c. at component and cladding edge strip # Zone 3 [refer to Figure 30.5-1 6-3 of ASCE 7] |
|  |  | 19/32 “ to ¾” | 8dd or 6de |  |  |
|  |  |  | 2 3/8” × 0.113” nailp |  |  |
|  |  |  | 2? 16 gagep |  |  |
|  |  | 7/8” to 1” | 8dc |  |  |
|  | Single Floor (combination subfloor-underlayment | 1 1/8” to 1 1/4 “ | 10dd or 8dd |  |  |
|  | to framing) | ¾” and less | 6de |  |  |
|  |  | 7/8” to 1” | 8de |  |  |
|  |  | 1 1/8” to 1 ¼” | 10dd or 8de |  |  |

[4219]

2304.5 Framing around flues and chimneys.  Change to read as shown.

2304.5 Framing around flues and chimneys. Combustible framing shall be a minimum of 2 inches (51 mm), but shall not be less than the distance specified in Sections 2111 and 2113 and the Florida Building Code, Mechanical, from flues, chimneys and fireplaces, and 6 inches (152 mm) away from flue openings.

Table 2304.6.1. Revise as shown.

TABLE 2304.6.1

MAXIMUM Vasd AS DETERMINED IN ACCORDANCE WITH SECTION 1609.3.1

BASIC WIND SPEED (mph) (3-SECOND GUST) PERMITTED FOR

WOOD STRUCTURAL PANEL WALL SHEATHING USED TO RESIST WIND PRESSURESa,b,c

| Remainder of table unchanged | MAXIMUM Vasd AS DETERMINED IN ACCORDANCE WITH SECTION 1609.3.1 WIND SPEED |  |  |
| --- | --- | --- | --- |
|  | Wind exposure category |  |  |
|  | B | C | D |
|  | Remainder of table unchanged |  |  |

No change to notes a or c

b. The table is based on wind pressures acting toward and away from building surfaces in accordance with Section 30.7 6.4.2.2 ofASCE7. Lateral requirements shall be in accordance with Section 2305 or 2308.

[4219]

2304.11.2.2 Wood supported by exterior foundation walls.  Change to read as shown.

2304.11.2.2 Wood supported by exterior foundation walls.  Wood framing members, including wood sheathing, which rest on exterior foundation walls and are less than 8 inches (203 mm) from exposed earth shall be of naturally durable or preservative-treated wood. Wood framing members and furring strips attached directly to masonry or concrete walls shall be of approved naturally durable or preservative-treated wood.

2304.11.4.3 Add to read as shown.

- 2304.11.4.3  Decks, fences, patios, planters, or other wooden building components that directly abut the sidewall of the foundation or structure shall be constructed so as to provide:

- 1. Eighteen-inch (457 mm) clearance beneath or,

- 2. Six-inch (152 mm) clearance between the top of the component and the exterior wall covering or,

3. Have components that are easily removable by screws or hinges to allow access for inspection of the foundation sidewall and treatment for termites.

2304.11.6 Termite protection.  Change to read as shown.

2304.11.6 Termite protection. Termite protection shall be provided by floor framing of naturally durable or preservative-treated wood, soil treatment or other approved methods of termite protection. In geographical areas where hazard of termite damage is known to be very heavy, wood floor framing shall be of naturally durable species (termite resistant) or preservative treated in accordance with AWPA U1 for the species, product preservative and end use or provided with approved methods of termite protection. [3931]

2304.11.10 Foam-plastic insulation.  Add to read as shown.

2304.11.10 Foam-plastic insulation.

- 2304.11.10.1 Add to read as shown.

- 2304.11.10.1  The provisions of Section 2603. 9 shall apply to the installation of foam plastic insulation in close proximity to the ground.

- Exception: Materials which are of naturally durable wood or are pressure treated for ground contact, and which are installed with at least 6 inches (152 mm) clear space from the structure to allow for inspection and treatment for termites.

In order to reduce chances of termite infestation, no wood, vegetation, stumps, dead roots, cardboard, trash, or other cellulose-containing material shall be buried on the building lot within 15 feet (4.6 m) of any building or the position of any building proposed to be built.

2304.13 Preparation of building site and removal of debris.  Add to read as shown.

2304.13  Preparation of building site and removal of debris.

- 2304.13.1 Add to read as shown.

- 2304.13.1 All building sites shall be graded to provide drainage under all portions of the building not occupied by basements.

- 2304.13.2 Add to read as shown.

- 2304.13.2  The foundation and the area encompassed within 1 foot (305 mm) therein shall have all vegetation, stumps, dead roots, cardboard, trash, and foreign material removed and the fill material shall be free of vegetation and foreign material. The fill shall be compacted to assure adequate support of the foundation.

2304.13.3 Add to read as shown.

2304.13.3  After all work is completed, loose wood and debris shall be completely removed from under the building and within 1 foot (305 mm) thereof. All wood forms and supports shall be completely removed. This includes, but is not limited to: wooden grade stakes, forms, contraction spacers, tub trap boxes, plumbing supports, bracing, shoring, forms, or other cellulose-containing material placed in any location where such materials are not clearly visible and readily removable prior to completion of the work. Wood shall not be stored in contact with the ground under any building.

Section 2305 General Design Requirements for Lateral-Force-Resisting Systems.

2305.1 General. Change to read as shown.

2305.1 General.  2305.1 General. Structures using wood shear walls and diaphragms to resist wind, seismic and other lateral loads shall be designed and constructed in accordance with

AF&PA SDPWS and the provisions of Sections 2305, 2306 and 2307.

Section 2306 Allowable Stress Design.

Table 2306.2.1(1) Change to read as shown.

Table 2306.2.1(1)

Allowable Shear (Pounds per Foot) for Wood Structural Panel Diaphragms With

Framing of Douglas Fir-Larch, or Southern Pinea for Wind Or Seismic Loadingh

Table 2306.2.1(2) Change to read as shown.

Table 2306.2.1(2)

Allowable Shear (Pounds per Foot) for Wood Structural Panel Blocked Diaphragms

Utilizing Multiple Rows of Fasteners (High Load Diaphragms) With Framing of

Douglas Fir-Larch or Southern Pinea for Wind Or Seismic Loadingb,

Table 2306.3 Change to read as shown.

Table 2306.3

Allowable Shear (Pounds per Foot) for Wood Structural Panel Shear Walls With

Framing of Douglas Fir-Larch or Southern Pinea for Wind Or Seismic Loadingb,

For SI: 1 inch = 25.4 mm, 1 pound per foot = 14.5939 N/m.

a. – h no change

i. Reserved.

j. – l no change

Table 2306.6 Change to read as shown.  Needs to be resolved.

Table 2306.6

Allowable Shear Values (Plf) For Wind Or Seismic Loading on Shear Walls of Fiberboard Sheathing Board Construction For Type V Construction Onlya,

For SI: 1 inch = 25.4 mm, 1 pound per foot = 14.5939 N/m.

A – d no change.

e. Reserved.

f. No change.

Table 2306.7Change to read as shown.

Table 2306.7

Allowable Shear for Wind Or Seismic Forces for Shear Walls of Lath

and Plaster or Gypsum Board Wood Framed Wall Assemblies

For SI: 1 inch = 25.4 mm, 1 foot = 304.8 mm, 1 pound per foot = 14.5939 N/m.

a. These shear walls shall not be used to resist loads imposed by masonry or concrete walls (see Section 4.1.5 of AF&PASDPWS).Values shown are for short-term loading due to wind or seismic loading. Walls resisting seismic loads shall be subject to the limitations in Section 12.2.1 of ASCE 7.Values shown shall be reduced 25 percent for normal loading.

b-k no change.

2306.4 Lumber sheathed shear walls.  Change to read as shown.

2306.4 Lumber sheathed shear walls. Single and double diagonally sheathed lumber shear walls shall be designed and constructed in accordance with AF&PA SDPWS. Single and double diagonally sheathed lumber walls shall not be used to resist seismic forces in structures assigned to Seismic Design Category E or F.

2306.5 Particleboard shear walls.  Revise to read as follows.

2306.5 Particleboard shear walls. Particleboard shear walls shall be designed and constructed in accordance with AF&PA SDPWS. Particleboard shear walls shall be permitted to resist

horizontal forces using the allowable shear capacities set forth in Table 2306.5. Allowable capacities in Table 2306.5 are permitted to be increased 40 percent for wind design. Particleboard shall not be used to resist seismic forces in structures

assigned to Seismic Design Category D, E or F.

2306.6 Fiberboard shear walls. Revise to read as follows:

2306.6 Fiberboard shear walls. Fiberboard shear walls shall be designed and constructed in accordance with AF&PA SDPWS. Fiberboard shear walls are permitted to resist horizontal

forces using the allowable shear capacities set forth in Table 2306.6. Allowable capacities in Table 2306.6 are permitted to be increased 40 percent for wind design. Fiberboard shall

not be used to resist seismic forces in structures assigned to Seismic Design Category D, E or F.

Section 2307 Load and Resistance Factor Design

2307.1.1 Wood structural panel shear walls.  Reserved.

2306.7 Shear walls sheathed with other materials.  Change to read as shown.

2306.7 Shear walls sheathed with other materials. Shear walls sheathed with portland cement plaster, gypsum lath, gypsum sheathing or gypsum board shall be designed and constructed

in accordance with AF&PA SDPWS. Shear walls sheathed with these materials are permitted to resist horizontal forces using the allowable shear capacities set forth in Table 2306.7. Shear walls sheathed with portland cement plaster, gypsum lath, gypsum sheathing or gypsum board shall not be used to resist seismic forces in structures assigned to Seismic Design Category E or F.

Table 2306.7 Allowable Shear for Wind Forces for Shear Walls of Lath and Plaster or Gypsum Board Wood Framed Wall Assemblies.  Change to read as shown.

TABLE 2306.7

ALLOWABLE SHEAR FOR WIND FORCE FOR SHEAR WALLS OF LATH

AND PLASTER OR GYPSUM BOARD WOOD FRAMED WALL ASSEMBLIES

For SI: 1 inch = 25.4 mm, 1 foot = 304.8 mm, 1 pound per foot = 14.5939 N/m.

a. These shear walls shall not be used to resist loads imposed by masonry or concrete construction (see Section 4.1.5 of AF&PA SDPWS 2305.1.5). Values shown are for short term loading due to wind loading.  Values shown shall be reduced 25 percent for normal loading.

b-k no change.

Section 2308 Conventional Light-Frame Construction

2308.1 General. Change to read as shown:

2308.1 General. The requirements of this section are intended for conventional light-frame construction. Other methods are permitted to be used, provided a satisfactory design is submitted showing compliance with other provisions of this code. Interior nonload-bearing partitions, ceilings and curtain walls of conventional light-frame construction are not subject to the limitations of this section. Alternatively, compliance with AF&PA WFCM shall be permitted subject to the limitations therein and the limitations of this code. Detached one- and two-family dwellings and multiple single-family dwellings (townhouses) not more than three stories above grade plane in height with a separate means of egress and their accessory structures shall comply with the  Florida Building Code, Residential.

2308.2 Limitations.  Change to read as shown.

2308.2 Limitations.   Buildings are permitted to be constructed in accordance with the provisions of conventional light-frame construction, subject to the following limitations, and to further limitations of Sections 2308.11 and 2308.12.

1. Buildings shall be limited to a maximum of three stories above grade plane.

2. Maximum floor-to-floor height shall not exceed 11 feet 7 inches (mm). Bearing wall height shall not exceed a stud height of 10 feet (3048 mm).

3. Loads as determined in Chapter 16 shall not exceed the following:

3.1. Average dead loads shall not exceed 15 psf (718 N/m2) for combined roof and ceiling, exterior walls, floors and partitions.

Exceptions:

1. Subject to the limitations of Sections 2308.11.2 and 2308.12.2, stone or masonry veneer up to the lesser of 5 inches (127 mm) thick or 50 psf (2395 N/m2) and installed in accordance with Chapter 14 is permitted to a height of 30 feet (9144 mm) above a noncombustible foundation, with an additional 8 feet (2438 mm) permitted for gable ends.

2. Concrete or masonry fireplaces, heaters and chimneys shall be permitted in accordance with the provisions of this code.

3.2. Live loads shall not exceed 40 psf (1916 N/m2) for floors.

3.3. Reserved. Ground snow loads shall not exceed 50 psf (2395 N/m2).

4. Ultimate Design Wind sSpeeds, Vult shall not exceed 115 100 miles per hour (mph) (44 m/s) (3-second gust).

Exception: Wind speeds shall not exceed 140 mph (48.4 m/s) (3-second gust) for buildings in Exposure Category B that are not located in a hurricane-prone region.

{4219}

5. Roof trusses and rafters shall not span more than 40 feet (12 192 mm) between points of vertical support.

6. Reserved.  The use of the provisions for conventional light-frame construction in this section shall not be permitted for Occupancy Category IV buildings assigned to Seismic Design Category B, C, D, E or F, as determined in Section 1613.

7. Reserved. Conventional light-frame construction is limited in irregular structures in Seismic Design Category D or E, as specified in Section 2308.12.6.

Section 2308.2.1 Basic wind speed greater than 100 mph (3-second gust). Change to read as shown:

2308.2.1 Ultimate Design Basic wWind sSpeed, Vult greater than 115 100 mph (3-second gust). Where the Ultimate Design basic wWind sSpeed, Vult exceeds 115 100 mph (3-second gust), the provisions of either AF&PAWFCM, or the ICC 600 are permitted to be used. Wind speeds in Figure 1609A, 1609B, and 1609C shall be converted in accordance with Section 1609.3.1 for use with AF&PAWFCM or ICC 600.

[4219]

2308.2.2 Buildings in Seismic Design Category B, C, D or E.  Change to read as shown.

2308.2.2 Buildings in Seismic Design Category B, C, D or E.  Reserved.

2308.3.2 Braced wall line connections.  Change to read as shown.

2308.3.2 Braced wall line connections. Wind and seismic lateral forces shall be transferred from the roofs and floors to braced wall lines and from the braced wall lines in upper stories to the braced wall lines in the story below in accordance with is section.

Braced wall line top plates shall be fastened to joists, rafters or full-depth blocking above in accordance with Table 2304.9.1, Items 11, 12, 15 or 19 as applicable based on the orientation of the joists or rafters to the braced wall line. Braced wall line bottom plates shall be connected to joists or blocking below in accordance with Table 2304.9.1, Item 6, or to foundations in accordance with Section 2308.3.3. At exterior gable end walls, braced wall panel sheathing in the top story shall be extended and fastened to roof framing where the spacing between parallel exterior braced wall lines is greater than 50 feet (15 240 mm).

Exception: No change

Figure 2308.9.3 Basic Components of the Lateral Bracing System.  Remove “seismic” from the figure as shown below.

| MAXIMUM WALL SPACING (feet) | REQUIRED BRACING LENGTH, b |
| --- | --- |
| 35'-0" | Table 2308.9.3(1) and Section 2308.9.3 |

Figure 2308.9.3 Basic Components of the Lateral Bracing System

2308.9.4.1 Bracing.   Change to read as shown.

2308.9.4.1 Bracing.  For the purposes of this section, cripple walls having a stud height exceeding 14 inches (356 mm) shall be considered a story and shall be braced in accordance with Table 2308.9.3(1).

Table 2308.9.3(1) Braced Wall Panels.  Change to read as shown.

Table 2308.9.3(1) Braced Wall Panels

| CONDITION | CONSTRUCTION METHODSb,c |  |  |  |  |  |  |  | BRACED PANEL LOCATION AND LENGTHd |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |  |
| One story, top of two or three story | X | X | X | X | X | X | X | X | Location in accordance with Section 2308.9.3 and not more than 25 feet on center |
| First story of two story or second story of three story | X | X | X | X | X | X | X | X |  |
| First story of three story | – | X | X | X | X | X | X | X |  |

For SI: 1 inch = 25.4 mm, 1 foot = 304.8 mm.

a. This table specifies minimum requirements for braced panels that form interior or exterior braced wall lines.

b. See Section 2308.9.3 for full description.

c. See Section 2308.9.3.1 for alternative braced panel requirement.

d. Building length is the dimension parallel to the braced wall length.

e. Reserved.

f. Reserved.

Table 2308.9.5 Header and Girder Spansa for Exterior Bearing Walls

(Maximum Spans for Douglas Fir-Larch, Hem-Fir, Southern Pine and Spruce-Pine-Firb and Required Number of Jack Studs)  Change to read as shown.

Table 2308.9.5 Header and Girder Spansa for Exterior Bearing Walls

(Maximum Spans for Douglas Fir-Larch, Hem-Fir, Southern Pine and Spruce-Pine-Firb and Required Number of Jack Studs)

| HEADERS SUPPORTING | SIZE | Building widthc (feet) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 20 |  | 28 |  | 36 |  |
|  |  | Span | NJd | Span | NJd | Span | NJd |
| Roof & Ceiling | 2-2 × 4 | 3-6 | 1 | 3-2 | 1 | 2-10 | 1 |
|  | 2-2 × 6 | 5-5 | 1 | 4-8 | 1 | 4-2 | 1 |
|  | 2-2 × 8 | 6-10 | 1 | 5-11 | 2 | 5-4 | 2 |
|  | 2-2 × 10 | 8-5 | 2 | 7-3 | 2 | 6-6 | 2 |
|  | 2-2 × 12 | 9-9 | 2 | 8-5 | 2 | 7-6 | 2 |
|  | 3-2 × 8 | 8-4 | 1 | 7-5 | 1 | 6-8 | 1 |
|  | 3-2 × 10 | 10-6 | 1 | 9-1 | 2 | 8-2 | 2 |
|  | 3-2 × 12 | 12-2 | 2 | 10-7 | 2 | 9-5 | 2 |
|  | 4-2 × 8 | 9-2 | 1 | 8-4 | 1 | 7-8 | 1 |
|  | 4-2 × 10 | 11-8 | 1 | 10-6 | 1 | 9-5 | 2 |
|  | 4-2 × 12 | 14-1 | 1 | 12-2 | 2 | 10-11 | 2 |
| Roof Ceiling & 1 Center-Bearing Floor | 2-2 × 4 | 3-1 | 1 | 2-9 | 1 | 2-5 | 1 |
|  | 2-2 × 6 | 4-6 | 1 | 4-0 | 1 | 3-7 | 2 |
|  | 2-2 × 8 | 5-9 | 2 | 5-0 | 2 | 4-6 | 2 |
|  | 2-2 × 10 | 7-0 | 2 | 6-2 | 2 | 5-6 | 2 |
|  | 2-2 × 12 | 8-1 | 2 | 7-1 | 2 | 6-5 | 2 |
|  | 3-2 × 8 | 7-2 | 1 | 6-3 | 2 | 5-8 | 2 |
|  | 3-2 × 10 | 8-9 | 2 | 7-8 | 2 | 6-11 | 2 |
|  | 3-2 × 12 | 10-2 | 2 | 8-11 | 2 | 8-0 | 2 |
|  | 4-2 × 8 | 8-1 | 1 | 7-3 | 1 | 6-7 | 1 |
|  | 4-2 × 10 | 10-1 | 1 | 8-10 | 2 | 8-0 | 2 |
|  | 4-2 × 12 | 11-9 | 2 | 10-3 | 2 | 9-3 | 2 |
| Roof Ceiling & 1 Clear Span Floor | 2-2 × 4 | 2-8 | 1 | 2-4 | 1 | 2-1 | 1 |
|  | 2-2 × 6 | 3-11 | 1 | 3-5 | 2 | 3-0 | 2 |
|  | 2-2 × 8 | 5-0 | 2 | 4-4 | 2 | 3-10 | 2 |
|  | 2-2 × 10 | 6-1 | 2 | 5-3 | 2 | 4-8 | 2 |
|  | 2-2 × 12 | 7-1 | 2 | 6-1 | 3 | 5-5 | 3 |
|  | 3-2 × 8 | 6-3 | 2 | 5-5 | 2 | 4-10 | 2 |
|  | 3-2 × 10 | 7-7 | 2 | 6-7 | 2 | 5-11 | 2 |
|  | 3-2 × 12 | 8-10 | 2 | 7-8 | 2 | 6-10 | 2 |
|  | 4-2 × 8 | 7-2 | 1 | 6-3 | 2 | 5-7 | 2 |
|  | 4-2 × 10 | 8-9 | 2 | 7-7 | 2 | 6-10 | 2 |
|  | 4-2 × 12 | 10-2 | 2 | 8-10 | 2 | 7-11 | 2 |

(continued)

TABLE 2308.9.5-continued HEADER AND GIRDER SPANSa FOR EXTERIOR BEARING WALLS (Maximum Spans for Douglas Fir-Larch, Hem-Fir, Southern Pine and Spruce-Pine-Firb and Required Number of Jack Studs)

| HEADERS SUPPORTING | SIZE | Building widthc(feet) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 20 |  | 28 |  | 36 |  |
|  |  | Span | NJd | Span | NJd | Span | NJd |
| Roof, Ceiling & 2 Center-Bearing Floors | 2-2 × 4 | 2-7 | 1 | 2-3 | 1 | 2-0 | 1 |
|  | 2-2 × 6 | 3-9 | 2 | 3-3 | 2 | 2-11 | 2 |
|  | 2-2 × 8 | 4-9 | 2 | 4-2 | 2 | 3-9 | 2 |
|  | 2-2 × 10 | 5-9 | 2 | 5-1 | 2 | 4-7 | 3 |
|  | 2-2 × 12 | 6-8 | 2 | 5-10 | 3 | 5-3 | 3 |
|  | 3-2 × 8 | 5-11 | 2 | 5-2 | 2 | 4-8 | 2 |
|  | 3-2 × 10 | 7-3 | 2 | 6-4 | 2 | 5-8 | 2 |
|  | 3-2 × 12 | 8-5 | 2 | 7-4 | 2 | 6-7 | 2 |
|  | 4-2 × 8 | 6-10 | 1 | 6-0 | 2 | 5-5 | 2 |
|  | 4-2 × 10 | 8-4 | 2 | 7-4 | 2 | 6-7 | 2 |
|  | 4-2 × 12 | 9-8 | 2 | 8-6 | 2 | 7-8 | 2 |
| Roof, Ceiling & 2 Clear Span Floors | 2-2 × 4 | 2-1 | 1 | 1-8 | 1 | 1-6 | 2 |
|  | 2-2 × 6 | 3-1 | 2 | 2-8 | 2 | 2-4 | 2 |
|  | 2-2 × 8 | 3-10 | 2 | 3-4 | 2 | 3-0 | 3 |
|  | 2-2 × 10 | 4-9 | 2 | 4-1 | 3 | 3-8 | 3 |
|  | 2-2 × 12 | 5-6 | 3 | 4-9 | 3 | 4-3 | 3 |
|  | 3-2 × 8 | 4-10 | 2 | 4-2 | 2 | 3-9 | 2 |
|  | 3-2 × 10 | 5-11 | 2 | 5-1 | 2 | 4-7 | 3 |
|  | 3-2 × 12 | 6-10 | 2 | 5-11 | 3 | 5-4 | 3 |
|  | 4-2 × 8 | 5-7 | 2 | 4-10 | 2 | 4-4 | 2 |
|  | 4-2 × 10 | 6-10 | 2 | 5-11 | 2 | 5-3 | 2 |
|  | 4-2 × 12 | 7-11 | 2 | 6-10 | 2 | 6-2 | 3 |

For SI: 1 inch = 25.4 mm, 1 foot = 304.8 mm, 1 pound per square foot = 47.8 N/m2.

a. Spans are given in feet and inches (ft-in).

b. Tabulated values are for No. 2 grade lumber.

c. Building width is measured perpendicular to the ridge. For widths between those shown, spans are permitted to be interpolated.

d. NJ - Number of jack studs required to support each end. Where the number of required jack studs equals one, the header is permitted to be supported by an approved framing anchor attached to the full-height wall stud and to the header.

e. Reserved.

Table 2308.10.1.  Revise as shown.

TABLE 2308.10.1

REQUIRED RATING OF APPROVED UPLIFT CONNECTORS (pounds)a,b,c,e,f,g,h,I

| Vasd AS DETERMINED IN ACCORDANCE WITH SECTION 1609.3.1 BASIC WIND SPEED (3-second gust) | ROOF SPAN (feet) |  |  |  |  |  |  | OVERHANGS (pounds/feet)d |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 12 | 20 | 24 | 28 | 32 | 36 | 40 |  |
| No change to remainder of table |  |  |  |  |  |  |  |  |

- No change

- No change

- No change

- No change

- The uplift connection requirements are based upon wind loading on end zones as defined in Figure 28.6.3 6-2 of ASCE 7. Connection loads for connections located a distance of 20 percent of the least horizontal dimension of the building from the corner of the building are permitted to be reduced by multiplying the table connection value by 0.7 and multiplying the overhang load by 0.8.

- No change

- Interpolation is permitted for intermediate values of Vasd basic wind speeds and roof spans.

- No change

[4219]

Table 2308.10.3(3) Rafter Spans for Common Lumber Species (Ground Snow Load = 30 pounds per square foot, Ceiling Not Attached to Rafters, L/ = 180).  Change to read as shown.

- Table 2308.10.3(3) Rafter Spans for Common Lumber Species (Ground Snow Load = 30 pounds per square foot, Ceiling Not Attached to Rafters, L/ = 180).  Reserved.

- Table 2308.10.3(4) Rafter Spans for Common Lumber Species.  (Ground Snow Load = 50 pounds per square foot.  Ceiling Not Attached to Rafters, L/ = 180).  Change to read as shown.

- Table 2308.10.3(4) Rafter Spans for Common Lumber Species.  (Ground Snow Load = 50 pounds per square foot.  Ceiling Not Attached to Rafters, L/ = 180).  Reserved.

- Table 2308.10.3(5) Rafter Spans for Common Lumber Species (Ground Snow Load = 30 pounds per square foot, Ceiling Attached to Rafters, L/ = 240).  Change to read as shown.

- Table 2308.10.3(5) Rafter Spans for Common Lumber Species (Ground Snow Load = 30 pounds per square foot, Ceiling Attached to Rafters, L/ = 240).  Reserved.

Table 2308.10.3(6) Rafter Spans for Common Lumber Species.  (Ground Snow Load = 50 pounds per square foot.  Ceiling Attached to Rafters, L/ = 240).  Change to read as shown.

Table 2308.10.3(6) Rafter Spans for Common Lumber Species.  (Ground Snow Load = 50 pounds per square foot.  Ceiling Attached to Rafters, L/ = 240).  Reserved.

Table 2308.10.4.1 Rafter Tie Connections.  Change to read as shown.

TABLE 2308.10.4.1

RAFTER TIE CONNECTIONS

| RAFTER SLOPE | TIE SPACING (inches) | Roof span (feet) NO SNOW LOAD |  |  |  | GROUND SNOW LOAD (pound per square foot) |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | 30 pounds per square foot |  |  |  |  |  | 50 pounds per square foot |  |  |  |
|  |  |  |  |  |  | Roof span (feet) |  |  |  |  |  |  |  |  |  |
|  |  | 12 | 20 | 28 | 36 | 12 | 20 | 28 |  |  | 36 | 12 | 20 | 28 | 36 |
|  |  | Required number of 16d common (31/2 |  |  |  |  |  |  | x 0.162 ) nailsa,b per connectionc,d,e,f |  |  |  |  |  |  |
| 3:12 | 12 | 4 | 6 | 8 | 10 | 4 | 6 |  |  | 8 | 11 | 5 | 8 | 12 | 15 |
|  | 16 | 5 | 7 | 10 | 13 | 5 | 8 |  |  | 11 | 14 | 6 | 11 | 15 | 20 |
|  | 24 | 7 | 11 | 15 | 19 | 7 | 11 |  |  | 16 | 21 | 9 | 16 | 23 | 30 |
|  | 32 | 10 | 14 | 19 | 25 | 10 | 16 |  |  | 22 | 28 | 12 | 27 | 30 | 40 |
|  | 48 | 14 | 21 | 29 | 37 | 14 | 32 |  |  | 36 | 42 | 18 | 32 | 46 | 60 |
| 4:12 | 12 | 3 | 4 | 5 | 6 | 3 | 5 |  |  | 6 | 8 | 4 | 6 | 9 | 11 |
|  | 16 | 3 | 5 | 7 | 8 | 4 | 6 |  |  | 8 | 11 | 5 | 8 | 12 | 15 |
|  | 24 | 4 | 7 | 10 | 12 | 5 | 9 |  |  | 12 | 16 | 7 | 12 | 17 | 22 |
|  | 32 | 6 | 9 | 13 | 16 | 8 | 12 |  |  | 16 | 22 | 10 | 16 | 24 | 30 |
|  | 48 | 8 | 14 | 19 | 24 | 10 | 18 |  |  | 24 | 32 | 14 | 24 | 34 | 44 |
| 5:12 | 12 | 3 | 3 | 4 | 5 | 3 | 4 |  |  | 5 | 7 | 3 | 5 | 7 | 9 |
|  | 16 | 3 | 4 | 5 | 7 | 3 | 5 |  |  | 7 | 9 | 4 | 7 | 9 | 12 |
|  | 24 | 4 | 6 | 8 | 10 | 4 | 7 |  |  | 10 | 13 | 6 | 10 | 14 | 18 |
|  | 32 | 5 | 8 | 10 | 13 | 6 | 10 |  |  | 14 | 18 | 8 | 14 | 18 | 24 |
|  | 48 | 7 | 11 | 15 | 20 | 8 | 14 |  |  | 20 | 26 | 12 | 20 | 28 | 36 |
| 7:12 | 12 | 3 | 3 | 3 | 4 | 3 | 3 |  |  | 4 | 5 | 3 | 4 | 5 | 7 |
|  | 16 | 3 | 3 | 4 | 5 | 3 | 4 |  |  | 5 | 6 | 3 | 5 | 7 | 9 |
|  | 24 | 3 | 4 | 6 | 7 | 3 | 5 |  |  | 7 | 9 | 4 | 7 | 10 | 13 |
|  | 32 | 4 | 6 | 8 | 10 | 4 | 8 |  |  | 10 | 12 | 6 | 10 | 14 | 18 |
|  | 48 | 5 | 8 | 11 | 14 | 6 | 10 |  |  | 14 | 18 | 9 | 14 | 20 | 26 |
| 9:12 | 12 | 3 | 3 | 3 | 3 | 3 | 3 |  |  | 3 | 4 | 3 | 3 | 4 | 5 |
|  | 16 | 3 | 3 | 3 | 4 | 3 | 3 |  |  | 4 | 5 | 3 | 4 | 5 | 7 |
|  | 24 | 3 | 3 | 5 | 6 | 3 | 4 |  |  | 6 | 7 | 3 | 6 | 8 | 10 |
|  | 32 | 3 | 4 | 6 | 8 | 4 | 6 |  |  | 8 | 10 | 5 | 8 | 10 | 14 |
|  | 48 | 4 | 6 | 9 | 11 | 5 | 8 |  |  | 12 | 14 | 7 | 12 | 16 | 20 |
| 12:12 | 12 | 3 | 3 | 3 | 3 | 3 | 3 |  |  | 3 | 3 | 3 | 3 | 3 | 4 |
|  | 16 | 3 | 3 | 3 | 3 | 3 | 3 |  |  | 3 | 4 | 3 | 3 | 4 | 5 |
|  | 24 | 3 | 3 | 3 | 4 | 3 | 3 |  |  | 4 | 6 | 3 | 4 | 6 | 8 |
|  | 32 | 3 | 3 | 4 | 5 | 3 | 5 |  |  | 6 | 8 | 4 | 6 | 8 | 10 |
|  | 48 | 3 | 4 | 6 | 7 | 4 | 7 |  |  | 8 | 12 | 6 | 8 | 12 | 16 |

For SI: 1 inch = 25.4 mm, 1 foot = 304.8 mm, 1 pound per square foot = 47.8 N/m2.

a. 40d box (5″0.162″) or l6d sinker (31/4″0.148″) nails are permitted to be substituted for 16d common (31/2″0.16″) nails.

b. Nailing requirements are permitted to be reduced 25 percent if nails are clinched.

c. Rafter tie heel joint connections are not required where the ridge is supported by a load-bearing wall, header or ridge beam.

d. When intermediate support of the rafter is provided by vertical struts or purlins to a load-bearing wall, the tabulated heel joint connection requirements are permitted to be reduced proportionally to the reduction in span.

e. Equivalent nailing patterns are required for ceiling joist to ceiling joist lap splices.

f. Connected members shall be of sufficient size to prevent splitting due to nailing.

g. Reserved.

2308.11 Additional requirements for conventional construction in Seismic Design Category B or C.  Change to read as shown.

- 2308.11 Additional requirements for conventional construction in Seismic Design Category B or C.  Reserved.

- 2308.11.1 Number of stories.  Change to read as shown.

- 2308.11.1 Number of stories.  Reserved.

- 2308.11.2 Concrete or masonry.  Change to read as shown.

- 2308.11.2 Concrete or masonry.  Reserved.

- 2308.11.3 Framing and connection details.  Change to read as shown.

- 2308.11.3 Framing and connection details.  Reserved.

- 2308.11.3.1 Anchorage.  Change to read as shown.

- 2308.11.3.1 Anchorage.  Reserved.

- 2308.11.3..2 Stepped footings.  Reserved

- 2308.11.3.3 Openings in horizontal diaphragms.  Reserved.

- 2308.12 Additional requirements for conventional construction in Seismic Design Category D or E.  Change to read as shown.

2308.12 Additional requirements for conventional construction in Seismic Design Category D or E.  Reserved.

Table 2308.12.4 Wall Bracing In Seismic Design Categories D And E

- (Minimum Length Of Wall Bracing Per Each 25 Linear Feet Of Braced Wall Linea) Change to read as shown.

Table 2308.12.4 Wall Bracing In Seismic Design Categories D And E

(Minimum Length Of Wall Bracing Per Each 25 Linear Feet Of Braced Wall Linea) Reserved.

Sections 2309-2313  Add to read as shown.

Sections 2309-2313 Reserved.

Section 2314 – 2330 High Velocity Hurricane Zone, add per the text in the 2007 Florida Building Code.

Sections 2314-2330 High-Velocity Hurricane Zone.

See Chapter 23 - HVHZ

Chapter 24 Glass and Glazing

Section 2401 General.

2401.1. Scope.  Change to read as shown.

2401.1 Scope.  The provisions of this chapter shall govern the materials, design, construction and quality of glass, light-transmitting ceramic and light-transmitting plastic panels for exterior and interior use in both vertical and sloped applications in buildings and structures.

Exception: Buildings and structures located within the high-velocity hurricane zone shall comply with the provisions of Sections 2410 through 2415.

Section 2403 General Requirements for Glass

Section 2403.1 Identification is revised to read as follows:

2403.1 Identification. Each pane shall bear the manufacturer’s mark designating the type and thickness of the glass or glazing material. With the exception of tempered glazing materials or laminated materials, the identification shall not be omitted unless approved and an affidavit is furnished by the glazing contractor certifying that each light is glazed in accordance with approved construction documents that comply with the provisions of this chapter. Safety glazing shall be identified in accordance with Section 2406.2. Each pane of tempered glass, except tempered spandrel glass, shall be permanently identified by the manufacturer and each pane of laminated glass shall be permanently identified with the laminator, overall glass thickness and trade name of interlayer.  The identification mark shall be acid etched, sand blasted, ceramic fired, laser etched, embossed or of a type that, once applied, cannot be removed without being destroyed. Tempered or laminated spandrel glass shall be provided with a removable paper marking by the manufacturer.

Section 2404 Wind and Dead Loads on Glass.  Change to read as shown.

Section 2404 Wind and Dead Loads on Glass

- 2404.1 Vertical glass.  Change to read as shown.

- 2404.1 Vertical glass.  Glass sloped 15 degrees (0.26 rad) or less from vertical in windows, curtain and window walls, doors and other exterior applications shall be designed to resist the wind loads for components and cladding.  The load resistance of glass under uniform load shall be determined in accordance with ASTM E 1300. Design of exterior windows and glass doors in accordance with Section 2404.1 shall utilize the same edition of ASTM E 1300 used for testing in accordance with Section 1715.51714.5. The design of vertical glazing shall be based on the following equation:

- Fgw   Fga	(Equation 24-1)

- where:

Fgw is the wind load on the glass computed in accordance with Section 1609 multiplied by 0.60 and

Fga is the short duration load resistance of the glass as determined in accordance with ASTM E 1300.

- 2404.2 Sloped glass.  Change to read as shown.

2404.2 Sloped glass. Glass sloped more than 15 degrees (0.26 rad) from vertical in skylights, sunrooms, sloped roofs and other exterior applications shall be designed to resist the most critical of the following combinations of loads.

Fg=Wo–D (Equation 24-2)

Fg=Wi+D (Equation 24-3)

Fg=0.5Wi+D (Equation 24-4)

where:

D = Glass dead load psf (kN/m2).

For glass sloped 30 degrees (0.52 rad) or less from horizontal,

D = 13 tg (For SI: 0.0245 tg).

For glass sloped more than 30 degrees (0.52 rad) from horizontal,

D = 13 tg cos (For SI: 0.0245 tg cos ).

Fg = Total load, psf (kN/m2) on glass.

tg = Total glass thickness, inches (mm) of glass panes and plies.

Wi = Inward wind force, psf (kN/m2) as calculated in Section 1609 multiplied by 0.60.

Wo = Outward wind force, psf (kN/m2) as calculated in Section 1609 multiplied by 0.60.

= Angle of slope from horizontal.

Exception: Unit skylights shall be designed in accordance with Section 2405.5. and tubular daylighting devices (TDDs) shall comply with the requirements of Section 2405.  [4332]

The design of sloped glazing shall be based on the following equation:

Fg Fga (Equation 24-5)

Fg = Total load on the glass determined from the load combinations above.

Fga = Short duration load resistance of the glass as determined according to ASTM E 1300 for Equations 24-2 and 24-3; or the long duration load resistance of the glass as determined according to ASTM E 1300 for Equation 24-4

2404.3.1 Vertical wired glass. (no change)

Fgw = Is the wind load on the glass computed per Section 1609 multiplied by 0.60.

2404.3.3 Vertical patterned glass.  (no change)

Fgw =  Wind load on the glass computed per Section 1609 multiplied by 0.60.

2404.3.5 Vertical sandblasted glass. (no change)

Fg = The wind load on the glass computed per Section 1609 multiplied by 0.60.

[S4706]

2405.5.2 Unit skylights – Change to read as shown.

2405.5.2 Unit skylights rated for separate performance grades for positive and negative design pressure. (no change)

Wo = Outward wind force, psf (kN/m2) as calculated in Section 1609 multiplied by 0.60.

(*2 places*)

[S4707]

Sections 2410 – 2415 High Velocity Hurricane Zone.  Florida specific, add per the 2007 Florida Building Code.

Sections 2410-2415 HVHZ

See Chapter 24 - HVHZ

Chapter 25 Gypsum Board and Plaster

Section 2501 General

2501.1.1 General.  Change to read as shown.

- 2501.1.1 General.  Provisions of this chapter shall govern the materials, design, construction and quality of gypsum board, lath, gypsum plaster and cement plaster.

Exception: Buildings and structures located within the high-velocity hurricane zone shall comply with the provisions of Sections 2514 through 2520.

Section 2505 Shear Wall Construction

2505.1 Resistance to shear (wood framing). Change to read as shown.

2505.1 Resistance to shear (wood framing). Wood-framed shear walls sheathed with gypsum board, lath and plaster shall be designed and constructed in accordance with Section 2306.7 and are permitted to resist wind and seismic loads. Walls resisting seismic loads shall be subject to the limitations in Section 12.2.1 of ASCE 7.

2505.2  Resistance to shear (steel framing).  Change to read as shown.

2505.2 Resistance to shear (steel framing). Cold-formed steel-framed shear walls sheathed with gypsum board and constructed in accordance with the materials and provisions of Section 2210.5 are permitted to resist wind loads.

Section 2506 Gypsum Board Materials

2506.2.1 Other materials.  Change to read as shown.

2506.2.1 Other materials. Metal suspension systems for acoustical and lay-in panel ceilings shall conform with ASTM C 635 listed in Chapter 35 and Section 13.5.6 of ASCE 7 for installation in high seismic areas.

2508.5 Horizontal gypsum board diaphragm ceilings – Change to read as shown.

2508.5 Horizontal gypsum board diaphragm ceilings (Allowable stress design). Gypsum board shall be permitted to be used on wood joists to create a horizontal diaphragm ceiling in accordance with Table 2508.5.

Table 2508.5 Shear Capacity for Horizontal Wood Framed Gypsum Board Diaphragm Ceiling Assemblies.  Change to read as shown.

- Table 2508.5 Allowable Shear Capacity for Horizontal Wood Framed Gypsum Board Diaphragm Ceiling Assemblies

[S4708]

- a. Values are not cumulative with other horizontal diaphragm values and are for short-term loading due to wind loading. Values shall be reduced 25 percent for normal loading.

- b.  Reserved.

c. 1¼-inch, No. 6 Type S or W screws are permitted to be substituted for the listed nails.

Section 2510.8 Fenestration.  Add to read as shown.

- 2510.8 Fenestration.  The juncture of exterior plaster and fenestration products shall be sealed with a sealant complying with AAMA 800 and ASTM C 920 Class 25 Grade NS or greater for proper joint expansion and contraction, ASTM C1281, AAMA 812,  or other approved standard as appropriate for the type of sealant.

Sections 2514 -2520 High Velocity Hurricane Zone.  Florida specific, add to read per the 2007 Florida Building Code.

Section 2514 through Section 2520 are HVHZ.

Also, see Chapter 25 - HVHZ

Chapter 26 Plastic

Section 2601 General

Section 2601.1 Scope, revise text to read as follows:

2601.1 Scope. These provisions shall govern the materials, design, application, construction and installation of foam plastic, foam plastic insulation, plastic veneer, interior plastic finish and trim and light-transmitting plastics. See Chapter 14 for requirements for exterior wall finish and trim.

Exception: Buildings and structures located within the high-velocity hurricane zone shall comply with the provisions of Sections 2603.8 and 2612.

Section 2603 Foam-Plastic Insulation

- 2603.4.1.12 Interior signs.  Change to read as shown.

2603.4.1.12 Interior signs. Foam plastic used for interior signs in covered mall buildings in accordance with Section 402.16 shall be permitted without a thermal barrier. Foam plastic signs that are not affixed to interior building surfaces shall comply with Chapter 8 of the International Florida Fire Prevention Code.

- 2603.8 Protection from termite damage.  Change to read as shown.

- 2603.8 Protection from termite damage.

- 2603.8.1  Add to read as shown.

- 2603.8.1  Foam-plastic insulation including, but not limited to, extruded or expanded polystyrene or polyisocyanurate shall not be installed below grade on foundation walls or below grade on the exterior of slab foundations.

- Exceptions:

- 1. When in addition to the requirements of Section 2304.11.6, an approved method of protecting the foam plastic and structure from subterranean termite damage is provided.

- 2. Within Types I and II-B construction.

- 3. On the interior side of basement walls.

2603.8 Protection against termites. In Florida areas where the probability of termite infestation is very heavy in accordance with Figure 2603.8, extruded and expanded polystyrene, polyisocyanurate and other foam plastics shall not be installed on the exterior face or under interior or exterior foundation walls or slab foundations located below grade. The clearance between foam plastics installed above grade and exposed earth shall be at least 6 inches (152 mm).

Exceptions:

1. Buildings where the structural members of walls, floors, ceilings and roofs are entirely of noncombustible materials or preservative-treated wood.

2. An approved method of protecting the foam plastic and structure from subterranean termite damage is provided.

3. On the interior side of basement walls.

FIGURE 2603.8

TERMITE INFESTATION PROBABILITY MAP

2603.8.2  Add to read as shown.

2603.8.2  Clearance between earth and foam plastics applied to the exterior wall shall be not less than 6 inches (152 mm).[3930]

Renumber Section 2612 as 2313.  (see HVHZ)

Section 2612 Fiber Reinforced Polymer and Fiberglass Reinforced Polymer

2612.6 Exterior use.  Change to read as shown.

2612.6 Exterior use. Fiber reinforced polymer or fiberglass reinforced polymer shall be permitted to be installed on the exterior walls of buildings of any type of construction when such polymers meet the requirements of Section 2603.5 and is fireblocked in accordance with Section 717. The fiber reinforced polymer or the fiberglass reinforced polymer shall be designed for uniform live loads as required in Table 1607.1 as well as for snow loads, wind loads and earthquake loads as specified in Sections 1608, 1609 and 1613, respectively.

Exceptions:

1. When all of the following conditions are met:

1.1. When the area of the fiber reinforced polymer or the fiberglass reinforced polymer does not exceed 20 percent of the respective wall area, the fiber reinforced polymer or the fiberglass reinforced polymer shall have a flame spread index of 25 or less or when the area of the fiber reinforced polymer or the fiberglass reinforced polymer does not exceed 10 percent of the respective wall area, the fiber reinforced polymer or the fiberglass reinforced polymer shall have a flame spread index of 75 or less. The flame spread index requirement shall not be required for coatings or paints having a thickness of less than 0.036 inch (0.9 mm) that are applied directly to the surface of the fiber reinforced polymer or the fiberglass reinforced polymer.

1.2. Fireblocking complying with Section 717.2.6 shall be installed.

1.3. The fiber reinforced polymer or the fiberglass reinforced polymer shall be installed directly to a noncombustible substrate or be separated from the exterior wall by one of the following materials: corrosion-resistant steel having a minimum base metal thickness of 0.016 inch

(0.41 mm) at any point, aluminum having a minimum thickness of 0.019 inch (0.5 mm) or other approved noncombustible material.

1.4. The fiber reinforced polymer or the fiberglass reinforced polymer shall be designed for uniform

live loads as required in Table 1607.1 as well as for snow loads, wind loads and earthquake loads as specified in Sections 1608, 1609 and 1613, respectively.

2. When installed on buildings that are 40 feet (12 190 mm) or less above grade, the fiber reinforced polymer or the fiberglass reinforced polymer shall meet the requirements of Section 1406.2 and shall comply with all of the following conditions:

2.1. Where the fire separation distance is 5 feet (1524 mm) or less, the area of the fiber reinforced polymer or the fiberglass reinforced polymer shall not exceed 10 percent of the wall area. Where the fire separation distance is greater than 5 feet (1524 mm), there shall be no limit on the area of the exterior wall coverage using fiber reinforced polymer or the fiberglass reinforced polymer.

2.2. The fiber reinforced polymer or the fiberglass reinforced polymer shall have a flame spread index of 200 or less. The flame spread index requirement shall not be required for coatings

or paints having a thickness of less than 0.036 inch (0.9 mm) that are applied directly to the surface of the fiber reinforced polymer or the fiberglass reinforced polymer.

2.3. Fireblocking complying with Section 717.2.6 shall be installed.

2.4. The fiber reinforced polymer or the fiberglass reinforced polymer shall be designed for uniform live loads as required in Table 1607.1 as well as for snow loads, wind loads and earthquake loads as specified in Sections 1608, 1609 and 1613, respectively.

Section 2613 is High Velocity Hurricane Zone.  Florida specific, add to read per the 2007 Florida Building Code.

Section 2613 is HVHZ.

See Chapter 26 - HVHZ

Chapter 27 Electrical

Section 2701 General

2701.1 Scope.  Change to read as shown.

2701.1 Scope.  This chapter governs the electrical components, equipment and systems used in buildings and structures covered by this code. Electrical components, equipment and systems shall be designed and constructed in accordance with the provisions of the NFPA 70, National Electrical Code..

Section 2702 Emergency and Standby Power Systems.

2702.1 Installation.  Change to read as shown.

- 2702.1 Installation.  Emergency and standby power systems shall be installed in accordance with the NFPA 70, National Electrical Code, NFPA 110 and NFPA 111.

2702.1.1 Stationary generators.  Change to read as shown.

2702.1.1 Stationary generators.  Reserved.

2702.2 Where required.  Change to read as shown.

2702.2 Where required.  Reserved.

- 2702.3 Maintenance.  Change to read as shown.

2702.3 Maintenance.  Reserved.

Section 2703 Cross References.  Add to read as shown.

2703 Cross References.

2703.1 Cross references.  Add to read as shown.

2703.1 Cross references.  See Table 2703.

Table 2703 Cross References Defining Electrical Requirements of the Florida Building Code.  Add to read as shown.

TABLE 2703

CROSS REFERENCES DEFINING ELECTRICAL REQUIREMENTS  OF THE FLORIDA BUILDING CODE

Note: This table is provided only as a tool to assist the construction industry as a general guide. User should review all sections of the code in order to determine specific applicable electrical requirements.

| Florida Building Code 2007 Electrical Systems |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | Cross Reference |  |  |  |
| ##### Florida Building Code - Building |  |  |  |  |
| Section |  |  | Section |  |
| Chapter 1 | Administration |  | Chapter 7 | Fire-Resistance-Rated Construction |
| 101 | General |  | 712 | Penetrations |
| 102 | Applicability |  | 714 | Fire-Resistance Rating of Structural Members |
| 105 | Permits |  | 715 | Opening Protective |
| 106 | Construction Documents |  | 716 | Ducts and Air Transfer Openings |
| 107 | Temporary Structures and Uses |  |  |  |
| 108 | Fees |  | Chapter 9 | Fire Protection Systems |
| 109 | Inspections |  | 901 | General |
| 111 | Service Utilities |  | 902 | Definitions |
|  |  |  | 903 | Automatic Sprinkler Systems |
| Chapter 2 | Definitions |  | 904 | Alternative Automatic Fire-Extinguishing |
| 202 | Definitions |  |  | Systems |
|  |  |  | 907 | Fire Alarm and Detection Systems |
| Chapter 3 | Use and Occupancy Classification |  | 908 | Emergency Alarm Systems |
| 302 | Classification |  | 909 | Smoke Control Systems |
| 306 | Factory Group F |  | 910 | Smoke and Heat Vents |
| 307 | High -Hazard Group H |  | 911 | Fire Command Center |
| 311 | Storage Group S |  |  |  |
|  |  |  | Chapter 10 | Means of Egress |
| Chapter 4 | Special Detailed Requirement |  | 1006 | Means of Egress Illumination and Signs |
|  | Based on Use and Occupancy |  | 1008 | Doors, Gates and Turnstiles |
| 402 | Covered Mall Buildings |  | 1033 | Day Care |
| 403 | High-Rise Buildings |  |  |  |
| 404 | Atriums |  | Chapter 11 | Florida Building Code, Accessibility |
| 405 | Underground Buildings |  |  |  |
|  |  |  |  | Part A |
| 406 | Motor-Vehicle-Related Occupancies |  |  |  |
| 407 | Group I-2 |  |  |  |
| 408 | Group I-3 |  |  |  |
| 409 | Motion Picture Projection Rooms |  |  |  |
| 412 | Aircraft-Related Occupancies |  |  |  |
| 414 | Hazardous Materials |  |  |  |
| 415 | Groups H-1, H-2, H-3, H-4 and H-5 |  |  |  |
| 419 | Hospitals |  | Chapter 12 |  |
| 420 | Nursing Homes |  | 1205 | Lighting |
| 421 | Ambulatory Surgical Centers |  |  |  |
| 423 | State Requirements for Educational |  | Chapter 13 | Florida Building Code, Energy Conservation |
|  | Facilities |  |  |  |
| 424 | Swimming Pools and Bathing Places |  |  |  |
|  | (Public and Private) |  |  |  |
| 425 | Public Lodging Establishments |  |  |  |
| 426 | Public Food Service Establishments |  |  |  |
| 427 | Mental Health Programs |  |  |  |
| 428 | Manufactured Buildings |  |  |  |
| 431 | Transient Public lodging Establishments |  |  |  |
| 435 | Control of Radiation Hazards |  | Chapter 26 | Plastic |
| 436 | Day Care Occupancies |  | 2606 | Light-Transmitting Plastics |
|  | Florida Building Code 2007 |  |  |  |
| Electrical Systems |  |  |  |  |
| Cross Reference Florida Building Code - Building Continued |  |  |  |  |
| Section |  |  | Section |  |
| Chapter 26 | Plastic |  | 3006 | Machine Rooms |
| Continued |  |  | 3011 | Alterations to Electric and Hydraulic |
| 2611 | Light-Transmitting Plastic Interior Signs |  |  | Elevators and Escalators |
| 2612 | High-Velocity Hurricane Zones-Plastics |  | Chapter 31 | Special Construction |
|  |  |  | 3102 | Membrane Structures |
| Chapter 27 | Electrical |  | 3108 | Radio and Television Towers |
| 2701 | General |  | 3112 | Lighting, Mirrors, Landscaping |
| 2702 | Emergency and Standby Power Systems |  |  |  |
|  |  |  | Chapter 33 |  |
| Chapter 30 | Elevators and Conveying Systems |  | 3306 | Protection of Pedestrians |
| 3003 | Emergency Operations |  | 3310 | Mean of Egress |
| 3005 | Conveying Systems |  |  |  |
| 3006 | Machine Romms |  | Chapter 35 | Referenced Standards |
|  | Florida Building Code 2007 Electrical Systems Cross Reference Residential |  |  |  |
| Chapter 3 | Building Planning |  | Chapter 24 | Fuel Gas |
| R303 | Light, Ventilation and Heating |  | G2403(202) | General Definitions |
| R313 | Smoke Alarms |  | G2410(309) | Electrical |
| R317 | Dwelling Unit Separation |  | G2411(310) | Electrical Bonding |
|  |  |  | G2440(615) | Sauna Heaters |
| Chapter 8 | Roof -Ceiling Construction |  |  |  |
| R808 | Insulation Clearance |  | Chapter 33 | General Requirements Electrical |
|  |  |  | E3301 | General Requirements Electrical |
| Chapter 13 | General Mechanical System |  |  |  |
|  | Requirements |  | Chapter 43 | Referenced Standards |
| M1303 | Labeling of Equipment |  |  |  |
| M1305 | Appliance Access |  |  |  |
|  | Florida Building Code 2007 Electrical Systems Cross Reference |  |  |  |
|  | Florida Building Code - Existing Building |  |  |  |
| Chapter 3 | Prescriptive compliance method |  | Chapter 12 | Relocated or Moved Buildings |
| 801 | Alteration-Level 3 |  | 1202 | Requirements |
| Chapter 5 | Repairs |  | Chapter 13 | Compliance Alternatives |
| 501 | General |  | 1301 | General |
| 507 | Electrical |  |  |  |
|  |  |  | Chapter 15 | Referenced Standards |
| Chapter 6 | Alterations Level 1 |  |  |  |
| 608 | Electrical |  | Appendix B | Standard for Rehabilitation |
| Chapter 7 | Alterations Level 2 |  |  |  |
| 708 | Electrical |  |  |  |
| Chapter 9 | Change of Occupancy |  |  |  |
| 908 | Electrical |  |  |  |
| 911 | Other Requirements |  |  |  |
| Chapter 10 | Additions |  |  |  |
| 1001 | General |  |  |  |
| 1004 | Smoke Alarms in Occupancy |  |  |  |
|  | Groups R-3 and R-4 |  |  |  |
|  | Florida Building Code 2007 Electrical Systems Cross Reference |  |  |  |
|  | Florida Building Code - Mechanical |  |  |  |
| Section |  |  | Section |  |
|  |  |  | 912 | Infrared Radiant Heaters |
| Chapter 3 | General Regulations |  | 917 | Cooking Appliances |
| 301 | General |  | 918 | Forced-Air Warm-Air Furnaces |
|  |  |  | 924 | Stationary Fuel Cell Power Plants |
| 306 | Access and Service Space |  | 927 | Residential Electric Duct Heaters |
|  |  |  | 928 | Vented Residential Floor Furnaces |
| Chapter 5 | Exhaust Systems |  |  |  |
| 502 | Required Systems |  | Chapter 10 | Boilers, Water Heaters and |
| 503 | Motors and Fans |  |  | Pressure Vessels |
| 504 | Clothes Dryer Exhaust |  | 1001 | General |
| 509 | Fire Suppression Systems |  | 1004 | Boilers |
| 513 | Smoke Control Systems |  | 1006 | Safety and Pressure Relief Valves |
|  |  |  |  | And Controls |
| Chapter 6 | Duct Systems |  |  |  |
| 601 | General |  | Chapter 11 |  |
| 602 | Plenums |  | 1104 | System Application Requirements |
| 606 | Smoke Detection System Control |  | 1105 | Machinery Room, General Requirements |
| 607 | Ducts and Air Transfer Openings |  | 1106 | Machinery Room, Special Requirements |
| Chapter 8 | Chimneys and Vents |  | Chapter 15 | Referenced Standards |
| 801 | General |  |  |  |
| 804 | Direct-Vent, Integral Vent and |  |  |  |
|  | Mechanical Draft System |  |  |  |
|  | Florida Building Code 2007 Electrical Systems Cross Reference |  |  |  |
|  | Florida Building Code - Plumbing |  |  |  |
| Chapter 6 | Water Supply and Distribution |  | Part II | Design Criteria |
| 601 | General |  | I. | Control Valves |
| 612 | Well Pumps and Tanks used for Private |  |  |  |
|  | Potable Water Systems |  | Part IV | Materials |
|  |  |  | H. | Low Voltage Wiring |
| Chapter 11 | Storm Drainage |  | I. | Irrigation Controllers |
| 1113 | Sumps and Pumping Systems |  | J. | Pumps and Wells |
| Chapter 13 | Referenced Standards |  | Part V. | Installation |
|  |  |  | E. | Low Voltage Wire Installation |
| Appendix F | Proposed Construction Building Codes |  | F. | Hydraulic Control Tubing |
|  | For Turf and Landscape Irrigation |  |  |  |
|  | Systems |  |  |  |
|  | Florida Building Code 2007 Electrical Systems Cross Reference |  |  |  |
|  | Florida Building Code - Fuel Gas |  |  |  |
| Chapter 2 | Definitions |  | Chapter 6 | Specific Appliances |
|  |  |  | 627 | Air Conditioning Equipment |
| Chapter 3 | General Regulations |  | 630 | Infrared Radiant Heaters |
| 306 | Access and Service Space |  |  |  |
| 309 | Electrical |  | Chapter 7 | Gaseous Hydrogen Systems |
| 310 | Electrical Bonding |  | 703 | General Requirements |
|  |  |  | 706 | Location of Gaseous Hydrogen Systems |
| Chapter 4 | Gas Piping Installations |  |  |  |
| 413 | Compressed natural Gas Motor Vehicle |  | Chapter 8 | Referenced Standards |
|  | Fuel- Dispensing Stations |  |  |  |

Section 2704 Bonding Metal Framing Members.  Add to read as shown.

2704  Bonding Metal Framing Members: Metal framing members. Metal framing members shall be bonded to the equipment grounding conductor for the circuit that may energize the framing and be sized in accordance with the National Electric Code Table 250.122. For the purpose of this section, a grounded metal outlet box attached to the framing shall be permitted.

Section 2705 GFCI Protection

2705.1 NFPA 70 - 08: National Electric Code, Article 680 (Swimming Pools, Fountains, and Similar Installation), Section 680.22(B), GFCI Protection, is amended to read as follows:

(B)  GFCI Protection.  Outlets supplying pool pump motors from branch circuits with short-circuit and ground-fault protection rated 15 or 20 amperes, 125 volt or 240 volt, single phase, whether by receptacle or direct connection, shall be provided with ground-fault circuit-interrupter protection for personnel.

Exception: One-and two-family dwellings.  (3450)

Chapter 28 Mechanical Systems

Section 2801 General

2801.1 Scope.  Change to read as shown.

2801.1 Scope.  Mechanical appliances, equipment and systems shall be constructed, installed and maintained in accordance with the Florida Building Code, Mechanical and the Florida Building Code, Fuel Gas. Masonry chimneys, fireplaces and barbecues shall comply with the Florida Building Code, Mechanical and Chapter 21 of this code.

Chapter 29 Plumbing Systems

Section 2901 General

2901.1. Scope.  Change to read as shown.

2901.1 Scope.  The provisions of this chapter and the Florida Building Code, Plumbing shall govern the erection, installation, alteration, repairs, relocation, replacement, addition to, use or maintenance of plumbing equipment and systems. Plumbing systems and equipment shall be constructed, installed and maintained in accordance with the Florida Building Code, Plumbing.

Section 2902 Minimum Plumbing Fixtures.  Change to read as shown.

Section 2902  Minimum Plumbing Fixtures. Reserved

Chapter 30 Elevators and Conveying Systems

Section 3001 General

3001.1 Scope.  Change to read as shown.

3001.1 Scope. This chapter governs the design, construction, installation, alteration, and repair and maintenance of elevators and conveying systems and their components.

Note: Other administrative and programmatic provisions may apply. See the Department of Business and Professional Regulation [DBPR] Chapter 399, Florida Statutes, and 61C-5, Florida Administrative Code. The regulation and enforcement of the following sections of the adopted codes, and their addenda, are preempted to the Bureau of Elevator Safety of the Department of Business and Professional regulation: ASME A17.1, Part 8, ASME A17.3, Sections 1.2, 1.5, ASME A18.1, Part 10.

[3468]

3001.2 Referenced standards.  Change to read as shown.

3001.2 Referenced standards. Except as otherwise provided for in this code, the design, construction, installation, alteration, repair and maintenance of elevators and conveying systems and their components shall conform to ASME A17.1/CSA B44, ASME A17.1S, ASME A17.3 and ASME A18.1, ASME A90.1, ASME B20.1, ALI ALCTV, and ASCE 24-05 for construction in flood hazard areas.

The Division of Hotels and Restaurants may grant exceptions, variances and waivers to the Elevator Safety Code as authorized by the Elevator Safety Code Safety Code for Elevators and Escalators (ASME A17.1, Section 1.2) and Florida Statutes (Chapter 120.)

[3468]

3001.3 Accessibility.  Change to read as shown.

3001.3 Accessibility. Passenger elevators are required to be accessible by the Florida Building Code, Accessibility Chapter 11. shall conform to ICC A117.1.

[S4727]

[3468]

- 3001.5 Design, installation and alteration of elevators.  Add to read as shown.

3001.5 Design, installation and alteration of elevators.

3001.5.1   Each new elevator shall comply with the Florida Elevator Safety Code that was in effect at the time of receipt of application for the construction permit for the elevator.

3001.5.2   Each alteration to, or relocation of, an elevator shall comply with the Florida Elevator Safety Code that was in effect at the time of receipt of the application for the construction permit for the alteration or relocation.

3001.5.3   All existing elevators shall comply with ASME A17.3

[3468]

3001.6  Add to read as shown.

- 3001.6  As used in this chapter, the term:

- ALTERATION.  Any change or addition to the vertical conveyance other than maintenance, repair or replacement.

ALTERATION.  Any change to equipment, including its parts, components, and/or subsystems, other than maintenance, repair, or replacement.

- [3468]

- CERTIFICATE OF OPERATION means a document issued by the department which indicates that the conveyance has had the required safety inspection and tests and that fees have been paid as provided in this Chapter 399, FS.

- CONVEYANCE. An elevator, dumbwaiter, escalator, moving sidewalk, platform lift and stairway chairlift.

- DEPARTMENT. For the purpose of this section, means the Department of Business and Professional Regulation.

DIVISION. For the purpose of this section, means the Division of Hotels and Restaurants of the Department of Business and Professional Regulation.

- ELEVATOR. One of the following mechanical devices:

- (a) A hoisting and lowering mechanism, equipped with a car and platform that moves in guide rails and serves two or more landings to transport material or passengers or both.

- (b) An escalator, which is a power-driven, inclined continuous stairway used for raising or lowering passengers.

- (c) A dumbwaiter, which is a hoisting and lowering mechanism equipped with a car of limited size which moves in guide rails and serves two or more landings.

- (d) A moving walk, which is a type of passenger-carrying device on which passengers stand or walk and in which the passenger-carrying surface remains parallel to its direction of motion and is uninterrupted.

- (e) An inclined stairway chairlift, which is a device used to transport physically handicapped persons over architectural barriers.

(f) An inclined or vertical wheelchair lift, which is a device used to transport wheelchair handicapped persons over architectural barriers.

- Exceptions:

- Personnel hoists and material hoists within the scope of ASME A10.

- Man lifts within the scope of ASME A90.1.

- Mobile scaffolds, towers, and platforms within the scope of ANSI A92.

- Powered platforms and equipment for exterior and interior maintenance within the scope of ASME A120.1.

- Conveyors and related equipment within the scope of ASME B20.1.

- Cranes, derricks, hoists, hooks, jacks and slings within the scope of ASME B30.

- Industrial trucks within the scope of ASME B56.

- Portable equipment, except for portable escalators that are covered by this code.

- Tiered or piling machines used to move materials to and from storage located and operating entirely within one story.

- Equipment for feeding or positioning materials at machine tools and printing presses.

- Skip or furnace hoists.

- Wharf ramps.

- Railroad car lifts or dumpers.

- Line jacks, false cars, shafters, moving platforms and similar equipment used for installing an elevator by a contractor licensed in this state.

- Automated people movers at airports.

- Elevators in television and radio towers.

- Hand-operated dumbwaiters.

- Sewage pump station lifts.

- Automobile parking lifts.

Equipment covered in Section 1.1.2 of the Elevator Safety Code ASME A17.1 Safety Code for Elevators and Escalators.

- [3468]

Elevators, inclined stairway chairlifts, and inclined or vertical wheelchair lifts located in private residences.

- ESCALATOR. An installation defined as an escalator in the Florida Building Code.

- EXISTING INSTALLATION. An installation defined as an “installation, existing” in the Florida Building Code.

PRIVATE RESIDENCE. A separate dwelling or a separate apartment in a multiple dwelling which is occupied by members of a single family.

Section 3002 Hoistway Enclosures

Section 3002.4 Elevator car to accommodate an ambulance stretcher, revise text to read as follows:

3002.4 Elevator car to accommodate an ambulance stretcher.  Where elevators are provided in buildings four or more stories above, or four or more stories below, grade plane, or where the rise exceeds 25 feet, at least one elevator shall be provided for Any building that is more than three stories high or in which the vertical distance between the bottom terminal landing and the top terminal landing exceeds 25 feet,must be constructed to contain at least one passenger elevator that is operational for building occupants and fire department emergency access to all floors.  The elevator car shall be of such a size and arrangement to accommodate an ambulance stretcher 24-inches by 76-inches (610 mm by 1950 mm) with not less than 5-inch radius corners in the horizontal, open position and shall be identified by the international symbol for emergency medical services (star of life). The symbol shall not be less than 3 inches (76 mm) high and shall be placed inside on both sides of the hoistway door frame.

[SP4597]

3002.9  Add to read as shown.

3002.9 Automatic fire alarm initiating devices shall be located and installed in accordance with ASME A 17.1 and NFPA 72.

Section 3004 Hoistway Venting

3004.3.1 Reduced vent area. Change to read as shown.

3004.3.1 Reduced vent area. Where mechanical ventilation conforming to the International Florida Building Code, Mechanical Code is provided, a reduction in the required vent area is allowed provided that all of the following conditions are met:

1. The occupancy is not in Group R-1, R-2, I-1 or I-2 or of a similar occupancy with overnight sleeping units.

2. The vents required by Section 3004.2 do not have outside exposure.

3. The hoistway does not extend to the top of the building.

4. The hoistway and machine room exhaust fan is automatically reactivated by thermostatic means.

5. Equivalent venting of the hoistway is accomplished.

[3463]

Section 3005 Conveying Systems

3005.4 Personnel and material hoists.  Change to read as shown.

3005.4 Personnel and material hoists. Personnel and material hoists shall be designed utilizing an approved method that accounts for the conditions imposed during the intended operation of the hoist device. The design shall include, but is not limited to, anticipated loads, structural stability, impact, vibration, and stresses and seismic restraint. The design shall account for the construction, installation, operation and inspection of the hoist tower, car, machinery and control equipment, guide members and hoisting mechanism. Additionally, the design of personnel hoists shall include provisions for field testing and maintenance which will demonstrate that the hoist device functions in accordance with the design. Field tests shall be conducted upon the completion of an installation or following a major alteration of a personnel hoist.

[3466]

Section 3008 Occupant Evacuation Elevators

3008.2 Fire safety and evacuation plan. The building shall have an approved fire safety and evacuation plan in accordance with the applicable requirements of Section 404 of the International Florida Fire Prevention Code. The fire safety and evacuation plan shall incorporate specific procedures for the occupants using evacuation elevators.

[3471]

Section 3009 Elevator Accessibilty Requirments for the Physically Handicapped.  Add to read as shown.

SECTION 3009

ELEVATOR ACCESSIBILITY REQUIREMENTS FOR THE PHYSICALLY HANDICAPPED

1.3009.1             In a building having any elevators that do not provide access to every floor level, elevator hallway call buttons on all main levels of ingress and on any floor that is commonly served by more than one group of elevators must be marked with Arabic and braille symbols that indicate floor levels to which access is provided. The symbols must be placed directly above each call button.

2.3009.2             Each elevator car interior must have a support rail on at least one wall. All support rails must be smooth and have no sharp edges and must not be more than 1½ inches (38 mm) thick or 2½ inches (63 mm) in diameter. Support rails must be continuous and a minimum length of 42 inches (1067 mm) overall.

The inside surface of support rails must be 1½ inches (38 mm) clear of the car wall. The distance from the top of the support rail to the finished car floor must be at least 31 inches (787 mm) and not more than 33 inches (838 mm). Padded or tufted material or decorative materials such as wallpaper, vinyl, cloth or the like may be not be used on support rails.

1.3009.3         A bench or seat may be installed on the rear wall of the elevator car enclosure, if the bench or seat does not protrude beyond the vertical plane of the elevator car enclosure wall when folded into a recess provided for the bench or seat and, when not in use, the bench or seat automatically folds into the recess. The bench or seat must be capable of supporting a live load of at least 250 pounds (113.4 kg) on any 12-inch by 12-inch (305 mm by 305 mm) area. A padded, tufted or other decorative material may not be used to cover the bench or seat; or may the bench or seat encroach on the minimum clear inside-car dimensions specified in this section.

This section applies only to elevators available for the transportation of the public. This section does not apply to elevators restricted by key or similar device to a limited number of persons in a building that has an elevator that otherwise meets the requirements of this section or to elevators used only for the transportation of freight. However, elevators that are used as freight and passenger elevators for the public and employees must comply with this section. This section does not apply to dumbwaiters or escalators.

This section supersedes all other state regulations and local ordinances and rules affecting the accessibility of passenger elevators to the physically handicapped, and the standards established by this section may not be modified by municipal or county ordinance.

[3472]

Section 3010 Serial Numbers.  Add to read as shown.

SECTION 3010 SERIAL NUMBERS

3010.1 Serial numbers. Each elevator shall have a serial number assigned by the division or authority having jurisdiction  painted on or  attached to the elevator car in plain view and also to the driving mechanism. This serial number shall be shown on all required certificates and permits.

3010.1.1.   Certificates of operation must be posted in a conspicuous location in the elevator and shall contain the text of Section 823.12, Florida Statutes relating to the prohibition against smoking in elevators. The certificate must be framed with a transparent cover.

3010.1.2.         In addition to Item 3, t The designation “NO SMOKING” along with the international symbol for no smoking shall be conspicuously displayed within the interior of the elevator in the plain view of the public.

3010.1.3.         The following ASME A17.1, rule is hereby amended to read as follows:

a.          Rule 2.29.1 amend to add the following to the rule: "Each car in a multicar group shall be sequentially identified from left to right, as viewed from the elevator lobby."

b.         Rule 2.7.3.1 of the ASME A17.1, which is amended to read as follows: “Rule 2.7.3.1 General Requirements. A permanent, safe and convenient means of access to elevator machine rooms and overhead machinery spaces shall be provided for authorized persons. The key to the machine rooms and overhead machinery spaces shall be kept on the premises at all times and readily available for use by State of Florida certified Elevator Inspectors.”

c.           Rule 3.11.3 of ASME A17.3 is amended to read as follows:

NOTE: Updates to the Safety Code for Existing Elevators and Escalators ASME A17.1 and ASME A17.3 which require Phase II Firefighters’ Service shall apply except where section 399.02(9) Florida Statute states Phase II Firefighters' Service on elevators may not be enforced until July 1, 2015, or until the elevator is replaced or requires major modification, whichever occurs first, on elevators in condominiums or multifamily residential buildings, including those that are part of a continuing care facility licensed under chapter 651, or similar retirement community with apartments, having a certificate of occupancy by the local building authority that was issued before July 1, 2008. This exception does not prevent an elevator owner from requesting a variance from the applicable codes before or after July 1, 2015. This subsection does not prohibit the division from granting variances pursuant to s. 120.542, Florida Statute. (A1)

[3473 A6]

c.	Rule 2.27.8 Switch Keys, of ASME A17.1, is amended to read as follows: “The switches required by Rule 211.2 through 211.5, for all elevators in a building, must be operable by the same keys. This key must not be part of a building master key system. There must be a key for the designated level switch and for each elevator in the group. These keys must be kept on the premises at all times in a location readily accessible to authorized personnel, and state elevator inspectors, but not where the key is available to the general public. NOTE: (RULE 2.27.8): Local authorities may specify a uniform keyed lock box to contain the necessary keys.”

d.	Rule 6.1.6.1 Starting Switch of ASME A17.1, is amended to read as follows: “Starting switches must be of the key-operated type and must be located so that the escalator steps are within sight. Automatic starting by any means is prohibited. The key for the starting switches must be kept on the premises at all times in a location readily available to authorized personnel and state elevator inspectors, but not where the key is available to the general public.”

e.	Rule 2.2.2.4 Drains connected directly to sewers shall not be installed in elevator pits. Where drains are not provided to prevent the accumulation of water, a sump of adequate size and depth to accommodate a pump shall be provided, with or without a pump.

Section 3011  Electrolysis Protection for Underground Hydraulic elevator Cylinders.  Add to read as shown.

SECTION 3011 ELECTROLYSIS PROTECTION FOR UNDERGROUND HYDRAULIC ELEVATOR CYLINDERS

3011.1 Electrolysis protection for underground hydraulic elevator cylinders. All newly installed underground hydraulic pressure cylinders shall be encased in outer plastic containment to minimize electrolytic corrosion between the metal cylinder and ground cathode. 1.3011.1.1 The plastic casing shall be capped at the bottom, and all joints must be solvent or heat welded to ensure water tightness. 2.3011.1.2 The plastic casing shall be constructed of polyethylene or polyvinyl chloride (PVC). The plastic pipe wall thickness must not be less than 0.125 inch (3.175 mm). 3.3011.1.3 The neck of the plastic casing shall have a means of inspection provided to monitor the annulus between the pressurized hydraulic cylinder and the protective plastic casing. 4.3011.1.4 Replacements of existing hydraulic cylinders shall be protected by the aforementioned method where existing physical dimensions permit. (3476 A1)

Section 3012 Bulletin Boards.  Add to read as shown.

SECTION 3012 BULLETIN BOARDS

3012.1 Bulletin boards.

1.3012.1.1          Bulletin boards and frames used in elevator cars shall not create any conditions which will be unsafe for users of the elevator car. Users shall include:

a.   Disabled persons;

b.   Persons confined to wheelchairs; and

c.   All other persons who may operate the elevator car in its normal course of use.

2.3012.1.2          Bulletin boards shall not protrude more than 1 inch (25.4 mm) beyond the vertical line of the car wall. They shall not encroach on any clearances required to be maintained in the elevator by Chapter 399, Florida Statutes, and ASME A17.1.

3.3012.1.3          Bulletin boards shall be framed and all edges must be smooth and rounded. No sharp edges of any kind shall protrude.

4.3012.1.4          A glass or plastic cover shall be provided. Glass, if used, must meet the following requirements:

a.   Be laminated;

b.   Meet the requirement for laminated glass as set forth in ANSI Z97.1;

c.   The cover shall be securely held in place by the frame.

5.3012.1.5          The frame and bulletin board shall be permanently fastened to the car wall in such a manner so that all parts including the cover in place will withstand any and all tests required of the elevator.

6.3012.1.6          All materials used shall be fire resistive equal to the requirements of the cab enclosure.

7.3012.1.7          The bottom of the bulletin boards shall not be less than 5 feet (1524 mm) above the cab floor, and the total area shall not exceed 4 square feet (0.37 m2).

[3477]

Section 3013 Alterations to Electric and Hydraulic Elevators and Escalators.  Add to read as shown.

SECTION 3013 ALTERATIONS TO ELECTRIC AND HYDRAULIC ELEVATORS AND ESCALATORS

3013.1 Alterations to electric and hydraulic elevators and escalators.

1.	In addition to the alterations set forth in Rule 8.10.3.3.2 and Rule 8.10.2.3.2 ASME A17.1, the following alterations require, in addition to a construction permit, that inspections and tests be performed to determine conformance with ASME A17.1, rules cited below:

| ALTERATIONS | Electric Elevators | Hydraulic Elevators |
| --- | --- | --- |
| (a) Addition of elevator to existing hoistway (new installation) | 8.7.2.1.2 | 8.7.2.1.2 |
| (b) Brake (replacements of existing drive, machine brake by a new brake) | 2.24 | — |
| (c) Buffer (addition of oil buffer) | 8.7.2.23 | 8.7.2.27 |
| (d) Driving machine (replacement of) | 8.7.2.25.1 | 8.7.3.23 |
| (e) Freight elevator converted to passenger service | 8.7.2.16.1 | 8.7.3.27 |
| (f) Rope, replacement in size or number of ropes | 8.6.2.5 | 8.6.2.5 |
| (g) Sheave, driving machine (replacement in size) | 8.7.2.25.1 | 8.7.2.25.1 |

- The following alterations require, in addition to a construction permit, that inspections be performed to determine conformance with ASME A17.1, rule cited below:

| ALTERATIONS | Electric Elevators | Hydraulic Elevators |
| --- | --- | --- |
| (a) Access Switch (addition of) (b) Automatic transfer device (addition of) (c) Car, door or gate (addition of car door or gate electric contacts) | 8.7.2.11.4, 8.7.7.2 8.7.2.14 | 8.7.3.11, 8.7.7.2 8.7.3.13 |
| (d) Car enclosure | 8.7.2.14 | 8.7.3.13 |
| (e) Car leveling device (addition of) and (trucking device) | 8.7.2.27.2 | 8.7.3.31.2 |
| (f) Control | 8.7.2.27.5 | 8.7.3.31.6 |
| (g) Control equipment | 8.7.2.27 | 8.7.3.31 |
| (h) Controller (existing controller w/new) (excluding dispatching device) (i) Counterweight (change of) | 8.7.2.27.4 8.7.3.23 | 8.7.3.31.5 8.7.3.26 |
| (j) Increase in travel (or decrease) | 8.7.2.17.1 | 8.7.3.22.1 |
| (k) Door, hoistway (replacement of all hoistway doors) | 8.7.2.10 | 8.7.3.10 |
| (l) Escalator, relocation of | 8.7.6.1 | — |
| (m) Escalator, skirt (switches addition of safety device) | 6.1.6 | — |
| (n) Freight elevator permitted to carry passengers | 8.7.2.16.3 | 8.7.3.19 |
| (o) Guide rails (change in type or size) | 8.7.2.24 | 8.7.3.28 |
| (p) Hoistway door, power operation of (addition of) | 8.7.2.12 | 8.7.3.12 |
| (q) Hoistway door locking device (addition of) | 8.7.2.11 | 8.7.3.11 |
| (r) Operation, change in type of | 8.7.2.27.6 | 8.7.3.31.7 |
| (s) Platform, car (complete replacement of) | 8.7.2.15.1 | 8.7.3.14 |
| (t) Roller guide shoe, counter-weight and car (addition of) | 8.7.2.22 | 8.7.2.22 |
| (u) Rope equalizer (addition of) | 8.7.2.21.2 | 8.7.3.25.2 |
| (v) Rope fastening device, auxiliary (addition of) | 8.7.2.21.3 | 8.7.2.21.3 |
| (w) Tank (replacement of) (with different capacity) | — | 8.7.3.29 |
| (x) Top of car operating device (addition of) | 8.7.2.27.1 | 8.7.3.31.1 |

Alterations set forth in Part 8, ASME A17.1 to include any change to equipment, including its parts, components, and/or subsystems, other than maintenance, repair, or replacement; require an elevator construction permit, along with documented performance of inspections and tests to determine conformance with ASME A17.1.  A repair or replacement of equipment, parts, components or subsystems that requires inspection, tests and independent witnessing in other sections of ASME A17.1,  A17.3  and A18.1 shall also require an elevator construction permit, in accordance with Section 105, Florida Building Code, Building.

[SP4608]

[3861]

Chapter 31 Special Construction

Section 3102 Membrane Structures

3102.1 General.  Change to read as shown.

3102.1 General.  The provisions of this section shall apply to air-supported, air-inflated, membrane-covered cable and membrane-covered frame structures, collectively known as membrane structures, erected for a period of 180 days or longer. Those erected for a shorter period of time shall comply with the Florida Fire Prevention Code. Membrane structures covering water storage facilities, water clarifiers, water treatment plants, sewage treatment plants, greenhouses and similar facilities not used for human occupancy, are required to meet only the requirements of Sections 3102.3.1 and 3102.7.  Membrane structures erected on a building, balcony, deck or other structure for any period of time shall comply with this section.

3102.7 Engineering design.  Change to read as shown.

3102.7 Engineering design. The structure shall be designed and constructed to sustain dead loads; loads due to tension or inflation; and live loads including wind, snow or flood and seismic loads and floodand in accordance with Chapter 16.

[S4513]

Section 3103 Temporary Structures

3103.1 General.  Change to read as shown.

- 3103.1 General.  The provisions of this section shall apply to structures erected for a period of less than 180 days. Tents and other membrane structures erected for a period of less than 180 days shall comply with the Florida Fire Prevention Code. Those erected for a longer period of time shall comply with applicable sections of this code.

Exception: Provisions of the Florida Fire Prevention Code shall apply to tents and membrane structures erected for a period of less than 180 days.

Section 3105 Awnings and Canopies

3105.1 Change to read as shown.

- 3105.1 Fabric awnings and fabric-covered frames.  Fabric awnings and fabric-covered frames shall comply with the provisions of Section 3105 as applicable.

3105.1 General. Awnings or canopies shall comply with the requirements of this section and other applicable sections of this code.  [3961]  Note: same as the I-Code.

- 3105.1.1 Location.  Add to read as shown.

- 3105.1.1 Location.

- 3105.1.1.1  Add to read as shown.

- 3105.1.1.1  Fabric awnings and fabric-covered frames located over public property or in areas accessible to the general public shall be constructed so that no rigid part of such fabric awnings or fabric-covered frames shall be less than 7 feet, 6 inches (2286 mm) from the grade directly below, and no part of the cloth drop shall be less than 7 feet (2134 mm).

- 3105.1.1.2  Add to read as shown.

- 3105.1.1.2  A fixed fabric awning or fabric-covered frame shall not extend over public property more than two-thirds the distance from the property line to the nearest curb line in front of the building site as measured from the exterior face of the building nor shall any portion be closer than 18 inches (457 mm) to the curb line.

- Exceptions:

- 1.	If installed over 14 feet (4267 mm) in height, it may occupy the entire width of the sidewalk.

- 2.	Unless otherwise regulated by local zoning requirements.

- 3105.1.1.3  Add to read as shown.

- 3105.1.1.3  Fabric-covered framework in whole or in part of fabric, erected in connection with gasoline service stations may not be erected within 15 feet (4572 mm) of where flammable liquids are transferred.

- 3105.1.1.4  Add to read as shown.

- 3105.1.1.4  Movable fabric awnings or fabric covered frames may extend over public property for a distance of not more than 5 feet (1524 mm), provided such awnings or any part thereof maintain a clear height of 8 feet  (2438 mm) above the  sidewalk.  All such movable awnings shall be supported on metal frames attached to the building.

- 3105.1.1.5  Add to read as shown.

3105.1.1.5  Every fabric awning or fabric-covered frame shall be located as not to interfere with the operation of any exterior standpipe, stairway, fire escape or any means of egress to and from the building.

3105.2 Definitions.  Change to add as shown.

- 3105.2 Area.  No fabric awning or fabric-covered frame shall exceed the area of the building to which it is attached.

- 3105.3  Change to read as shown.

- 3105.3 Material.

Section 3105.3.1, add text to read as follows:

3105.3.1 Fabric used for awnings or fabric-covered frames shall meet the flame propagation performance criteria of NFPA 701.

Exception: Awnings or fabric-covered frames used in conjunction with Group R-3 occupancies

- 3105.3.2  Add to read as shown.

3105.3.2  Supports for fabric awnings and fabric-covered frame shall be of metal or similar durable material.

3105.4  Add to read as shown.

- 3105.4 Design.

3105.4.1  Add to read as shown.

- 3105.4.1  Design of the framing members shall not be based on removal or repositioning of parts, or the whole, during periods of 75 mph wind velocity.

3105.4.2  Add to read as shown.

- 3105.4.2  Design of the structural framing members shall be based on rational analysis, using the applicable wind loads of Chapter 16 as shown below:

3105.4.2.1  Add to read as shown.

- 3105.4.2.1  The wind design loads for any fabric or membrane-covered structure designed with a quick removal or breakaway membrane or fabric at wind velocities of 75 mph, shall be based on the following criteria:

- 1.	Minimum wind speed velocity of 3-second wind gust 10590 mph

- 2.	Importance factor based on low hazard to human life of 0.77.

- 23.	Exposure Category B for or C, or D as defined in Chapter 16.

3105.4.2.2  Add to read as shown.

- 3105.4.2.2  The wind design loads for any fabric or membrane covered structure designed with a permanent or nonremovable fabric or membrane, shall be based on the following criteria:

1.	Minimum wind speed  velocity as required in Chapter 16 using Figure 1609C..

- .

      - Importance factor based on low hazard to human life of 0

2. Exposure B, C or D as defined in Chapter 16.

3105.4.3  Add to read as shown.

- 3105.4.3  The fabric portions of awnings fabric covered frames shall be securely laced, tied or otherwise fastened to the frame; no rafter or front bar will be permitted in pockets; and in no case shall a rolling curtain be caused to operate over a canopy frame.

3105.4.4  Add to read as shown.

3105.4.4  The horizontal projection of cantilevered portions shall not be greater than two times the height, except where the building construction does not permit a proper installation; in which case, variance may be permitted by the building official, based on special design and construction.

3105.5 Rigid awnings and canopy shutters.  Add to read as shown.

- 3105.5 Rigid awnings and canopy shutters.

3105.5.1 Loads  Add to read as shown.

- 3105.5.1 Loads.  Rigid awnings and canopy shutters shall be designed to resist the loads set forth in Chapter 16 of this Code except that structures or parts thereof which are intended to be removed or repositioned during periods of high wind velocity shall be designed in their open or extended position to design pressures based on a basic wind speed of minimum 11590 mph, 3-second wind gust with applicable shape factors and to resist not less than 10 psf (478 Pa) roof live load.

[S4710]

3105.5.2  Add to read as shown.

- 3105.5.2  Where such structure is intended to be folded or otherwise repositioned to close an opening when the building is unattended or act as a storm shutter the design in the closed position shall also comply with Chapter 16 and shall be impact resistant in accordance with Section1609.1.4.

3105.5.3  Add to read as shown.

3105.5.3  Structures designed to be readily removed or repositioned during periods of high wind velocity shall be posted with a legible and readily visible decal or painted instructions to the owner or tenant to remove or reposition the structure or part thereof during such periods of time as are designated by the U.S. Weather Bureau as being a hurricane warning or alert.

Section 3109 Add to read as shown.

SECTION 3109 STRUCTURES SEAWARD OF A COASTAL CONSTRUCTION CONTROL LINE

301.9.1 General.  Add to read as shown.

3109.1 General.

3109.1.1 Scope.  Add to read as shown.

3109.1.1 Scope. The provisions of Section 3109 shall ensure that structures located seaward of the coastal construction control line are designed to resist the predicted forces associated with a 100-year storm event and shall apply to the following:

1.   All habitable structures which extend wholly or partially seaward of a coastal construction control line (CCCL) or 50-foot (15.3 m) setback line.

2.   Substantial improvement of or additions to existing habitable structures.

3.        Swimming pools that are located in close proximity to a habitable structure or armoring. An environmental permit from the Florida Department of Environmental Protection, requiring special siting considerations to protect the beach-dune system, proposed or existing structures and public beach access, is required prior to the start of construction. The environmental permit may condition the nature, timing and sequence of construction of permitted activities to provide protection to nesting sea turtles and hatchlings and their habitat, including review, submittal and approval of lighting plans.

Exception: The standards for buildings seaward of a CCCL area do not apply to any modification, maintenance or repair to any existing structure within the limits of the existing foundation which does not require, involve or include any additions to, or repair or modification of, the existing foundation of that structure.

Exception: The standards for buildings seaward of a CCCL area do not apply to any modification, maintenance or repair of any existing structure within the limits of the existing foundation which does not require, involve or include any additions to, or repair or modification of, the existing foundation of that structure, except for substantial improvement of or additions to existing habitable structures.

An environmental permit from the Florida Department of Environmental Protection, requiring special siting considerations to protect the beach-dune system, proposed or existing structures and public beach access, is required prior to the start of construction. The environmental permit may condition the nature, timing and sequence of construction of permitted activities to provide protection to nesting sea turtles and hatchlings and their habitat, including review, submittal and approval of lighting plans.

Comment after Glitch

[4203]

3109.1.2 Certification.  Add to read as shown.

3109.1.2 Certification.  As part of the permit process and upon placement of the lowest horizontal structural member, the applicant shall submit to the building official certification of the elevation of the lowest horizontal structural member of the lowest floor as built in relation to National Geodetic Vertical Datum (N.G.V.D.). Said certification shall be prepared by or under the direct supervision of a registered land surveyor or professional engineer or architect and certified by same and be submitted prior to commencing any addition work. Any work undertaken prior to submission of the certification shall be at the applicant’s risk. The building official shall review the submitted elevation data, and any deficiencies found shall be corrected by the permit holder immediately and prior to any further work being permitted to proceed.

3109.2 Definitions.  Add to read as shown.

3109.2 Definitions.

ARMORING. A manmade structure designed to either prevent erosion of the upland property or protect upland structures from the effects of coastal wave and current action. Armoring includes certain rigid coastal structures such as geotextile bags or tubes, seawalls, revetments, bulkheads, retaining wall or similar structures, but does not include jetties, groins or other construction whose purpose is to add sand to the beach and dune system, alter the natural coastal currents or stabilize the mouths of inlets.

BREAKAWAY WALL. A partition independent of supporting structural members that is intended to withstand design wind forces but to collapse from a water load less than that which would occur during a 100 year storm event without causing collapse, displacement or other structural damage to the elevated portion of the building or supporting foundation system.

COASTAL CONSTRUCTION CONTROL LINE. The line established by the State of Florida pursuant to Section161.053, Florida Statutes, and recorded in the official records of the county which defines that portion of the beach-dune system subject to severe fluctuations based on a 100-year storm surge, storm waves or other predictable weather conditions.

DESIGN GRADE. The predicted eroded grade caused by the 100-year storm.

FIFTY-FOOT SETBACK LINE. A line of jurisdiction, established pursuant to the provisions of Section161.052, Florida Statutes, in which construction is prohibited within 50 feet  (15.13 m) of the line of mean high water at any riparian coastal location fronting the Gulf of Mexico or the Atlantic coast shoreline.

HABITABLE STRUCTURE. Structures designed primarily for human occupancy and are potential locations for shelter from storms. Typically included within this category are residences, hotels and restaurants.

LOWEST HORIZONTAL STRUCTURE MEMBER. Any shore-parallel structural member which supports floor, wall or column loads and transmits them to the pile foundation.

ONE-HUNDRED-YEAR STORM ELEVATION. The height of the breaking wave crest or wave approach as superimposed on the storm surge with dynamic wave set-up of a 100-year storm. This 100-year storm elevation is determined by the Florida Department of Environmental Protection based on studies published as part of the coastal construction control line establishment process and an analysis of topographic and other site specific data.

REBUILDING. See definition of “Substantial improvement.”

SUBSTANTIAL IMPROVEMENT. See definition in Section 161.54(12), Florida Statutes. See Section 1612. [4234]

3109.3 Elevation standards.  Add to read as shown.

3109.3 Elevation standards.  All habitable structures shall be elevated at or above an elevation which places the lowest horizontal structural member above the 100-year storm elevation as determined by the Florida Department of Environmental Protection in the report titled “One-Hundred-Year Storm Elevation Requirements for Habitable Structures Located Seaward of a Coastal Construction Control Line.”

An applicant may request the Department of Environmental Protection to determine a site-specific 100-year storm elevation for the applicant’s proposed habitable structure as part of the environmental permit application process. The elevation will be provided as part of the applicant’s environmental permit and shall be subject to review under the provisions of Chapter 120, Florida Statutes.

Exceptions:

1.	Additions, repairs or modifications to existing nonconforming habitable structures that do not advance the seaward limits of the existing habitable structure and do not constitute rebuilding of the existing structure.

2.	Habitable structures located landward of existing armoring which is capable of protecting buildings from the effects of erosion from a 100-year storm surge. The applicant shall provide scientific and engineering evidence that the armoring has been designed, constructed and maintained to survive the effects of the design storm and provide protection to existing and proposed structures from the erosion associated with that event. Evidence shall include a report with data and supporting analysis, and shall be certified by a professional engineer registered in this state, that the armoring was designed and constructed and is in adequate condition to meet the following criteria:

a.	The top must be at or above the still water level, including setup, for the design storm plus the breaking wave calculated at its highest achievable level based on the maximum eroded beach profile and highest surge level combination, and must be high enough to preclude runup overtopping.

b.	The armoring must be stable under the design storm including maximum localized scour, with adequate penetration and toe protection to avoid settlement, toe failure, or loss of material from beneath or behind the armoring.

c.	The armoring must have sufficient continuity or return walls to prevent flanking under the design storm from impacting the proposed construction.

d.	The armoring must withstand the static and hydrodynamic forces of the design storm.

3.	A higher elevation standard is required by either the National Flood Insurance Program (NFIP), as found on a community’s Flood Insurance Rate Map (FIRM), or the local flood damage prevention ordinance. In such instances, the higher elevation standard shall apply.

3109.4 Construction standards.  Add to read as shown.

3109.4 Construction standards.

3109.4.1 Pile foundations.  Add to read as shown.

3109.4.1 Pile foundations.  All habitable structures shall be elevated on, and securely anchored to, an adequate pile foundation. Pile foundations for habitable structures shall be designed to withstand all reasonable anticipated erosion, scour and loads resulting from a 100-year storm including wind, wave, hydrostatic and hydrodynamic forces acting simultaneously with typical structural (live and dead) loads. All habitable structures should be anchored to their pile foundation in such a manner as to prevent flotation, collapse or lateral displacement. The elevation of the soil surface to be used in the calculation of pile reactions and bearing capacities for habitable structures shall not be greater than that which would result from erosion caused by a 100-year storm event. Calculation of the design grade shall account for localized scour resulting from the presence of structural components. Design ratio or pile spacing to pile diameter should not be less than 8:1 for individual piles located above the design grade. Pile caps shall be set below the design grade unless designed to resist increased flood loads associated with setting the cap above the design grade, but at or below the natural grade. Pile penetration shall take into consideration the anticipated loss of soil above the design grade.

Exceptions:

1.	Additions, repairs or modifications to existing nonconforming habitable structures that do not advance the seaward limits of the existing habitable structure and do not constitute rebuilding of the existing structure.

2.	Habitable structures located landward of existing armoring which is capable of protecting buildings from the effects of erosion from a 100-year storm surge. The applicant shall provide scientific and engineering evidence that the armoring has been designed, constructed and maintained to survive the effects of the design storm and provide protection to existing and proposed structures from the erosion associated with that event. Evidence shall include a report with data and supporting analysis, and shall be certified by a professional engineer registered in this state, that the armoring was designed and constructed and is in adequate condition to meet the following criteria:

a.	The top must be at or above the still water level, including setup, for the design storm plus the breaking wave calculated at its highest achievable level based on the maximum eroded beach profile and highest surge level combination, and must be high enough to preclude runup overtopping.

b.	The armoring must be stable under the design storm including maximum localized scour, with adequate penetration and toe protection to avoid settlement, toe failure or loss of material from beneath or behind the armoring.

c.	The armoring must have sufficient continuity or return walls to prevent flanking under the design storm from impacting the proposed construction.

d.	The armoring must withstand the static and hydrodynamic forces of the design storm.

3109.4.2 Walls below the 100-year storm elevation.  Add to read as shown.

3109.4.2 Walls below the 100-year storm elevation.  No substantial walls or partitions shall be constructed below the level of the first finished floor of habitable structures. All other walls shall be designed to break away.

Exceptions:

1.	Stairways and stairwells;

2.	Shear walls perpendicular to the shoreline;

3.	Shear walls parallel to the shoreline, which are limited to a maximum of 20 percent of the building length in the direction running parallel to the shore;

4.	Shear walls parallel to the shoreline, which exceed 20 percent of the total building length (including any attached major structure) when they meet the following criteria:

a.	A certification is provided by a Florida-registered professional engineer that certifies that the increased length of shear walls, over 20 percent, are located landward of the 100-year erosion limit;

b.	A hydraulic analysis is provided and certified by a Florida-registered professional engineer that evaluates the potential impact of flow increase on the subject parcel and adjacent properties;

c.	The hydraulic analysis demonstrates that although the overall shearwall coverage is more than 20 percent, the increased shearwall length will not result in substantial increase of flow velocities and drag forces on the structural components of the proposed structure and neighboring structures; and

d.	The provisions under Section 3109.4.2 (Exception 4) do not include any low-rise building as defined in Section 1609.2.

5.	Wind or sand screens constructed of fiber or wire mesh;

6.	Light, open lattice partitions with individual, wooden lattice strips not greater than 3/4 inch (19 mm) thick and 3 inches (76 mm) wide;

7.	Elevator shafts;

8.	Small mechanical and electrical rooms; and

9.	Break-away or frangible walls.

3109.5 Flood loads during a 100-year storm.  Add to read as shown.

3109.5 Flood loads during a 100-year storm.

3109.5.1 Load basis.  Add to read as shown.

3109.5.1 Load basis.  The structural design shall be based on the 100-year storm as determined by the Florida Department of Environmental Protection in studies published as part of the coastal construction control line establishment process. Breaking, broken and nonbreaking waves shall be considered as applicable. Design wave loading analysis shall consider vertical uplift pressures and all lateral pressures to include impact, as well as dynamic loading and the harmonic intensification resulting from repetitive waves.

3109.5.2 Hydrostatic load.  Add to read as shown.

3109.5.2 Hydrostatic load.  Habitable structures shall be designed in consideration of the hydrostatic loads which would be expected under the conditions of maximum inundation associated with a 100-year storm event. Calculations for hydrostatic loads shall consider the maximum water pressure resulting from a fully peaked, breaking wave superimposed on the design storm surge with dynamic wave setup. Both free and confined hydrostatic loads shall be considered. Hydrostatic loads which are confined shall be determined using the maximum elevation to which the confined water would freely rise if unconfined. Vertical hydrostatic loads shall be considered as forces acting both vertically downward and upward on horizontal or inclined surfaces of major structures (e.g., floors, slabs, roofs, walls). Lateral hydrostatic loads shall be considered as forces acting horizontally above and below grade on vertical or inclined surfaces of major structures and coastal or shore protection structures. Hydrostatic loads on irregular or curving geometric surfaces may be determined in consideration of separate vertical and horizontal components acting simultaneously under the distribution of the hydrostatic pressures.

3109.5.3 Hydrodynamic loads.  Add to read as shown.

3109.5.3 Hydrodynamic loads.  Habitable structures shall be designed in consideration of the hydrodynamic loads which would be expected under the conditions of a 100-year storm event. Calculations for hydrodynamic loads shall consider the maximum water pressures resulting from the motion of the water mass associated with a 100-year storm event. Full-intensity loading shall be applied on all structural surfaces above the design grade which would affect the flow velocities.

3109.6 Wind loads.  Add to read as shown.

3109.6 Wind loads.  All habitable structures shall be designed in accordance with Chapter 16.

3109.7 Swimming pools.  Add to read as shown.

3109.7 Swimming pools.  Swimming pools located in close proximity to an existing habitable structure or armoring shall be designed with an adequate pile foundation for the erosion and scour conditions of a 100-year storm event.

3109.8 Storm debris.  Add to read as shown.

3109.8 Storm debris.  All structures will be designed to minimize the potential for wind and water-borne debris during a storm.

Section 3111 Deposit of Materials in Tidewater Regulated.  Add to read as shown.

SECTION 3111 DEPOSIT OF MATERIAL IN TIDEWATER REGULATED

3111.1  It is not lawful for any person to discharge or cause to be discharged or deposit or cause to be deposited, in the tide or salt waters of any bay, port, harbor or river of this state, any ballast or material of any kind other than clear stone or rock, free from gravel or pebbles, which said clear stone or rock shall be deposited or discharged only in the construction of enclosures in connection with wharves, piers, quays, jetties or in the construction of permanent bulkheads connecting the solid and permanent portion of wharves. It is lawful to construct three characters of bulkheads for retention of material in solid wharves.

First, clear stone or rock enclosures, or bulkheads, may be built upon all sides to a height not less than 2½ feet (762 mm) above high watermark; and after the enclosures have been made so solid, tight and permanent as to prevent any sand, mud, gravel or other material that may be discharged or deposited in them from drifting or escaping through such enclosures, any kind of ballast may be discharged or deposited within the enclosures. The enclosures may be constructed of wood, stone and rock combined, the stone and rocks to be placed on the outside of the wood to a height not less at any point than 2½ feet (762 mm) above high watermark; and after the enclosures have been made so solid, tight and permanent as to prevent any sand, mud gravel or other material that may be discharged or deposited in them from drifting or escaping through such enclosures, any kind of ballast may be discharged or deposited within the enclosures.

Second, a bulkhead may be built by a permanent wharf consisting of thoroughly creosoted piles not less than 12 inches (305 mm) in diameter at the butt end, to be driven close together and to be capped with timber not less than 10 or 14 inches drift (254 or 302 mm), bolted to each pile, and one or more longitudinal stringers to be placed on the outside of the bulkhead and securely anchored by means of iron rods to piles driven within the bulkheads, clear rock to be on the inside of the bulkhead, to a height of not less than 2½ feet (762 mm) above high water; and after this is done, ballast or other material may be deposited within the permanent enclosure so constructed.

Third, a bulkhead may be constructed to consist of creosoted piles, as described herein, driven not exceeding 4 feet (1219 mm) apart from center to center, inside of which two or more longitudinal stringers may be placed and securely bolted to the piles. Inside of these longitudinal pieces, two thicknesses of creosoted sheet piling are to be driven, each course of the sheet piling to make a joint with the other to form an impenetrable wharf; and within this permanent bulkhead so constructed, any ballast or other material may be deposited.

No such enclosure, pier, quay or jetty shall be begun until the point whereat it is to be built shall have been connected by a substantial wharf with a shore or with a permanent wharf; except that the owners of wharves may at any time, with the consent of the Board of Pilot Commissioners of the Division of Professions of the Department of Business and Professional Regulation, build wharves of clear stone or rock, or creosoted walls as hereinafter provided, on each side of their wharves from the shore to a point at which the water is not more than 15 feet (4.6 m) deep, and when such walls have attained a height of 2½ feet (762 mm) above high watermark and have been securely closed at the deepwater end by stone or creosoted walls of the same height, any kind of ballast may be deposited in them.

Nothing contained in this section shall interfere with any rights or privileges now enjoyed by riparian owners. While this section empowers those who desire to construct the several characters of wharves, piers, quays, jetties and bulkheads provided for and described herein, nothing in this section shall be so construed as to require any person not desiring to construct a permanent wharf by filling up with ballast, stone or other material to construct under the specifications contained herein; and nothing in this chapter shall be so construed as to prevent any person from constructing any wharf or placing any pilings, logs or lumber in any waters where the person would have heretofore had the right so to do.

3111.2  Add to read as shown.

3111.2 This section shall not prohibit Escambia County from placing in Pensacola Bay, on the Escambia County side, beside the old Pensacola Bay Bridge, certain materials, as recommended by the Department of Environmental Protection, in coordination with the Fish and Wildlife Conservation Commission, to increase the number of fish available for persons fishing from the old Pensacola Bay Bridge.

3111.3  Add to read as shown.

3111.3 This section shall not prohibit Manatee County from placing in the Manatee County portions of Sarasota Bay and Tampa Bay and in the Manatee River, certain materials, as recommended by the Department of Environmental Protection, in coordination with the Fish and Wildlife Conservation Commission, to increase the number of fish available for persons fishing in the above areas.

3111.4  Add to read as shown.

3111.4 This section shall not prohibit Pinellas County from placing in Tampa Bay certain materials as recommended by the Department of Environmental Protection, in coordination with the Fish and Wildlife Conservation Commission, to increase the number of fish available for persons fishing in the bay. Deposit of material on a wharf or quay is regulated. It is not lawful for any person to deposit or cause to be deposited on any wharf or quay, any ballast, stone, earth or like material, except such wharf or quay may be so secured as to prevent such ballast or other material from washing into the waters of the harbor.

Section 3112 Lighting, Mirrors, Landscaping.  Add to read as shown.

SECTION 3112 LIGHTING, MIRRORS, LANDSCAPING

3112.1 Add to read as shown.

3112.1 Each operator of an automated teller machine that controls the access area or defined parking area to be lighted shall comply with Sections (2), (3), and (4) no later than one year after October 1, 1994. If the access area or defined parking area to be lighted is controlled by a person other than the operator, such other person shall comply with Sections (2), (3), and (4) no later than one year after October 1, 1994.

3112.2 Add to read as shown.

3112.2 Each operator, or other person responsible for an automated teller machine pursuant to Sections 655.960 through 655.965, shall provide lighting during the hours of darkness with respect to an open and operating automated teller machine and any defined parking area, access area and the exterior of an enclosed automated teller machine installation, as follows:

1.	There shall be a minimum of 10 candlefoot (108 lux) power at the face of the automated teller machine and extending in an unobstructed direction outward 5 feet (1.5 m).

2.	There shall be a minimum of 2 footcandle (21.5 lux) power within 50 feet (15.25 m) in all unobstructed directions from the face of the automated teller machine. If the automated teller machine is located within 10 feet (3 m) of the corner of the building and the automated teller machine is generally accessible from the adjacent side, there shall be a minimum of 2 footcandle (21.5 lux) power along the first 40 unobstructed feet (12 m) of the adjacent side of the building.

3.	There shall be a minimum of 2 footcandle (12.5 lux) power in that portion of the defined parking area within 60 feet (18 m) of the automated teller machine.

4.	The operator shall provide reflective mirrors or surfaces at each automated teller machine which provide the customer with a rear view while the customer is engaged in using the automated teller machine.

5.	The operator, or other person responsible pursuant to Sections 655.960 through 655.965 for an automated teller machine, shall ensure that the height of any landscaping, vegetation or other physical obstructions in the area required to be lighted pursuant to Section (2) for any open and operating automated teller machine shall not exceed 3 feet (914 mm), except that trees trimmed to a height of 10 feet (3 m) and whose diameters are less than 2 feet (610 mm) and manmade physical obstructions required by statute, law, code, ordinance or other governmental regulation shall not be affected by this section.

Section 3113 Airport Noise.  Add to read as shown.

SECTION 3113 AIRPORT NOISE

3113.1 Airport noise study guidelines.   Add to read as shown.

3113.1 Airport noise study guidelines.  The Aviation Safety and Noise Abatement Act of 1979, 14 CFR Part 150 (U.S. Department of Transportation), including revisions through January, 2005, are hereby adopted as a guideline for establishing airport noise control.

3113.1 and R325.1  The Aviation Safety and Noise Abatement Act of 1979 14 CFR Part 150 (US Department of Transportation) including revisions through January 2005 and hereby adopted as a guideline for establishing airport noise control. When required by a local government by local ordinance to providereduce noise attenuation in a new structure or addition to an existing structure near an airport in the area of the local government, the applicant must provide either:

*  a testing certificate from an accredited noise testing lab that a new structure or addition to existing structure built to the submitted engineering plans will achieve an average minimum dBA reduction equal to or greater than the reduction required,

*  an engineering judgement signed and sealed by an engineer licensed in the State of Florida that the structure or addition built to the submitted engineering plans will achieve an average minimum dBA reduction equal to or greater than the reduction required, or

*  plans using the standards contained in "Guidelines for Sound Insulation of Residences Exposed to Aircraft Operations" prepared for the Department of the Navy by Wyle Research and Consulting, Arlington, Virginia, April 2005 on file with the Florida Building Commission.

[3574]

CHAPTER 32 ENCROACHMENTS INTO THE PUBLIC RIGHT-OF-WAY

Section 3202 Encroachments

3202.5 Sidewalk or street obstructions.   Add to read as shown.

3202.5 Sidewalk or street obstructions.   Unless allowed by the applicable governing authority having jurisdiction of the right-of-way or public property, public property shall be maintained clear of any and all obstructions, including among others, posts, columns, display of wares or merchandise and sidewalk signs.

CHAPTER 33 SAFEGUARDS DURING CONSTRUCTION

Section 3304 Site Work

3304.1.4 Fill supporting foundations.  Change to read as shown.

3304.1.4 Fill supporting foundations.  Fill to be used to support the foundations of any building or structure shall comply with Section 18034.5.  Special inspections of compacted fill shall be in accordance with Section 1704.7.[3959]

Section 3305 Sanitary

3305.1 Facilities required.  Change to read as shown.

3305.1 Facilities required.  Sanitary facilities shall be provided during construction, remodeling or demolition activities in accordance with the Florida Building Code, Plumbing.

Section 3309 Fire Extinguishers

3309.2 Fire hazards.  Change to read as shown.

3309.2 Fire hazards.  The provisions of this code and the Florida Fire Prevention Code shall be strictly observed to safeguard against all fire hazards attendant upon construction operations.

Section 3310.1 Stairways required.  Change to read as shown.

3310.1 Stairways required. Where a building has been constructed to a height greater than one story, or where an existing building exceeding one story in height is altered, at least one temporary lighted stairway shall be provided unless one or more of the permanent stairways are erected as the construction progresses.  During construction, the stairway shall be enclosed where the building exterior walls are in place.

Chapter 34 Existing Structures

Section 3401 General

3401.1 Scope.  Change to read as shown.

3401.1 Scope.  Alteration, repair, addition, relocation and change of occupancy of existing structures and buildings shall comply with the provisions of the Florida Existing Building Code.

3401.2 Maintenance.  Change to read as shown.

3401.2 Maintenance.  Reserved

3401.3 Compliance.  Change to read as shown.

3401.3 Compliance.  Reserved.

3401.4 Building materials. Change to read as shown.

3401.4 Building materials.  Reserved.

3401.5 Alternative compliance. Change to read as shown.

3401.5 Alternative compliance.  Reserved.

Section 3402 Definitions.  Change to read as shown.

Section 3402 Definitions.  Reserved.

Section 3403 Additions.  Change to read as shown.

Section 3403 Additions.  Reserved.

3404 Alternations.  Change to read as shown.

3404 Alternations.  Reserved.

3405 Repairs. Change to read as shown.

3405 Repairs.  Reserved

Section 3406 Fire Escapes.  Change to read as shown.

Section 3406 Fire Escapes.  Reserved.

Section 3407 Glass Replacement.  Change to read as shown.

Section 3407 Glass Replacement.  Reserved.

Section 3408 Change of occupancy.  Change to read as shown.

Section 3408 Change of occupancy. Reserved.

Section 3409 Historic Buildings.  Change to read as shown.

Section 3409 Historic Buildings.  Reserved.

Section 3410 Moved Structures.  Change to read as shown.

Section 3410 Moved Structures.  Reserved.

Section 3411 Accessibility for Existing Buildings.  Change to read as shown.

Section 3411 Accessibility for Existing Buildings.  Reserved.

Section 3412 Compliance Alternatives.  Change to read as shown.

Section 3412 Compliance Alternatives. Reserved

Chapter 35 Referenced Standards

Change to read as shown.

AA

1525 Wilson Blvd, Suite 600

Arlington, VA 22209

www.aluminum.org

Standard reference number	Title		Referenced in code section number

ADM 1—05 	Aluminum Design Manual: Part 1-A Aluminum Structures, Allowable Stress Design; and Part 1-B—Aluminum Structures, Load and Resistance Factor Design of Buildings and Similar Type Structures AA 94	 1604.3.5, 2002.2, 2003.2

Specifications for Aluminum Structures	2003.2

The Aluminum Formed Sheet Building Sheathing Design Guide   2003.2

The Commentary on Specifications for Aluminum Structures  	2003.2

Engineering Data for Aluminum Structures	2003.2

Revise text to read as follows:  Need to resolve conflict.

AAF              Aluminum Association of Florida, Inc.

3165 McCrory Place, Suite 185

Orlando, FL 32803

AAF—07-1 10 Guide to Aluminum Construction in High Wind Areas 2007-1 2010 2002.4.1

AAF—07-1    Guide to Aluminum Construction in High Wind Areas 2007-1         1622.1.2

[4341]

AAF

Aluminum Association of Florida, Inc.

Standard reference number 	Title		Referenced in code section number

AAF—07  10 Guide to Aluminum Construction in High Wind Areas 2010 2007,  2002.4.1

[4285]

Revisions to the AAF Guide:

General Notes: Chapter 2

Allowable Roof Panel Spans (Table 201) are for industry standard generic panel products, alternate roof panel approved equivalent products may be substituted based upon a Florida Product Approval, in accordance with design pressures specified in Table 201.

General Notes: Chapter 4

Allowable Roof Panel Spans (Table 401) are for industry standard generic panel products, alternate roof panel approved equivalent products may be substituted based upon a Florida Product Approval, in accordance with design pressures specified in Table 401.

General Notes: Chapter 5

Allowable Roof Panel Spans (Table 501) are for industry standard generic panel products, alternate roof panel approved equivalent products may be substituted based upon a Florida Product Approval, in accordance with design pressures specified in Table 501.

General Notes: Chapter 6

4) Allowable Roof Panel Spans (Table 601) are for industry standard generic panel products, alternate roof panel approved equivalent products may be substituted based upon a Florida Product Approval, in accordance with design pressures specified in Table 601.

General Notes: Chapter 8

Allowable Roof Panel Spans (Table 801) are for industry standard generic panel products, alternate roof panel approved equivalent products may be substituted based upon a Florida Product Approval, in accordance with design pressures specified in Table 801.

[S4632]

General Notes: Chapter 9

Allowable Roof Panel Spans (Table 901) are for industry standard generic panel products, alternate roof panel approved equivalent products may be substituted based upon a Florida Product Approval, in accordance with design pressures specified in Table 901.

(4285A3)

AAMA

American Architectural Manufacturers Association

1827 Waldon Walden Office Square, Suite 104550

Schaumburg, IL 60173-4268

[CA4589]

Standard reference number	Title		Referenced in code section number

Add to read as shown.

101/I.S.2—97	Voluntary Specifications for Aluminum, Vinyl (PVC) and Wood Windows and Glass Doors		1008.1.6, 1714.5.2.1, 1714.5.2.2, 2411.3.2.1

101/I.S.2/NAFS—02	Voluntary Performance Specification for Windows, Skylights and Glass Doors				1714.5.2.1, 1714.5.2.1.1, 2405.5, 2612.2

Add to read as shown.

103.3—83 - 09	Procedural Guide, Sec. 2 — Engineering Design Rules		2411.3.2.6

203—98	 03	Procedural Guide for the Window Inspection and Notification System	1714.5.2.2

501—05		Method for Test for Exterior Wall	1714.5.2.1, 1714.5.2.1.1, 1714.5.3.3.1, 2405.5, 2411.3.2.1.1, 2612.2

AAMA/WDMA/CSA101/I.S. 2/A440-05 or 08 Specifications for Windows, Doors and Unit Skylights             1714.5.2.1

AAMA 450-06  or  - 10 Voluntary Performance Rating Method for Mulled Fenestration  Assemblies             1714.5.5.1, 1714.5.5.1.2, 1714.5.5.1.3

AAMA 506-06 or -08 Voluntary Specifications for Hurricane Impact and Cycle Testing of Fenestration Products  1609.1.4

AAMA/NPEA/NSA 2100-02 Voluntary Specifications for Sunrooms   2002.6

- AAMA 800—05 or -08 Voluntary Specifications and Test Methods  for Sealants ……… 2510.8

- AAMA 812-04 Voluntary Practice for Assessment of Single Component Aerosol Expanding Polyurethane Foams for Sealing Rough Openings of Fenestration Installations …… 2510.8

[4264]

Add to read as shown.

AASHTO

American Association of State Highway & Transportation Officials

444 North Capitol Street N.W., Suite 249

Washington, DC 20001

Standard reference number	Title		Referenced in code section number

LTS 4		Structural Specifications for Highway Signs, Luminaries and Traffic Signals	1609.1.1

Add to read as shown.

ACI

American Concrete Institute

P.O. Box 9094

Farmington Hills, MI 48333-9094

Standard reference number	Title		Referenced in code section number

117		Standard Tolerances for Concrete Construction and Materials	1920.2

224.3R—95	Joints in Concrete Construction (Reapproved 2001)	1911.2

301		Specifications for Structural Concrete for Buildings	1920.2

315		Manual of Standard Practice for Detailing Reinforced Concrete Structures	1920.2

Change to read as shown.

318—08	Building Code Requirements for Structural Concrete	1604.3.2, 1805.4.2.6, 1805.9, 1806.4, 1808.2.23.1.1, 1808.2.23.2, 1808.2.23.2.1, 1808.2.23.2.2, 1809.2.3.2, 1809.2.3.2.2, 1810.1.2.2, 1812.8, 1901.2, 1901.3, 1901.4, 1902, 1903.1, 1903.2, 1903.3, 1903.4, 1903.5.1, 1903.6, 1904.4.2, 1905.1.4, 1905.3, 1905.4, 1905.5, 1905.6.5.5, 1905.8.3, 1905.11.3, 1906.1.5, 1906.3, 1906.4.3, 1907.1, 1907.2, 1907.4.1, 1907.6, 1907.7.2, 1907.7.3, 1907.7.4, 1907.7.5, 1907.8, 1907.9, 1907.10, 1907.11, 1907.12, 1907.13, 1908, 1908.1.1, 1908.1.2, 1908.1.3, 1908.1.4, 1908.1.5, 1908.1.6, 1908.1.7, 1908.1.8, 1908.1.9, 1909.1, 1909.3, 1909.4, 1909.5, 1909.6, 1910, 1910.2.1, 1910.2.2, 1910.2.3, 1910.2.4, 1910.3.1, 1910.4.1, 1910.4.2, 1910.4.3, 1910.4.3.1, 1910.5.2, 1913.1, 1918.1, 1918.2, 1919.3, 1920.2, 1921.1, 1922.4.1, 1922.4.3, 1922.6.4, 1926.4.1, 1926.4.3, 1926.5.6, 1928.3.1, 1928.7.2, 2108.3

Add to read as shown.

347		Recommended Practice for Concrete Foamwork	1920.2, 1925.1.1

506		Recommended Practice for Shotcreting	1920.2

506.2		Specification for Shotcrete		1920.2, 1929.1.2, 1929.8.1

Change to read as shown.

530—08	Building Code Requirements for Masonry Structures	1405.5, 1405.5.3, 1405.9, 1604.3.4, 1605.3.1.1, 1618.9,1805.5.2, 1812.7, 2101.2.3, 2101.2.4, 2101.2.5, 2103.11.6, 2106.1, 2106.1.1.1, 2106.1.1.2, 2106.1.1.3, 2106.3, 2106.4, 2106.5, 2106.6, 2107.1, 2107.2, 2107.2.1, 2107.2.2, 2107.2.4, 2107.2.5, 2107.2.6, 2108.1, 2108.2, 2108.3, 2108.4, 2109.1, 2109.2.3.1, 2109.2.3.2, 2114.2, 2121.2.12, 2122.1

AF&PA

American Forest & Paper Association

1111 19th St, NW Suite 800

Washington, DC 20036

Standard reference number	Title		Referenced in code section number

Add to read as shown.

AF&PA—92   Wood Structural Design Data                        2314.4.7

AF&PA—93   Working Stresses for Joists and Rafters AF&PA—05 Design Values for Joists and Rafters            2314.4.7

[4099]

Change to read as shown.

NDS—05	National Design Specification (NDS) for Wood Construction— with 2005 Supplement	721.6.3.2, 1715.1.1, 1715.1.4, 1805.4.5, 1808.1, 1823.1.8.1, 2306.1, 2306.2.1, 2306.3.2, Table 2306.3.1, Table 2306.4.1, 2306.3.4, 2306.3.5, 2306.4.1, Table 2308.9.3(4), 2314.4.7, 2315.4.1, 319.17.2.2.1, 2319.17.2.1.3, 2319.17.2.1.5

Add to read as shown.

T.R. No. 7—87           Permanent Wood Foundation System            PWF--07 Permanent Wood Foundation (PWF) Design Specification   1805.4.6, 1807.2, 2304.9.5, 2314.4.7

WCD 1—01    Wood Construction Data No. 1, Details for Conventional Wood Frame Construction        2314.4.7

WCD 3—83    Wood Construction Data No. 3, Design of Wood Formwork for Concrete Structures         2314.4.7

WCD 4—89 03 Wood Construction Data No. 4, Plank and Beam Framing for Residential Buildings         2306.1.2, 2314.4.7

AF&PA—87   All-Weather Wood Foundation System, Design, Fabrication, Installation Manual               2314.4.7

WCD 5—89    Wood Construction Data No. 5, Heavy Timber Construction Details                                   2314.4.7

WCD 6—88 06 Wood Construction Data No. 6, Design of Wood Frame Structures for Permanence       314.4.7, 2326.2.11

[4099]

Change to read as shown.

AHA

American Hardboard Association

1210 West N.W. Highway

Palatine, IL 60067

Standard reference number	Title		Referenced in code section number

A135.4—2004	Basic Hardboard						1404.3.1, 2303.1.6, 2314.4.1

A135.5—2004	Prefinished Hardboard Paneling				2303.1.6, 2304.6.2, 2314.4.1

A135.6—98	Hardboard Siding						1404.3.2, 2303.1.6, 2314.4.1

A194.1—85	Cellulosic Fiber Board						2303.1.5, 2314.4.1

Add to read as shown.

IB Spec. No. 1	Recommended Product and Application Specification —Structural Insulating Roof Deck					2314.4.1

IB Spec. No. 2	Recommended Product and Application Specification —½ inch Fiberboard Nail-Base Sheathing					2314.4.1

IB Spec. No. 3	Recommended Product and Application Specification —½ inch Intermediate Fiberboard Sheathing				2314.4.1

Add to read as shown.

AIA

American Institute of Architects

1735 New York  Ave. N.W

Washington, D.C. 20006-5292

FGI

Facility Guidelines Institute

1919 McKinney Avenue

Dallas, Texas 75201

www.fgiguidelines.org

Standard reference number	Title		Referenced in code section number

HHCF  06 10 	Guideline for the Design and Construction of  Health Care Facilities    419.2.1.2, 419.2.2, 419.3.2, 419.3.3, 419.3.4, 419.3.4.1, 419.3.4.2, 419.3.5, 419.3.5.1, 419.3.5.2, 419.3.6, 419.3.6.1, 419.3.7, 419.3.8.8, 419.3.8.9, 419.3.9, 419.3.10, 419.3.11, 419.3.13, 419.3.15, 419.3.17, 420.2.2, 420.2.5, 421.2.1.2, 421.2.2, 421.3.2, 421.3.2.1,  421.3.2.2, 421.3.3, 421.3.3.2.2, 421.3.3.3, 421.3.4, 421.3.5, 421.3.10

[3593]

AISC

American Institute of Steel Construction

One East Wacker Drive, Suite 3100

Chicago, IL 60601-2001

Standard reference number	Title		Referenced in code section number

Add to read as shown.

AISC	Torsional Analysis of Steel Members	2214.3

Change to read as shown:

AISC	Detailing for Steel Construction					2214.3

AISC	Engineering for Steel Construction					2214.3

AISC	Iron and Steel Beams - 1873 to 1952				2214.3

AISC	Plastic Design in Steel						2214.3

AISC	Plastic Design of Braced Multistory Steel Frames			2214.3

AISC	Serviceability Design Considerations for Low-Rise Buildings		2214.3, 2223.5.2

AISC	Simple Shear Connection, ASD					2214.3

AISC	Simple Shear Connections, LRFD					2214.3

AISC	Allowable Stress Design, Manual of Steel Construction, 2005, Thirteenth Edition		2214.3

AISC	Load Resistance Factor Design, Manual of Steel Construction		2214.3

AISC		Metal Building Certification Program, Category MB Certified		2223.11.2

[3638]

AISI

American Iron and Steel Institute

1140 Connecticut Avenue, Suite 705

Washington, DC 20036

Standard reference number	Title		Referenced in code section number

Add to read as shown.

AISI	Design Manual For Cold-Formed Steel			2214.3

AISI	Design Manual for Structural Tubing			2214.3

Z—2	Designing Fire Protection for Steel Trusses			2214.3

Z—3	Designing Fire Protection for Steel Columns (Beams), No column listed 		2214.3

AISI	Fire-Resistant Steel-Frame Construction			2214.3

AISI	Fire-Safe Structural Steel - A Design Guide			2214.3

AISI	Specifications for Design of Light-Gage Cold-Formed Stainless Structural Members	2214.3

AISI	Specification for the Criteria for Structural Application of Steel Cables for Buildings	2214.3

SG02—1	North American Specification for Design of Cold-Formed Steel Structural Members 	2214.3

Illuminating Engineering Society of North America,

120 Wall Street, 17th Floor,

New York, NY 10005-4001.

ANSI/IESNA RP-28-07 Lighting and the Visual Environment for Senior Living

……420.3.22.3

[4295]

Change to read as shown.

AITC

American Institute of Timber Construction

7012 S. Revere Parkway, Suite 140

Englewood, CO 80112

Standard reference number	Title		Referenced in code section number

A 190.1—07	Structural Glued Laminated Timber	   2303.1.3, 2306.1, 2314.4.2, 2315.1.1

Technical Note 7—96	Calculation of Fire Resistance of Glued Laminated Timbers	721.6.3.3, 2314.4.2

104—03	Typical Construction Details			2306.1, 2314.4.2

106	Code of Suggested Practices				2314.4.2

108—93	Standard for Heavy Timber Construction			2314.4.2

109—98	Standard for Preservative Treatment for Structural Glued Laminated Timber		2314.4.2

110—01	Standard Appearance Grades for Structural Glued Laminated Timber		2306.1, 2314.4.2

112—93	Tongue-and-Groove Heavy Timber Roof Decking	2306.1, 2314.4.2

113—01	Dimensions of Structural Glued Laminated Timber	2306.1, 2314.4.2

117—04	Standard Specifications for Structural Glued Laminated Timber of Softwood Species—Design Requirements—Standard Specifications for Structural Glued Laminated Timber of Softwood Species—Manufacturing Requirements					2306.1, 2314.4.2

119—96	Standard Specifications for Structural Glued Laminated Timber of Hardwood Species	2306.1, 2314.4.2

200—04		Inspection Manual					2306.1

AMCA

Air Movement and Control Association International, Inc.

30 W. University Drive

Arlington Heights, Illinois

60004 (4033 A1)

AMCA 540-08   Test Method for Louvers Impacted by Wind Borne Debris.....1609.1.2.1

[4034]

ANSI

American National Standards Institute

25 West 43rd Street, Fourth Floor

New York, NY 10036

Standard reference number	Title		Referenced in code section number

Add to read as shown.

A 41.1	Building Code Requirements for Masonry		2119.1.1, 2121.2.8

A 41.2	Building Code Requirements for Reinforced Masonry		2119.1.1

A 42.1	Specification For Gypsum Plastering			2515.1.1

A 42.4	Standard Specification for Interior Lathing and Furring	2514.1

A 97.1	Specification for the Application and Finishing of Gypsum Wallboard		2517.2

[S4759]

A 112.19.8M—87(R1996)	Suction Fittings for Use in Swimming Pools, Spas, Hot Tubs and Whirlpool Bathtub Appliances				424.2.6.6.2

Z 53.1	American National Standard Safety Color Code for Marking Physical Hazards	                                                                            423.4.6, 423.14.6

Change to read as shown.

Z 97.1—04 	Safety Glazing Materials Used in Buildings—Safety Performance Specifications and Methods of Test (Reaffirmed 1994) 1618.4.6.3, 2406.1.3, 2406.1.2, 2407.1, 2411.1.4, 2411.1.6, 3010.1

APA

APA - Engineered Wood Association

7011 So. 19th

Tacoma, WA 98466

Standard reference number	Title		Referenced in code section number

Add to read as shown.

APA E30		Engineered Wood Construction Guide		2314.4.3

APA PDS-Y510J—04       Plywood Design Specification (revised 1998)      2306.1, Table 2306.3.1, 2306.3.2, 2306.4.1, 2314.4.3

Change to read as shown.

APA PDS Supplement 1—90  Design and Fabrication of Plywood Curved Panels (revised1995) 2306.1, 2314.4.3

APA PDS Supplement 2—92 	Design and Fabrication of Plywood-lumber Beams (revised 1998)       2306.1, 2314.4.3

APA PDS Supplement 3—90	Design and Fabrication of Plywood Stressed-skin Panels (revised 1996)	2306.1, 2314.4.3

APA PDS Supplement 4—90	Design and Fabrication of Plywood Sandwich Panels (revised 1993)	2306.1, 2314.4.3

APA PDS Supplement 5—95	Design and Fabrication of All-plywood Beams (revised 1995)	2306.1, 2314.4.3

Add to read as shown.

APA B840		Siding Manufacturing Specifications		2314.4.3

APA L350		Design/Construction Guide Diaphragms and Shearwalls			2314.4.3

APA PRP108		Performance Standards and Policies for Structural-Use Panels	2314.4.3, 2315.1.2

APA V910		Plywood Folded Plate Laboratory Report 21		2314.4.3

ASCE/SEI

American Society of Civil Engineers

Structural Engineering Institute

1801 Alexander Bell Drive

Reston, VA 20191-4400

Standard reference number	Title		Referenced in code section number

Change to read as shown.

3—91	Structural Design of Composite Slabs	1604.3.3, 1920.3, 2209.2, 2214.3

5—08	Building Code Requirements for Masonry Structures	1405.5, 1405.5.3, 1405.9, 1604.3.4, 1618.9, 1805.5.2, 1812.7, 2101.2.3, 2101.2.4, 2101.2.5, 2103.11.6, 2106.1, 2106.1.1.1, 2106.1.1.2, 2106.1.1.3, 2106.3, 2106.4, 2106.5, 2106.6, 2107.1, 2107.2, 2107.2.1, 2107.2.2, 2107.2.4, 2107.2.5, 2107.2.6, 2108.1, 2108.2, 2108.3, 2108.4, 2109.1, 2109.2.3.1, 2109.2.3.2, 2121.2.12,

7-10 7-05                             Minimum Design Loads for Buildings and Other Structures (with Errata dated January 11, 2011)

[S4711]

including Supplements No. 1 and 2, excluding Chapter 14 and Appendix 11A [4220]

419.4.2.2.6, 420.4.2.2.6, 423.4.7, 423.9.1, 423.25.4, 423.28.2.6.4, 1514.4, 1605.1, 1605.2.2, 1605.3.1.2, 1605.3.2, 1608.1, 1608.3, 1608.3.4, 1608.3.5, 1608.4, 1608.5, 1608.6, 1608.7, 1608.8, 1608.9, 1609.1.1, 1609.1.4.1, Table 1609.3.1, 1609.4, 1609.7.3, 1612.1.3, 1612.2, 1614.1, 1615.1, 1615.2, 1618.4.8, 1618.9, 1619.1, 1619.2.1, 1619.2.2, 1620.1, 1621.1, 1622.1.1, 1626.1, 2002.6

8—02	Specification for the Design of Cold-formed Stainless Steel Structural Members	1604.3.3, 2209.1, 2214.3

Add to read as shown.

11	Guidelines for Structural Condition Assessment of Existing Buildings	1920.3, 2003.2, 2214.3

Add to read as shown.

ASHRAE

American Society of Heating, Refrigerating and Air-Conditioning Engineers, Inc.

1791 Tullie Circle NE

Atlanta, GA 30329-2305

Standard reference number	Title		Referenced in code section number

52.1—92	Gravimetric and Dust-Spot Procedures for Testing Air-Cleaning Devices Used in General Ventilation for Removing Particulate Matter ASHRAE Handbook—HVAC Applications 			Table 420.3.13.7

62—01	Ventilation for Acceptable Indoor Air Quality	Table 420.3.13.7

ASME

American Society of Mechanical Engineers

Three Park Avenue

New York, NY 10016-5990

Standard reference number	Title		Referenced in code section number

Change to read as shown.

A 17.1/CSA B44—07	Safety Code for Elevators and Escalators includes A17.1a in 2008 and A17.1b-2009 Addenda 1607.8.1, 3001.1, 3001.2, 3001.4, 3002.5, 3003.2, 3007.1, 3008.3,  3008.11.5, 308.14.1, 3008.1, 3010.1, 3011.1 (3519 A3)

[SP4724]

Add to read as shown.

A17.1S-05 	 Supplement to Safety Code for Elevators and Escalators       3001.2 (3519 A3)

A 17.3—96	Safety Code for Existing Elevators and Escalators	3001.1, 3001.2, 3001.5

Change to read as shown.

A18.1—03 A18.1—08                      	Safety Standard for Platform Lifts and Stairway Chairlifts              3001.1, 3001.2

Delete text to read as follows:

ASME

Add to read as shown.

A 120.1—01	Safety Requirements for Powered Platforms for Building Maintenance		3001.6

B 18.6.1-97         Wood Screws (Inch Series)                     1506.6

A17.1 - 1990 ...........................................................11-4.10

A17.1----(2004)                                  Safety Code for Elevators and Escalators includes A17.1a-in-  2005 Addenda

A90.1 - 03                                           Safety Standard for Belt Manlifts                 3001.2

A120.1—01                                          Safety Requirements for Powered Platforms for Building Maintenance                 3001.6

B20.1 - 2003                                           Safety Standard for Conveyors and related equipment                                         3001.2,  3005.3

(3519 A3)

ASTM

ASTM International

100 Barr Harbor Drive

West Conshohocken, PA 19428-2959

Standard reference number	Title		Referenced in code section number

01760—76	Standard Specification for Pressure Treatment of Timber Products		Table 1823

A 6/A 6M— 04a	Specification for General Requirements for Rolled Steel, Structural Steel Bars, Plates, Shapes, and Sheet Piling			2214.3

A 29	Standards for General Requirements for Hot-Rolled and Cold-Finished Carbon and Alloy Steel Bars		1827.1

A 252—98(2002)	Specification for Welded and Seamless Steel Pipe Piles	1809.3.1, 1810.6.1, 1826.1.5.3

A 306	Carbon Steel Bars Subject to Mechanical Property Requirements		1827.1

A 325—94	Specification for Structural Bolts, Steel, Heat-Treated, 120/105 Ksi Minimum Tensile Strength			2214.3

A 361	Specification for Steel Sheet Zinc-Coated (Withdrawn)	2319.17.1.1

A 421/A 421M—02     Specification for Uncoated Stress-Relieved Steel Wire for

Prestressed Concrete    1922.4.2, 2103.11.6

A 446	Specification for Steel Sheet, Zinc-coated (Galvanized) by the Hot-Dip Process, Structural (Physical) Quality			1917.4.4

A 490—93          Specification for Heat-Treated, Steel Structural Bolts, 150 ksi

Minimum Tensile Strength                                                 2214.3

A 525—87	Specification for General Requirements for Steel Sheet, Zinc-Coated (Galvanized) by the Hot-Dip Process	1917.4.4, 2214.3, 2517.2, 2517.5.1, 2517.5.4

A570/A570M-98	Specification for Steel, Sheet and Strip, Carbon, Hot-Rolled (withdawn)	1826.1.5.3

A 611	Standard Specification for Structural Steel (SS), Sheet, Carbon, Coil-Rolled	1826.1.5.3, 1917.4.4

A 615/A 615M—04a	Specification for Deformed and Plain Billet-Steel Bars for Concrete Reinforcement	1908.1.8, 1920.2, 1920.4, 1922.4.6, 2103.11.1, 2103.11.6

A616/A616M-96a	Specification for Rail-Steel Deformed and Plain Bars for Concrete Reinforcement (withdrawn)			1922.4.6

A 617	Standard Specification for Axle-Steel Reformed and Plain Bars for Concrete Reinforcement					1922.4.6

A 653/A 653M—07 	Specification for Steel Sheet, Zinc-Coated Galvanized or Zinc-Iron Alloy-Coated Galvannealed by the Hot-Dip Process	Table 1507.4.3, 2211.2, 2211.2.2.1, 2319.17.2.2.7

A 706/A 706M—05a	Specification for Low-Alloy Steel Deformed and Plain Bars for Concrete Reinforcement	1903.5.2, 1908.1.3, 1922.4.6

A 722/A 722M—07     Specification for Uncoated High-Strength Steel Bar for Prestressing Concrete	1922.4.2, 2103.11.6, 2106.1.1.3.1

A 767/A 767M—00b	Specification for Zinc-Coated (Galvanized) Steel Bars for Concrete Reinforcement	1922.4.6, 1926.5.5, 2103.11.1

A 775/A 775M—04 Specification for Epoxy-Coated Steel Reinforcing Bars		1922.4.6, 2103.11.1

Revise text to read as follows:

ASTM A 924 /A924M—07  Standard Specification for General Requirements for Steel Sheet, Metallic-coated by the Hot-dip Process . . . . . . . . . . . Table 1507.4.3(1). 2319.17.2.2.7.

A 924/A924M—99	Standard Specification for General Requirements for Steel Sheet, Metallic-Coated by the Hot-Dip Process		2319.19.2.2.7

B 370-03              Specification for Copper Sheet and Strip for Building Construction        Table 1507.4.3

C 5—03	Specification for Quicklime for Structural Purposes	Table 2507.2, 2525.2.3

C 28/C 28M—00 (2005) Specification for Gypsum Plasters		Table 2507.2, 2515.2.2

C 31/C 31M—06	Practice for Making and Curing Concrete Test Specimens in the Field.	1905.6.3.2, 1905.6.4.2, 1923.2.2.3, 1923.2.3.2

C 33—03	Specification for Concrete Aggregates 	721.3.1.4, 721.4.1.1.3, Table 1904.2.1, 1922.1, 1922.2, 1922.2.2

C 34—03	Specification for Structural Clay Load-Bearing Wall Tile	2103.2, 2119.8.3

C 35—01(2005)	Specification for Inorganic Aggregates for Use in Gypsum Plaster 	Table 2507.2, 2515.2.1.1

C 36/C 36M—03	Specification for Gypsum Wallboard 		Figure 721.5.1(2), Figure 721.5.1(3), Table 721.5.1(2), Table 2506.2, 2517.2

C 37/C 37M—-01	Specification for Gypsum Lath		Table 2507.2, 2514.2

C 39—99ae1	Test Method for Compressive Strength of Cylindrical Concrete Specimens 	1905.6.3.2, 1923.2.2.3

C 42/C 42M—99	Test Method for Obtaining and Testing Drilled Cores and Sawed Beams of Concrete	1923.2.4.1, 1923.2.4.3

C 52-01A	Specification for Gypsum Partition Tile or Block					2119.9.3

C 55—06e01	Specification for Concrete Brick	Table 721.3.2, 2103.1, 2105.2.2.1.2, 2119.4.3.2, 2119.4.3.3

C 56—05	Specification for Structural Clay Non-Load-Bearing Tile		2103.2, 2119.8.3.3

C 57	Specification for Structural Clay Floor Tile			2119.8.3.2

C 61/C 61M—00 (2006)	Specification for Gypsum Keene’s Cement			Table 2507.2, 2515.2.4

C 62—05	Specification for Building Brick (Solid Masonry Units Made from Clay or Shale)		2103.2, 2105.2.2.1.1, 2119.4.3.1

C 67—07	Test Methods of Sampling and Testing Brick and Structural Clay Tile 	721.4.1.1.1, 1507.3.5, 2104.5, 2105.2.2.1.1, 2109.8.1.1, 2119.4.2

C 90—06b	Specification for Loadbearing Concrete Masonry Units	Table 721.3.2, 1805.5.2, 2103.1, 2105.2.2.1.2, 2119.7.2

C 91—05	Specification for Masonry Cement			Table 2103.7(1), Table 2507.2, 2515.2.6

C 94/C 94M—07	Specification for Ready-Mixed Concrete		109.3.1, 1905.8.2, 1924.2.2, 1924.2.3

C 144—03	Standard Specification for Aggregate for Masonry Mortar		1928.7.2, 2119.12.1.1

C 150—07	Specification for Portland Cement 	1904, Table 1904.2.3, 1922.1, Table 2103.7(1), Table 2507.2, 2515.2.4

C 172—04	Practice for Sampling Freshly Mixed Concrete			1905.6.3.1, 1923.2.2.2

C 206—03	Specification for Finishing Hydrated Lime			Table 2507.2, 2525.2.3

C 212—00(2006)	Specification for Structural Clay Facing Tile					2103.2, 2119.8.2

C 216—07	Specification for Facing Brick (Solid Masonry Units Made from Clay or Shale)	2103.2, 2105.2.2.1.1, 2119.4.3.1

C 270—07	Specification for Mortar for Unit Masonry			2103.7, Table 2103.7(2), 2119.12.1

C 330—05	Specification for Lightweight Aggregates for Structural Concrete	721.1.1, 1905.1.4,

1922.2.2

C 471M—01	Standard Test Methods for Chemical Analysis of Gypsum and Gypsum Products		2119.9.2

C 472—99 (2004)	Specification for Standard Test Methods for Physical Testing of Gypsum, Gypsum Plasters and Gypsum Concrete						Table 2506.2, 2119.9.2

C 473—06a	Test Method for Physical Testing of Gypsum Panel Products		Table 2506.2, 2119.9.2

C 475—05	Specification for Joint Compound and Joint Tape for Finishing Gypsum Wallboard		Table 2506.2, 2517.2

C 494/C494M-99	Standard Specification for Chemical Admixtures for Concrete				1917.4.5

C 495–99a	Standard Test Method for Compressive Strength of Lightweight Insulating Concrete	1917.1.1, 1917.1.2, 1917.1.3

C 509-00               Elastomeric Cellular Preformed Gaskets and Sealing Material      2411.3.4

C 578—07	Standard Specification for Rigid, Cellular Polysturene Thermal Insulation	1917.4.12

C 595—07	Specification for Blended Hydraulic Cements	1922.1.2, Table 2103.7(1), Table 2507.2

C 645—07	Specification for Nonstructural Steel Framing Members	2319.17.1.3, Table 2506.2, Table 2507.2, 2517.2, 2517.5.1, 2517.5.4

C 652—05a	Specification for Hollow Brick (Hollow Masonry Units Made from Clay or Shale)	2103.2, 2105.2.2.1.1, 2119.4.3.1, 2119.4.3.1

C 685/ C 685M—98a	Specification for Concrete Made by Volumetric Batching and Continuous Mixing	1905.8.2, 1924.2.2

C 794—01	Standard Test Method for Adhesion-in-Peel of Elastomeric Joint Sealants	2415.4

C 796—97	Standard Test Method for Foaming Agents For Use in Producing Cellular Concrete Using Performed Foam	1917.1.1, 1917.1.2, 1917.1.3, 1917.4.6

C 864-05               Dense Elastomeric Compression Seal Gaskets, Setting Blocks, and Spacers   ________________________________________                                                        2411.3.4

…

- C 920—05 Specification for Elastomeric Joint Sealants .……………. 2415.4, 2510.8.8

C 926—98a(2005)	Specification for Application of Portland Cement-Based Plaster	2510.3, Table 2511.1, 2511.3, 2511.4, 2512.1, 2512.1.2, 2512.2, 2512.6, 2512.8.2, 2513.7, 2512.9, 2513.7, 2516.1.1, 2516.1.4

C 1036—01	Specification for Flat Glass							2411.1.1

C 1048—97b	Standard Specification for Heat-Treated Flat Glass—Kind HS, Kind FT Coated and Uncoated Glass									2411.1.5

C 1077	Standard Practice for Laboratories Testing Concrete and Congete Apparatus for Use in Construction and Criteria for Laboratory Evaluation				1920.4, 1922.6.2

C 1115-00             Dense Elastomeric Silicone Rubber Gaskets and Accessories        2411.3.4

C 1167—03	Specification for Clay Roof Tiles		1507.3.4, 1507.3.5, 1523.6.5.2

C 1225	Specification For Nanasbestos Fiber-Cement Roofing Shingles, Shakes and Slates	1518.5.1

C 1281- 03 Standard Specification for Preformed Tape Sealants for Glazing Applications …………………………………………………………. 2510.8

D 25—99- ((2005)	Specification for Round Timber Piles		1809.1.1, 1823.1

D 41—05	Specification for Asphalt Primer Used in Roofing, Dampproofing, and Waterproofing	Table 1507.10.2, 1514.2.3.2, 1517.6.2.4, 1519.6, 1521.6, 1521.14.1

D 43-00 (2006)	Specification for Coal Tar Primer Used in Roofing, Dampproofing, and Waterproofing 	Table

1507.10.2, 1521.14.2, 1517.6.2.4, 1519.6, 1521.6

D 92	Standard Test Method for Flasin and Fire Points by Cleveland Open Cup		1519.2.2

D 256—03	Standard Test Methods for Determining the Izod Pendulum Impact Resistance of Plastics	2612.2

D 312—00(2006)	Specification for Asphalt Used in Roofing	Table 1507.10.2, 1519.3, Table 1519.3A, 1519.4,

1521.14.1

D412—98a (2002)e1	Standard Test Methods for Vulcanized Rubber and Thermoplastic Elastomers—Tension

D 450—07	Specification for Coal-Tar Pitch Used in Roofing, Dampproofing, and Waterproofing	Table 1507.10.2, Table 1519.3B

D624—00e1	Standard Test Method for Tear Strength of Conventional Vulcanized Rubber and Thermoplastic Elastomers			2415.4

D 635—06	Test Method for Rate of Burning and/or Extent and Time of Burning of Self-Supporting Plastics in a Horizontal Position	2606.4, 2612.2

D 638-03              Test Method for Tensile Properties of Plastics          2612.2

D1079—02	Standard Terminology Relating to Roofing, Waterproofing, and Bituminous Materials	1513.1

D1143/D 1143M- 07	Test Method for Piles Under Static Axial Compressive Load	1808.2.8.3, 1829.1.7

D1167	Methods of Testing Asphalt-Base Emulsions for Use as Protective Coatings for Built-Up Roofs	1523.6.5.2

D1556	Standard Test Method for Density of Soil In-Place by the Sandcone	1820.3.2, 1834.3.3

D1557—02e01	Test Method for Laboratory Compaction Characteristics of Soil Using Modified Effort (56,000 ft-lb/ft3 (2,700 kN m/m3))	1803.5, 1820.3.2

D1621	Standard Test Method for Compressive Properties of Rigid Cellular Plastics	1523.6.5.2.17.1

D1622	Standard Test Method for Apparent Pensity of Rigid Cellular Plastics	1523.6.5.2.17.2

D1623	Standard Test Method for Tersile and Tersile Adhesion Properties of Rigid Cellular Plastics	523.6.5.2.17.3

ASTM D 1761-88 (2000) Standard Test Methods for Mechanical Fasteners in Wood…1716.1.2 [4411]

D1761—06     Test Method for Mechanical Fasteners in Wood	1715.1.1, 1715.1.2, 1715.1.3, 1834.3.3, 2314.4.4 [4417]

D1836 	Specification for Commercial Hexanes			1519.12.1

D1863—05	Specification for Mineral Aggregate Used on Built-Up Roofs	Table 1507.10.2, 1519.2.1

D1929—96 (2000)e01	Test Method for Determining Ignition Properties of Plastics	402.14.4, 406.5.2,

1407.11.2.1, 2606.4, 2612.2

D2126	Standard Test Method for Response of Rigid Cellular Plastics to Thermal and Humid Aging	523.6.5.2.17.4

D2240—03	Standard Test Method for Rubber Property—Durometer Hardness			2415.4

Add text to read as follows:

ASTM D 2824 Standard Specification for Aluminum-Pigmented Asphalt Roof Coatings, Nonfibered Asbestos Fibered, and Fibered without Asbestos…….    Table 1507.10.2

D2565—00	Standard Practice for Xenon Arc Exposure of Plastics Intended for Outdoor Applications	2612.2

D2626—04	Specification for Asphalt-Saturated and Coated Organic Felt Base Sheet Used in Roofing	1507.3.3, Table 1507.10.2, 1518.4

D2842	Standard Test Method for Water Absorption of Rigid Cellular Plastics	1523.6.5.2.17.6

D2843—99(2004)e01	Test for Density of Smoke from the Burning or Decomposition of Plastics	2606.4,

2612.2

D2856	Standard Test Method for Open-cell Content of Rigid Cellular Plastics by the Air- Pycnometer.	523.6.5.2.17.5

D2898—04	Test Methods for Accelerated Weathering of Fire-Retardant-Treated Wood for Fire Testing	1505.1, 1516.1, 2303.2.1, 2303.2.3, 2314.4.4, 2327.4, 2329.1

D2922	Standard Test Method for Density of Soil and Soil Aggregate In-Place by Nuclear Methods (Shallow Depth)				1820.3.2

D3018	Standard Specification for Class A Asphalt Shingles Surfaced with Mineral Granules	1523.6.5.1

D3201—07	Test Method for Hygroscopic Properties of Fire-Retardant Wood and Wood-Base Products						2303.2.4, 2314.4.4, 2327.5

D3441	Static Cone Soundings					1834.3.3

D3462—07	Specification for Asphalt Shingles Made from Glass Felt and Surfaced with Mineral Granules

1507.2.5, 1523.6.5.1

D 3498—03	Standard Specifications for Adhesives for Field-Gluing Plywood to Lumber Framing for Floor Systems			2314.4.4, 2322.1.5

D3679—06a	Specification for Rigid Poly (Vinyl Chloride) (PVC) Siding		1404.9, 1405.13

D3737—07	Practice for Establishing Allowable Properties for Structural Glued Laminated Timber (Glulam)	2303.1.3

D3746—85 (2002) el	Test Method for Impact Resistance of Bituminous Roofing Systems	1504.7, 1515.2.4

D3787—89	Test Method for Bursting Strength of Textiles-Constant-Rate-of-Traverse (CRT) Ball Burst Test	424.2.17.1.15

D4272—03	Test Method for Total Energy Impact of Plastic Films by Dart Drop		1504.7, 1515.2.4

D4402	Viscosity Determinations of Unfilled Asphalt Using the Brookfield Thermoset Apparatus	1519.2.3

D4477-04a           Standard Specification for Rigid (Unplasticized) Poly (Vinyl Chloride) (PVC) Siding

1404.9, 1404.9.1, 1405.13

D5034—95	Standard Test Method for Breaking Strength and Elongation of Textile Fabrics (Grab Test)	24.2.17.1.15

D5055—05	Specification for Establishing and Monitoring Structural Capacities of Prefabricated Wood I-joists	424.2.14.1.15, 2303.1.2

D5456—05a	Specification for Evaluation of Structural Composite Lumber Products		2303.1.9

D5957-98             Standard Guide for Flood Testing Horizontal Waterproofing Installation 1519.16.6

D6083—05e01	Specification for Liquid Applied Acrylic Coating Used in RoofingTable 1507.10.2, 1507.15.2,

1523.6.2.1.1, 1523.6.3.1, 1523.6.5.12.2

D6380-03	Specifications for Asphalt Roll Roofing (Organic Felt)	1507.3.3

D 7147-05, Standard Specification for Testing and Establishing Allowable Loads of Joist Hangers…….2303.5 [4417]

Add text to read as follows:

ASTM D 6509-00 Specification for Atactic Polypropylene (APP) Modified Bituminous Base Sheet Materials Using Glass Fiber Reinforcements……….1507.11.2

D6841-03             Standard Practice for Calculating Design Value Treatment Adjustment Factors for Fire-Retardant-Treated Lumber                          2303.2.2.2

D7158-07               Standard Test Method for Wind Resistance of Sealed Asphalt Shingles (Uplift Force/Uplift

Resistance Method)                                        Table 1507.2.10

E 84—07	Test Method for Surface Burning Characteristics of Building Materials	402.10, 402.14.4, 406.5.2, 410.3.5.3, 422.2.16.3, 423.11.5, 703.4.2, 719.1, 719.4, 802.1, 803.1, 803.5, 803.6.1, 803.6.2, 1407.10, 1407.10.1, 2303.2, 2314.4.4, 2327.1, 2603.3, 2603.4.1.13, 2603.5.4, 2604.2.4, 2606.4, 2612.2, 2612.3

E 96/E 96M—05	Test Method for Water Vapor Transmission of Materials		1203.2, 1523.6.5.2.17.7

E 108—07a	Test Methods for Fire Tests of Roof Coverings	423.12.1, 1505.1, 1513.1, 1516.1, 1523.1.2, 2329.1, 2603.6, 2610.2, 2610.3

E 119—07	Test Methods for Fire Tests of Building Construction and Materials	410.3.5.2, 703.2, 703.2.1, 703.2.3, 703.3, 704.7, 704.9, 706.7, 711.3.2, 712.3.1, 712.4.1, 712.4.6, 713.1, 713.4, 714.7, 715.2, 716.5.2, 715.5.3.1, 715.6.2, 716.5.2, 716.5.3.1, 716.6.2, Table 721.1(1), 1407.10.2, 2103.2, 2603.3, 2603.4, 2603.4.1.13, 2603.5.4, 2604.2.4, 2606.4, 2612.2, 2612.3.1.1, 2612.3.1.4

E163-84E01	Methods of Fire Tests For Window Assemblies (withdrawn)			2121.2.1.2.8

Add text to read as follows:

ASTM E 283-04 Test Method for Determining Rate of Leakage Through Exterior Windows, Curtain Walls and Doors Under Specified Pressure Differences Across the Specimen------------  13-606.ABC.1.1, 13-606.ABC.1.2.4

E 330—02	Test Method for Structural Performance of Exterior Windows, Curtain Walls, and Doors by Uniform Static Air Pressure Difference				1714.5.3, 2415.4, 2415.7.1

E 331—00	Test Method for Water Penetration of Exterior Windows, Skylights, Doors, and Curtain Walls by Uniform Static Air Pressure Difference					1403.2, 2415.4

E1300—04e01, 09a or 98 (HVHZ)	Practice for Determining Load Resistance of Glass in Buildings	1714.5.2.1, 2404.1, 2404.2, 2404.3, 2411.2.1.1, 2411.2.1.2, 2411.3.1.2 [4264]

E1592—01	Test Method for Structural Performance of Sheet Metal Roof and Siding Systems by Uniform Static Air Pressure Difference					1504.3.2, 2411.2.1.2

E 1886-02 or 06 05	Standard Test Method for Performance of Exterior Windows, Curtain Walls, Doors, and Storm Shutters Impacted by Missile(s) and Exposed to Cyclic Pressure Differentials	202, 1609.1.4 [4264]

E 1996-02 or 06  or 09 Specification for Performance of Exterior Windows, Glazed Curtain Walls, Doors, and Storm Shutters Impact by Windborne Debris in Hurricanes                                              202, 1609.1.4 [4264]

ASTM E 1966 change to read as shown.

ASTM E 1966 2003

E 2203-02             Dense Thermoplastic Elastomers Used for Compression Seals, Gaskets, Setting Blocks, Spacers and Accessories                                                                                             2411.3.4

[S4806]

F851—87 (2000)	Standard Test Method for Self-Rising Seat Mechanisms	1024.10

F1346—91 (2003)	Performance Specification for Safety Covers and Labeling Requirements for All Covers for Swimming Pools, Spas and Hot Tubs		424.1.3.9, 424.2.2, 424.2.17,

G53—96	Practice for Operating Light-and Water-Exposure Apparatus (Fluorscent UV-Condensation Type) for Exposure of Nonmetallic Materials					424.17.1.15.2

G85	Standard Practice for Modified Salt Spray (Fog) Testing	1517.5.1, 1517.5.2, 1523.6.5.2.10, 1523.6.5.2.11

G60—01	Standard Practice for Conducting Cyclic Humidity Tests			2319.17.2.2.8

ASTM G 155 Add to read as shown:

ASTM G 155 – 05a Standard Practice for Operating Xenon Arc Light Apparatus for Exposure of Non-Metallic Materials………….2612.2

AWPA

American Wood-Preservers’ Association

P.O. Box 5690

Grandbury, TX 76049

Standard reference number	Title			Referenced in section number

Change to read as shown.

C1—03	All Timber Products—Preservative Treatment by Pressure Processes	1505.6, 2303.1.8, 2314.4.5

C2—01	Lumber, Timber, Bridge Ties and Mine Ties—Preservative Treatment by Pressure Processes

Table 1507.9.5, 1805.4.5, 1805.7.1, 2303.1.8, 2304.11.2, 2304.11.4, 2304.11.7, 2314.4.5

C3—99	Piles—Preservative Treatment by Pressure Processes	1805.4.5, 1809.1.2, 1823.1.3, 2303.1.8, 2314.4.5

C4—99	Poles—Preservative Treatment by Pressure Processes		1805.7.1, 1808.1.2, 2303.1.8, 2314.4.5

Add to read as shown.

C5	Posts - Pressure Treatment					2314.4.5

C6	Cross Ties and Switch Ties Pressure Treatment		2314.4.5

C7	Incised (Red, White & Alaska Yellow Cedar) Poles Butts Thermal Treatment		2314.4.5

C8	Poles (Western Red & Alaska Yellow Cedar) Full Length Thermal Treatment		2314.4.5

Change to read as shown.

C9—00	Plywood—Preservative Treatment by Pressure Processes	2304.11.2, 2304.11.4, 2304.11.7, 2314.4.5

Add to read as shown.

C10	Poles (Lodgepole Pine) Full Length Thermal Treatment	2314.4.5

C11	Wood Blocks for Floors & Platforms Pressure Treatment	2314.4.5

Change to read as shown.

C14—99	Wood for Highway Construction, Pressure Treatment by Pressure Process          2314.4.5

C16—00	Wood Used on Farms, Pressure Treatment by Pressure Process 	2314.4.5

C18—99	Standard for Pressure Treated Material in Marine Construction	    2314.4.5

Add to read as shown.

C20	Structural Lumber, Fire Retardant Pressure Treatment	    2314.4.5

Change to read as shown.

C22—96	Lumber and Plywood for Permanent Wood Foundations— Preservative Treatment by Pressure Processes		1805.4.6, 2314.4.5

C23—00	Round Poles and Posts Used in Building Construction— Preservative Treatment by Pressure Processes			2314.4.5

Add to read as shown.

C25	Crossarms Pressure Treatment				2314.4.5

C26		Crossarms, Non-Pressure Treatment			2314.4.5

Change to read as shown.

C28—99	Standard for Preservative Treatment by Pressure Process of Structural Glued Laminated Members and Laminations before Gluing					2314.4.5

Add to read as shown.

C29	Lumber to be Used for the Harvesting, Storage and Transportation of Food Stuffs— Preservative Treatment by Pressure Processes	2314.4.5

Change to read as shown.

M4—06	Standard for the Care of Preservative-Treated Wood Products	1809.1.2, 1823.1.4, 2303.1.8, 2314.4.5

Add to read as shown.

M6—96	Brands Used on Forest Products							2315.1.9

AWS

American Welding Society

550 N.W. LeJeune Road

Miami, FL 33126

Standard reference number	Title			Referenced in section numb

Add to read as shown.

B2.1	Standard Welding Procedure and Performance Qualification	2214.3

C5.4	Recommended Practice for Stud Welding			2214.3

Change to read as shown.

D1.1—04	Structural Welding Code—Steel				2214.3

Add to read as shown.

D1.2	Structural Welding Code—Aluminum			2003.3

Change to read as shown.

D1.3—98	Structural Welding Code—Sheet Steel			2214.3

D1.4—98	Structural Welding Code—Reinforcing Steel	1903.5.2, 1922.4.4, 1922.4.5, 1926.4.6, 1926.4.8, 2119.1.1, 2214.3

Add to read as shown.

D9.1	Specification for Welding of Sheet Metal			2214.3

D10.9	Standard for Qualification of Welding Procedures and Welders for Piping and Tubing	2214.3

CPSC

Consumer Product Safety Commission

4330 East West Highway

Bethesada, MD 20814-4408

Standard reference number	Title			Referenced in section number

Change to read as shown.

16 CFR Part 1201(1977)	Safety Standard for Architectural Glazing Material		2406.1.1, 2406.2.1, 2407.1, 2408.2.1, 2408.3, 2411.1.3, 2411.3.1.3, 2411.4.2, 2612.4.8,

Add to read as shown.

Pub. No. 362		Safety Barrier Guidelines for Home Pools		424.1.3.1.9

DASMA

Door and Access Systems Manufacturers

Association International

1300 Summer Avenue

Cleveland, OH 44115-2851

Standard reference number	Title		Referenced in section number

Revise text to read as follows:

ANSI/DASMA 107-98 (R200)    Room Fire Test Standard…. (remainder unchanged)

ANSI/DASMA 108- 05   Standard Method for Testing Sectional Garage Doors and Rolling Doors:  Determination of Structural Performance Under Uniform Static Air Pressure Difference                                                 1714.5.3.1

Add to read as shown.

Revise text to read as follows:

ANSI/DASMA 115-05           Standard Method for Testing Garage Doors….. (remainder unchanged)

115-05    Standard Method for Testing Garage Doors and Rolling Doors: Determination of Structural Performance Under Missile Impact and Cyclic Wind Pressure              1609.1.2

DECO

Document Engineering Co., Inc.,

5210 Stagg Street

Van Nuys, California 9140

ANSI Z 358.1 04  Emergency Eyewash and shower Equipment    Table 420.3.17.2

DOC/NIST

Department of Commerce

National Institute of Standards and Technology

100 Bureau Drive Stop 3460

Gaithersburg, MD 20899

Standard reference number	Title		Referenced in section number

Add to read as shown.

CS236	Mat-Formed Particleboard					2314.4.6, 2315.1.6

Change to read as shown.

PS-1-07	Construction and Industrial Plywood	2211.2.2.2, 2303.1.4, 2304.6.2, Table 2304.7(4), 2306.3.2, 2314.4.6, 2315.1.2

PS-2-04	Performance Standard for Wood Based Structural Use Panels	1809.1.1, 2211.3.1, 2303.1.4, 2304.6.2, Table 2304.7(4), Table 2304.7(5), Table 2306.3.1, 2306.3.2, 2314.4.6, 2315.1.2

PS20-05	American Softwood Lumber Standard        1809.1.1, 2302.1, 2303.1.1, 2314.4.6, 2315.1.8

Add to read as shown.

PS56	Structural Glued Laminated Timber					2314.4.6

DOL/OSHA

Department of Labor

Occupational Safety and Health Administration

Frances Perkins Building

200 Constitution Avenue, NW

Washington, DC 20210

Standard reference number	Title			Referenced in section number

Add to read as shown.

29CFR Part 1910		Occupational Safety and Health Standards		1618.4

29CFR 1926-950 (p)	Occupational Safety and Health Administration

Excavation Safety Act	1817.1

DOT

Department of Transportation

c/o Superintendent of Documents

U.S. Government Printing Office

Washington, DC 20402-9325

Standard reference number	Title			Referenced in section number

Add to read as shown.

14 CFR Part 150 (2005) Airport Noise Compatibility Planning, Federal Aviation Administration	3113.1

Florida Building Code, Accessibility Ch. 11 FBC-B—2012 Ch. 11, Florida Building Code, Building (Florida Accessible Code for Building Construction)        101.4.8, 104.11.3, 201.5, 403.1.1, 406.2.2, 412.1.6, 423.10.2.8.7, 423.27.4, 423.28.2.4, 427.1.4.1.1.3, 427.1.4.4.1, 427.1.4.4.2, 1003.3.4, 1003.5.3, 1007.1, 1008.1, 1009.5.3, 1009.11.8, 1009.14, 1010.1, 1010.8, 1010.9, 1208.2, 3001.3

[SP4731]

Add to read as shown.

FC&PA

Florida Concrete & Products Association Inc.

3030 Dade Ave.

Orlando, Fla. 32804

Masonry Assciation of Florida…

MAF

Masonry Association of Florida

398 Camino Gardens Blvd.

Suite 108

Boca Raton, FL 33432

[4350]

Standard reference number	Title		Referenced in section number

FC&PA—97	Guide to Concrete Masonry Residential Construction in High Wind Areas		1609.1.1

FEMA

Federal Emergency Management Agency

Federal Center Plaza

500 C Street S.W.

Washington, DC 20472

Standard reference number	Title		Referenced in section number

Add to read as shown.

44CFR Part 59 National Flood Insurance Program Emergency Management and Assistance, General Provisions     1612.2 423.4.2, 3110.1.2

44CFR Part 60—97        Criteria for Land Management and Use           1612.2 423.4.2, 3110.1.2

[3890]

Add to read as shown.

FINA

Federation Internationale de Natation Amateur

Av. de l' Avant-Poste 4

1005 Lausanne

SWITZERLAND

Standard reference number	Title		Referenced in section number

CHG-22	FINA Handbook 1998-2000					424.1.2.7

Add to read as shown.

Florida

Codes

Florida Building Commission

Building Codes and Standards

Department of Community Affairs

2555 Shumard Oak Blvd.

Tallahassee, FL 32399-2100

Standard reference number	Title			Referenced in section number

Ch. 11 FBC-B—2010	Ch. 11, Florida Building Code, Building (Florida Accessible Code for Building Construction)	101.4.8, 104.11.3, 201.5, 403.1.1, 406.2.2, 412.1.6, 423.10.2.8.7, 423.27.4, 423.28.2.4, 427.1.4.1.1.3, 427.1.4.4.1, 427.1.4.4.2, 1003.3.4, 1003.5.3, 1007.1, 1008.1, 1009.5.3, 1009.11.8, 1009.14, 1010.1, 1010.8, 1010.9, 1208.2, 3001.3

FBC-Energy Conservation—2010	Ch. 13 Florida Building Code, Building (Energy Efficiency)	101.4.7, 201.6, 1202.3.2, 1301.1.1, 1403.2

Ch. 27 FBC-B—2010	Ch. 27 Florida Building Code, Building (Electrical Systems)	101.4.1, 102.2.6, 107.3, 414.5.4, 414.9.2.8.1, 415.9.2.8, 419.3.8.3, 419.3.8.8, 419.3.14.2, 419.3.14.4, 419.3.15.2, 420.3.19.3, 420.3.19.5, 420.3.20.2, 420.3.20.3, 421.3.9.3, 421.3.9.5, 421.3.10.10, 423.25.5, 423.25.5.2, 424.1.4.1, 424.1.6.5.16.4.1, 424.1.6.5.1, 424.1.9.8.5, 424.2.16, 425.3.5, 426.3.5, 427.1.4.1.5, 603.1.3, 904.3.1, 907.1.3, 907.5, 907.9.3, 909.11, 909.12.1, 909.16.3, 1006.2.3.4, 1006.2.4, 1205.4.1, 1405.10.4, 2701.1, 2702.1

FEBC—2010	Florida Existing Building Code			101.2. 1009.3

FPC—2010	Florida Fire Prevention Code	101.4.6, 102.6, 201.3, 307.2, Table 307.7(1), Table 307.7(2), 307.9, Table 307.7(1), Table 307.7(2), 307.9, 308.2, 308.3, 404.2, 406.5.1, 406.5.2, 406.6.1, 410.3.6, 411.1, 412.4.1, 413.1, 414.1.1, 414.1.2, 414.1.2.1, 414.2.4, Table 414.2.4, 414.3, 414.5, 414.5.1, Table 414.5.1, 414.5.2, 414.5.4, 414.5.5, 414.6, 415.1, 415.3, 415.3.1, Table 415.3.1, Table 415.3.2, 415.7, 415.7.1, 415.7.1.4, 415.7.2, 415.7.2.3, 415.7.2.5, 415.7.2.7, 415.7.2.8, 415.7.2.9, 415.7.3, 415.7.3.3.3, 415.7.3.5, 415.7.4, 415.8, 415.9.1, 415.9.2.7, 415.9.5.1, 415.9.7.2, 704.8.2, 706.1, 901.2, 901.3, 901.5, 901.6.2, 903.2.6.1, 903.2.11, Table 903.2.13, 903.5, 904.2.1, 905.1, 906.1, 907.2.5, 907.2.12.2, 907.2.14, 907.2.16, 907.19, 909.20, 910.2.3, Table 910.3, 1001.3, 1203.4.2, 1203.5, 2702.2.8, 2702.2.10, 2702.2.11, 2702.2.12, 2702.3, 3102.1, 3103.1, 3309.2

FBC-FG—2010	Florida Building Code, Fuel Gas	101.4.2, 109.3, 201.1, 201.3, 415.7.3, 424.2.1.2, 424.2.15, 425.3.7, 426.6.1, 426.3.6.2, 2113.11.1.2, 2113.15, 2801.1

FBC-M—2010	Florida Building Code, Mechanical	101.4.3, 201.3, 202, 307.9, 406.4.2, 406.6.3, 406.6.5, 409.3, 412.4.6, 414.1.2, 414.1.2.1, 414.1.2.2, 414.3, 415.7.1.4, 415.7.2, 415.7.2.8, 415.7.3, 415.7.4, 415.9.11.1, 416.3, 603.1, 707.2, 716.2.2, 716.5.4, 716.6.1, 716.6.2, 716.6.3, 717.5, 719.1, 903.2.12.1, 904.2.1, 904.11, 908.6, 909.1, 909.10.2, 1014.5, 1016.4.1, 1203.1, 1203.2.1, 1203.4.2, 1203.4.2.1, 1203.5, 1209.3, 2304.5, 3004.3.1

FBC-P 2010	Florida Building Code, Plumbing	101.4.4, 109.3, 201.3, 415.7.4, 419.3.13.1, 421.3.8.1, 424.2.1.2, 424.2.3, 424.2.8.1, 424.2.13.2, 425.4.2, 426.3.1.2, 426.3.2.1, 427.1.4.1.2, 430.6.1, 603.1.2, 717.5, 903.3.5, 1206.3.3, 1503.4, 1503.4.3, 151.4.2, 1514.4.3, 1807.4.3, 2901.1, 2902.1.1, 3305.1

61C-5	Rule 61C, Florida Administrative Code (Bureau of Elevator Safety Regulations),		3001.1

64E	Rule 64E, Florida Administrative Code (Sewage Disposal)	101.4.4, 2901.1

FBC-R—2010	Florida Building Code, Residential	101.2, 308.3, 308.5, 310.1, 1706.1.1

FBC-TPHVHZ—2010	Florida Building Code, Test Protocols for High Velocity Hurricane Zones

RAS 109	1521.18, 1523.6.2.1

RAS 111	1503.3, 1504.5, 1514.2, 1514.2.1, 1514.2.2, 1514.2.3, 1514.2.4, 1514.2.5.2, 1514.3, 1514.4.1.1, 1515.2.3.2, 1517.6.1, 1517.6.2.1, 1517.6.2.3, 1517.6.2.5, 1518.5.3, 1518.6.2, 1518.7.3.4, 1518.9.5, 1519.8, 1519.10, 1519.13, 1523.6.5.2.14, 1519.16.5, 1523.6.5.2.14

RAS 115	1518.7

RAS 117              1519.7, 1519.11, 1520.4, 1520.5, 1521.7.1, 1521.14.3, 1523.6.5.29

RAS 118	1518.8.1

RAS 119	1518.8.1

RAS 120	1518.8.1

RAS 127	1518.8.5, 1518.8.6, 1523.6.5.2, 1523.6.5.2.2.2, 1523.6.5.2.2.3, 1523.6.5.2.3.2, 1523.6.5.2.3.3, 1523.6.5.2.6.2, 1525

RAS 128	1525

RAS 130	1518.10

RAS 133	1519.9.2

RAS 150	1519.1

TAS 100	1523.6.5, 1523.6.5.1, 1523.6.5.2, 1523.6.5.2.4, 1523.6.5.2.4.1, 1523.6.5.2.5, 1523.6.5.2.6, 1523.6.5.2.7

TAS 100A	1523.6.5.2.13

TAS 101	1523.6.5.22.2 1523.6.2.22, 1523.6.5.2.2.3

TAS 102	1523.6.5.2.3, 1523.6.5.2.3.2, 1523.6.5.2.3.3, 1523.6.5.2.6.2, 1523.6.5.2.6.3

TAS 102A	1523.6.5.2.3, 1523.6.5.2.3.2, 1523.6.5.2.3.3, 1523.6.5.2.6.2, 1523.6.5.2.6.3

TAS 103	1523.6.5.2.1

TAS 104	1523.6.5.2.1

TAS 105	1513.1, 1519.7.1, 1521.7, 1521.11

TAS 106	1512.4.2.4, 1523.6.5.2.2.4, 1523.6.5.2.3.4, 1523.6.5.2.6.4

TAS 107	1507.2.10, Table 1507.2.10, 1523.6.5.1

TAS 108	1523.6.5.2.2.1, 1523.6.5.2.2.2, 1523.6.5.2.2.3, 1523.6.5.2.3.1, 1523.6.5.2.3.2, 1523.6.5.2.3.3, 1523.6.5.2.6.1, 1523.6.5.2.6.2, 1523.6.5.2.6.3, 1715.2, 1715.2.2

TAS 110	1515.1.4, 1515.2.5, 1520.1, 1520.4, 1523.1.1, 1523.6.2, 1523.6.2.1, 1523.6.3, 1523.6.5.2.4.1, 1523.6.5.2.6, 1523.6.5.2.7, 1523.6.5.2.8, 1523.6.5.2.9, 1523.6.5.2.12, 1523.6.5.2.13.1, 1523.6.5.2.14, 1523.6.5.2.15, 1523.6.5.2.16, 1523.6.5.2.17

TAS 110A	1523.6.5.2.13

TAS 111A	1523.6.5.2.14

TAS 111B	1523.6.5.2.14

TAS 111C	1523.6.5.2.14

TAS 112	1523.6.5.2

TAS 113	1518.8.1.1

TAS 114	1513.1, 1515.1.1, 1515.2.4, 1517.5.1, 1519.5.1, 1520.4, 1523.6.2, 1523.6.2.1, 1523.6.3, 1523.6.5.2.9, 1523.6.5.2.10, 1523.6.5.2.11

TAS 115	1523.6.5.2.6.3

TAS 116	1513.1, 1523.6.5.2.2.1, 1523.6.5.2.3.1, 1523.6.5.2.6.1

TAS 121	1523.6.5.2.12

TAS 123	1518.8.1.1, 1523.6.5.2.15, 1523.6.5.2.17

TAS 123A	1523.6.5.2.16

TAS 124	1521.10, 1523.6.4

TAS 125	1518.9.1, 1523.6.5.2.4.1

TAS 126	1521.12

TAS 135	1523.6.5.2.6

TAS 201	202, 1609.1.4

TAS 202    1609.1.4, 1008.1.6, 1714.5.2.1, 1714.5.2.1.1, 1714.5.3, 1714.6

TAS 203	202, 1609.1.4

TAS 301	1515.1.3

FM

Factory Mutual

Standards Laboratories Department

1151 Boston-Providence Turnpike

Norwood, MA 02062

Standard reference number	Title			Referenced in section number

Change to read as shown.

4450 (1992) 	Approval Standard for Class 1 Insulated Steel Deck Roofs—with Supplements through July 1992	1504.3.1, 1508.1, 2603.3, 2603.4.1.5, 2612.3.2.5.2

Add to read as shown.

FM

4470 (1992) Approval Standard for Class 1 Roof Covers  .. . .1504.3.1, 1504.7, 1515.1.1

4471		Approval Standard for Class I Panel Roofs			1515.1.1

Add to read as shown.

FRSA

Florida Roofing, Sheet Metal and Air Conditioning Contractors Association

4111 Metric Drive

Winter Park, Florida 32792

Standard reference number	Title			Referenced in section number

FRSA/TRI 07320/8-05   Concrete and Clay Roof Tile Installation Manual, Fourth Edition 1507.3.3, 1507.3.7, 1507.3.8, 1507.3.9

Add to read as shown.

GSA

General Services Administration

1800 F Street, NW

Washington, DC 20405

Standard reference number	Title		Referenced in section number

DD-G-451D (1977)	Glass, Flat and Corrugated for Glazing Mirrors and Other Uses		2411.1.2

ICC

International Code Council

5203 Leesburg Pike, Suite 600

Falls Church, VA 22041

Standard reference number	Title			Referenced in section number

Add to read as shown.

IBHS-05    Guideline for Hurricane Resistant Residential Construction with errata for the

first printing.              1609.1.1, 1609.1.1.1, 2308.2.1

SBCCI SSTD 12—99  Standard for Determining the Wind Resistance from Windborne

Debris 423.25.4, 423.25.4.1, 1606.1.4, 1609.1.4

NFPA

National Fire Protection Association

1 Batterymarch Park

Quincy, MA 02269-9101

Standard reference number	Title			Referenced in section number

Add to read as shown.

10—07		Standard for Portable Fire Extinguisher		419.4.2.10.2, 420.4.2.10.1.2, 423.28.2.14

Change to read as shown.

13—07                Installation of Sprinkler Systems	402.4.6, 431, 704.12, 707.2, 903.1.4, 903.3.1.1, 903.3.2, 903.3.5.1.1, 904.11, 907.8, 1621.3.10.1, 2121.2.12.8, 3104.5, 3104.9

30—08 	Flammable and Combustible Liquids Code			415.3, 423.20.4.1

Revise text to read as follows:

NFPA

32—07 Dry Cleaning Plants  . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .415.6.4

61—08	Prevention of Fires and Dust Explosions in Agricultural and Food Product Facilities	415.7.1,

423.7.7

.

Change to read as shown.

72—07	National Fire Alarm Code	423.7.7, 436.7.1.1, 436.7.1.3, 416.7.2, 436.10.5.1, 436.10.5.2, 505.4, 901.6, 903.4.1, 904.3.5, 907.2, 907.2.1, 907.2.1.1, 907.2.10, 907.2.10.4, 907.2.11.2, 907.2.11.3, 907.2.12.2.3, 907.2.12.3, 907.4, 907.5, 907.9.2, 907.10, 907.14, 907.16, 907.17, 911.1, 1008.1.3.7.4, 3002.8, 3006.5

Add to read as shown.

91—99	Standard for Exhaust Systems for Air Conveying of Vapors, Gases, Mists and NonCombustible Particulate Solids			423.20.4.1

96-04 Standard for Ventilation Control and Fire Protection of Commercial Cooking Operations . . . . . . . . . . . . . . . . . . . . . . . . 436.6.2

96		Standard for Ventilation Control and Fire Protection of Commercial Cooking Operations	436.6.2

99—05  Standard for Health Care Facilities. . . . . . . . . . . . . . . . . . . . . . . . . . . . . 4203.18.1, 420.3.20.2, 420.3.25.1, 419.3.18, 419.3.18.8

99—02		Standard for Health Care Facilities	4203.18.1, 420.3.20.2, 420.3.25.1,419.3.18, 419.3.18.8

Change to read as shown.

101—09 Life Safety Code . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . 420.3.3.6, 423.6.1, 423.14.2.1, 423.27.9.1, 423.27.10.1, 427.2.2.1.1.1, 427.1.4.13.2, 427.1.4.2.13, 427.1.4.1.1.2, 427.1.3.1.1.2, 903.6.2, 1024.6.2

101—09	Life Safety Code	420.3.3.6, 423.6.1, 423.14.2.1, 423.27.9.1, 423.27.10.1, 427.2.2.1.1.1, 427.1.4.13.2, 427.1.4.2.13, 427.1.4.1.1.2, 427.1.3.1.1.2, 903.6.2, 1024.6.2

110—05	Emergency and Standby Power Systems	419.3.18, 419.3.18.8, 420.3.25, 1006.2.33, 421.3.13.1, 4006.2.3.3, 1006.2.3.3, 2702.1

111—05		Stored Electrical Energy Emergency and Standby Power Systems	1006.2.3.3, 2702.1

120—04  Coal Preparation Plants  . . . . . . . . . . . . . . . . . . . . . . . . . . . .415.6.1

259—04		Test Method for Potential Heat of Building Materials	2603.4.1.10, 2603.5.3, 2612.3.2.4.4

NFPA 303 change to read as shown:

NFPA 303 2006

Add to read as shown.

780—04  Installation of Lighting Systems . . .419.3.19, 420.3.26.1, 423.17.7

780—97		Installation of Lighting Systems		419.3.19, 420.3.26.1, 423.17.7

Add to read as shown.

NRCA

National Roofing Contractors Association

10255 W. Higgins Road, Suite 600

Rosemont, IL 60018

Standard reference number	Title			Referenced in section number

P0405	Roofing and Waterproofing Manual, 5th Edition			1513.1

Revise text to read as follows:

APSP

Association of Pool and Spa Professionals

NSPI

National Spa and Pool Institute

[4311]

2111 Eisenhower Avenue

Alexandria, VA 22314

Standard reference number	Title			Referenced in section number

ANSI/NSF	International Standard 50-1996, Circulation System Components and Related Materials for Swimming Pools, Spas/Hot Tubs	424.1.6.5.1, 424.1.6.5.2, 424.1.6.5.16, 424.1.6.5.16.4.2, 424.1.6.5.16.5.2, 424.1.9.2.5.2

ANSI/NSPI 3—99	American National Standard for Permanently Installed Residential Spas	424.2.6.1

ANSI/NSPI 4—99	American National Standard for Aboveground/Onground Residential Swimming Pools					424.2.6.1

ANSI/NSPIAPSP NSPI 5—03 0310 	American National Standard for Residential Inground Swimming Pools	424.2.6.1 [4311]

ANSI/NSPI 6—99  American National Standard for Portable Spas…………………………………………………………………………424.2.6.1

ANSI/NSPI 6—92	American National Standard for Residential Portable Spas		424.2.6.1

[4311]

ANSI/APSP  7—06 American National Standard for Suction Entrapment Avoidance in Swimming Pools, Wading Pools, Spas, Hot Tubs, and Catch Basins…………….……………424.2.6.1, 424.2.6.3, 424.2.6.6

Add to read as shown.

PCA

Portland Cement Association

5420 Old Orchard Road

Skokie, IL 60077

Standard reference number	Title			Referenced in section number

EB008-9	Concrete Masonry Handbook				2119.1.1

Add to read as shown.

RCSC

Research Council on Structural Connections

c/o Stanley D. Lindsey & Assoc. Ltd.

2244 Metro Center Blvd., Suite 208

Nashville, TN 37228-1320

Standard reference number	Title		Referenced in section number

RCSC—88	Specification for Structural Joints Using ASTM A 325 or A 490 Bolts		2214.3

RMI

Rack Manufacturers Institute

8720 Red Oak Boulevard, Suite 201

Charlotte, NC 28217

Standard reference number	Title			Referenced in section number

Change to read as shown.

10100	Manual of Safety Practices - A Code of Practices for the Use of Industrial and Commercial Steel Storage Racks			2214.3

10150	Industrial Steel Storage Racks Manual				2214.3

10083	Specification for the Design, Testing and Utilization of Industrial Steel Storage Racks		2208.1

Add to read as shown.

SDI

Steel Door Institute

c/o Wherry Associates

30200 Detroit Road, Cleveland, Ohio 44145-1967

Standard reference number	Title		Referenced in section number

ANSI A250.13—03	Testing and Rating of Severe Windstorm Resistant Components For Swinging Door Assemblies	1609.1.4.2, 1714.5.3.3.2

Add to read as shown.

SDI

Steel Deck Institute

PO Box 25

Fox River Grove, IL 60021

Standard reference number	Title		Referenced in section number

DDP		Deck Damage and Penetrations				2214.3

DDM—023	Diaphragm Design Manual			2214.3, 2222.4

Number 30 31	Design Manual For Composite Decks, Form Decks and Roof Decks			2214.3

MOC1 2		Manual of Construction with Steel Deck			2214.3

SPD2		Standard Practice Details					2214.3

[3460]

Add to read as shown.

SFPA

Southern Forest Products Association

PO Box 641700

Kenner, LA 70064-1700

Standard reference number	Title		Referenced in section number

2001	Permanent Wood Foundations: Design and Construction Guide (Replaces AF&PA Technical Report No. 7)

Add to read as shown.

SFPE

Society of Fire Protection Engineers

7315 Wisconsin Avenue, Suite 620E

Bethesda, MD 20814

Standard reference number	Title		Referenced in section number

SFPE	Engineering Guide to Performance-Based Fire Protection Analysis and Design of Buildings	104.11

SJI

Steel Joist Institute

3127 10th Avenue, North

Myrtle Beach, SC 29577-6760

Standard reference number	Title		Referenced in section number

Add to read as shown.

SJI—71	Structural Design of Steel Joist Roofs to Resist Ponding Loads, Technical Digest No. 3		2214.3

SJI—88	Vibration of Steel Joist-Concrete Slab Floors, Technical Digest No. 5				2214.3

SJI—03	Structural Design of Steel Joist Roofs to Resist Uplift Loads, Technical Digest No. 6		2214.3

SJI—83	Welding of Open Web Steel, Technical Digest No. 8			2214.3

SJI—87	Handling and Erection of Steel Joists and Joist Girders, Technical Digest No. 9			2214.3

SJI—02	Standard Specifications, Load Tables and Weight Tables for Steel Joists and Joist Girders							1604.3.3, 2206, 2214.3

SJI—03	75-Year Steel Joist Manual					2214.3

Add to read as shown.

SMA

Storage Equipment Manufacturers Association

8720 Red Oak Blvd, Suite 201

Charlotte, NC 28217

Standard reference number	Title		Referenced in section number

ANSI/SMA MH281—97	Specification of Industrial Grade Steel Shelving	2214.3

Add to read as shown.

SMACNA

Sheet Metal and Air Conditioning Contractors' National Association

8224 Old Courthouse Rd.

Vienna, VA 22180

Standard reference number	Title		Referenced in section number

SMACNA—2003	Fire, Smoke and Radiation Damper Installation Guide for HVAC Systems							419.2.1.3, 420.2.3, 421.2.1.3,

#### Metal Roof and Wall Systems . . .RAS 133-9.2

SPRI

Single Ply Roofing Institute

77 Rumford Avenue, Suite 3-B

Walthem, MA 02453

Change to read as shown.

ES-1-03           Wind Design Standard for Edge systems Used with Low Slope Roofing Systems                          1503.3, 1504.5

Add to read as shown.

SSPC

The Society for Protective Coatings

40 24th Street, 6th Floor

Pittsburgh PA 15222-4656

Standard reference number	Title		Referenced in section number

SSPC - Paint 15	Steel Joist Shop Paint					2214.3

SSPC/AISC	Guide to the Shop Painting of Structural Steel		2214.3

Add to read as shown.

STI

Steel Tube Institute

522 Westgate Tower

Cleveland, OH 44116

Standard reference number	Title		Referenced in section number

STI	Manual of Cold-Formed Welded Structural Steel Tube		2214.3

Add to read as shown.

TECO

Timber Company, Inc.

2402 Daniels Street

Madison, WI 53704

Standard reference number	Title			Referenced in section number

TECO PRP-133	Performance Standards and Policies for Structural Use Panels	2314.4.8, 2315.1.2

TPI

Truss Plate Institute

583 D’Onofrio Drive, Suite 200

Madison, WI 53719

Standard reference number	Title			Referenced in section number

Change to read as shown.

TPI 1—2007	National Design Standards for Metal-Plate-Connected Wood Truss Construction	  2303.4, 2306.1, 2314.4.9, 2319.17.2.1.1, 2319.17.2.2.8

Add to read as shown.

TPI/WTCA BCSI -06 Building Component Safety Information Guide to Good Practice for Handling, Installing, Restraining and Bracing of Metal Plate Connected Wood Trusses [A Joint publication with WTCA – Representing the Structural Building Components Industry] 2314.4.9, 2319.17.2.4.1, 2319.17.2.4.3

UL

Underwriters Laboratories

333 Pfingsten Road

Northbrook, IL 60062-2096

Standard reference number	Title			Referenced in section number

Add to read as shown.

9—00		Standard For Fire Tests of Window Assemblies		2121.2.12.8

181—96		Standard for Factory-Made Air Ducts and Air Connectors	419.3.11.6

Change to read as shown.

580—06 	Test for Uplift Resistance of Roof Assemblies—with Revisions through February 1998	1504.3.1, 1504.3.2, 2214.3, 2222.4.6

790—04	Tests for Fire Resistance of Roof Covering Materials—with Revisions through July 1998	1505.1, 1513.1, 1516.1, 1523.1.2, 2314.4.10, 2603.6, 2610.2, 2610.3

Add to read as shown.

924-06		Standard for Emergency Lighting and Power Equipment 	1006.3.6

Change to read as shown.

Underwriters Laboratories Inc. (UL),

333 Pfingsten Road, Northbrook,

IL 60062-2096.

UL 1069, 7th edition…..420.3.25

[4297]

1256—02            Fire Test of Roof Deck Construction—with Revisions through March 2000

1508.1, 2603.3, 2603.4.1.5, 2612.3.2.5.2

Add to read as shown.

2017 -02		Standard for General-Purpose Signaling Devices and Systems 			424.2.17.1.9

2017-04 Standard for General-Purpose Signaling Devices and Systems – with Revisions through October 13, 2009        424.2.17.1.9

[3939]

Add text to read as follows:

UL

1703-02 Flat-Plate Photovoltaic Modules and Panels – with revisions through April 2008….1507.17.1

{4152}

ANSI/UL 2034 - 96, Standard for Single and Multiple Station CO Alarms…………202

UL 2075 - 04, Gas and Vapor Detector Sensor………………………...…………….202

Add to read as shown.

WPPC

Wood Products Promotional Council

c/o Florida Wood Council

1300 Limit Avenue

Mount Dora, FL 32758

Standard reference number	Title		Referenced in section number

WWPC—97	Guide to Wood Construction in High Wind Areas	1609.1.1, 1609.1.1.1

Chapter 36 Florida Fire Prevention Code.  Add to read as shown.

Chapter 36 Florida Fire Prevention Code

3601.1 Scope.  Add to read as shown.

3601.1 Scope.  Provisions of this chapter shall govern the design, construction and arrangement of elements to provide a safe means of egress from buildings and structures and to minimize hazard to life and property due to fire and panic.

3601.2 Add to read as shown.

3601.2  In addition to the provisions of this code, buildings shall comply with the 2004 Florida Fire Prevention Code as adopted by the Florida State Fire Marshal.

Appendix A Employee Qualifications.  Change to read as shown.

Appendix A Employee Qualifications.  Reserved.

Appendix B Board of Appeals.  Change to read as shown.

APPENDIX B

CHAPTER 9B-52 F.A.C.

FLORIDA STANDARD FOR PASSIVE RADON-RESISTANT CONSTRUCTION

See Appendix B

Appendix C Group U – Agricultural Buildings.  Change to read as shown.

APPENDIX C

CHAPTER 9B-53 F.A.C STANDARD FOR MITIGATION OF RADON IN EXISTING BUILDINGS

See Appendix C

Appendix D Fire Districts.  Change to read as shown.

Appendix D Fire Districts Reserved.

Appendix E Supplementary Accessibility Requirements.  Change to read as shown.

APPENDIX E

Chapter 9 B-67 FLORIDA STANDARD FOR RADON-RESISTANT NEW COMMERCIAL CONSTRUCTION

See Appendix E

Appendix F Rodent Proofing.  Change to read as shown.

Appendix F Rodent Proofing.  Reserved.

Appendix G Flood-Resistant Construction.  Change to read as shown.

Appendix G Flood-Resistant Construction.  Reserved.

Appendix H Signs. Change to read as shown.

Appendix H Signs.  Reserved.

Appendix I Patio Covers.  Change to read as shown.

Appendix I Patio Covers.  Reserved.

Appendix J Grading.  Change to read as shown.

Appendix J Grading.  Reserved

Appendix K Administrative Provisions.  Change to read as follows.

Appendix K  Administrative Provisions. Reserved.