**7th Edition (2020) Florida Building Code - Energy Conservation**

**Commercial Provisions**

**Chapter 4 [CE] COMMERCIAL ENERGY EFFICIENCY**

Revise Table C403.2.3(1) to read as follows:

**TABLE C403.2.3(1)**

**MINIMUM EFFICIENCY REQUIREMENTS:**

**ELECTRICALLY OPERATED UNITARY AIR CONDITIONERS AND CONDENSING UNITS**

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| **EQUIPMENT TYPE** | **SIZE CATEGORY** | **HEATING SECTION TYPE** | **SUBCATEGORY OR RATING CONDITION** | **MINIMUM EFFICIENCY** | **TEST PROCEDUREa** |
| Air conditioners, air cooled | < ~~6~~45,000 Btu/hb | All | Split System, single phaseb | 14.0 SEER  before 1/1/2023  14.3 SEER2  after 1/1/2023 | AHRI 210/240 – 2017  before 1/1/2023  AHRI 210/240 – 2023  after 1/1/2023 |
| ≥ 45,000 Btu/hb and  < 65,000 Btu/hb | 14.0 SEER  before 1/1/2023  13.8 SEER2  after 1/1/2023 |
| < 65,000 Btu/hb | Single Package, single phaseb | 14.0 SEER |
| Through-the-wall (air cooled) | ≤30,000 Btu/hb | All | Split system, three phase and US applications single phaseb | 12.0 SEER |
| Single Package, three phase and US applications single phaseb | 12.0 SEER |
| Small-duct high-velocity (air cooled) | < 65,000 Btu/hb | All | Split system, single phaseb | 12.0 SEER |
| Air conditioners, air cooled |  65,000 Btu/h and  < 135,000 Btu/h | Electric Resistance (or None) | Split System and Single Package | 11.2 EER  12.9 IEER | AHRI 340/360 |
| All other | Split System and  Single Package | 11.0 EER  12.7 IEER |
|  135,000 Btu/h and  < 240,000 Btu/h | Electric Resistance (or None) | Split System and  Single Package | 11.0 EER  12.4 IEER |
| All other | Split System and  Single Package | 10.8 EER  12.2 IEER |
|  240,000 Btu/h and  < 760,000 Btu/h | Electric Resistance (or None) | Split System and  Single Package | 10.0 EER  11.6 IEER |
| All other | Split System and  Single Package | 9.8 EER  11.4 IEER |
|  760,000 Btu/h | Electric Resistance (or None) | Split System and  Single Package | 9.7 EER  11.2 IEER |
| All other | Split System and Single Package | 9.5 EER  11.0 IEER |

*(continued)*

**C-32 FLORIDA BUILDING CODE — ENERGY CONSERVATION, 7th EDITION (2020)**

**COMMERCIAL ENERGY EFFICIENCY**

**TABLE C403.2.3(1)—continued MINIMUM EFFICIENCY REQUIREMENTS:**

**ELECTRICALLY OPERATED UNITARY AIR CONDITIONERS AND CONDENSING UNITSc**

|  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| **EQUIPMENT TYPE** | **SIZE CATEGORY** | **HEATING SECTION TYPE** | **SUB-CATEGORY OR RATING CONDITION** | **MINIMUM EFFICIENCY** | **TEST PROCEDUREa** |
|  | < 65,000 Btu/hb | All | Split System and | 12.1 EER | AHRI |
|  | Single Package | 12.3 IEER | 210/240 |
| Air conditioners, water cooled |  65,000 Btu/h and  < 135,000 Btu/h | Electric Resistance (or None) | Split System and Single Package | 12.1 EER  13.9 IEER | AHRI 340/360 |
| All other | Split System and Single Package | 11.9 EER  13.7 IEER |
|  135,000 Btu/h and  < 240,000 Btu/h | Electric Resistance (or None) | Split System and Single Package | 12.5 EER  13.9 IEER |
| All other | Split System and Single Package | 12.3 EER  13.7 IEER |
|  240,000 Btu/h and  < 760,000 Btu/h | Electric Resistance (or None) | Split System and Single Package | 12.4 EER  13.6 IEER |
| All other | Split System and Single Package | 12.2 EER  13.4 IEER |
|  | Electric Resistance | Split System and | 12.2 EER |
|  760,000 Btu/h | (or None) | Single Package | 13.5 IEER |
| All other | Split System and | 12.0 EER |
|  | Single Package | 13.3 IEER |
| Air conditioners, evaporatively cooled | < 65,000 Btu/hb | All | Split System and | 12.1 EER | AHRI |
| Single Package | 12.3 IEER | 210/240 |
|  65,000 Btu/h and  < 135,000 Btu/h | Electric Resistance (or None) | Split System and Single Package | 12.1 EER  12.3 IEER | AHRI 340/360 |
| All other | Split System and Single Package | 11.9 EER  12.1 IEER |
|  135,000 Btu/h and  < 240,000 Btu/h | Electric Resistance (or None) | Split System and Single Package | 12.0 EER  12.2 IEER |
| All other | Split System and Single Package | 11.8 EER  12.0 IEER |
|  240,000 Btu/h and  < 760,000 Btu/h | Electric Resistance (or None) | Split System and Single Package | 11.9 EER  12.1 IEER |
| All other | Split System and Single Package | 11.7 EER  11.9 IEER |
|  | Electric Resistance | Split System and | 11.7 EER |
|  760,000 Btu/h | (or None) | Single Package | 11.9 IEER |
| All other | Split System and | 11.5 EER |
|  | Single Package | 11.7 IEER |
| Condensing units,  air cooled |  135,000 Btu/h |  |  | 10.5 EER | AHRI 340/360 |
| 11.8 IEER |
| Condensing units,  water cooled |  135,000 Btu/h |  |  | 13.5 EER |
| 14.0 IEER |
| Condensing units,  evaporatively cooled |  135,000 Btu/h |  |  | 13.5 EER |
| 14.0 IEER |

For SI: 1 British thermal unit per hour = 0.2931 W.

1. Chapter 6 contains a complete specification of the referenced standards, which include test procedure, including the reference year version of the test procedure.
2. Single-phase, US air-cooled air conditioners less than 65,000 Btu/h are regulated ~~by NAECA~~as consumer products by the US Department of Energy Code of Federal Regulations DOE 10 CFR 430. SEER and SEER2 values for single-phase products are set by the US Department of Energy~~SEER values are those set by NAECA.~~

**FLORIDA BUILDING CODE — ENERGY CONSERVATION, 7th EDITION (2020) C-33**