2010 Florida Building Code, Energy Conservation

Glitch Supplement

Chapter 1 - ADMINISTRATION

101.4.7 .1 Replacement HVAC equipment – Change to read as shown.

101.4.7.1 Replacement HVAC equipment

101.4.7.1.1 Duct sealing upon equipment replacement. [No change.] 
101.4.7.1.2 Replacement equipment sizing. [No change.]
101.4.7.1.3 Existing equipment efficiencies. Existing cooling and heating equipment need not meet the minimum equipment efficiencies of Sections 403.6.2.2 or 403.6.2.3 except to preserve the original approval or listing of the equipment.

EN4798

101.5 Compliance – Change to read as shown.

101.5 Compliance. Residential buildings less than 4 stories not more than three stories above grade in height shall meet the provisions of Chapter 4. Commercial buildings and residential buildings greater than 3 stories shall meet the provisions of Chapter 5.

[No change to the remaining text]

EN4645

103.2 Information on construction documents - Change to read as shown.

103.2.1 Code demonstration forms. See Table 103.2.1.

103.2.1.1 Residential ≤ 3 stories

103.2.1.1.1 Building thermal envelope alternative. An accurately completed Residential Building Form 402 or FlaResCheck printout shall be submitted to the building official for to demonstrate code compliance by this method.

103.2.1.1.2 Simulated performance alternative. An accurately completed Residential Building Form 405 (generated by the EnergyGauge USA Fla/Res computer program Commission approved software) shall be submitted to the building official to demonstrate code compliance by Section 405.

103.2.1.2 Commercial and residential >3 stories.

103.2.1.2.1 Building thermal envelope alternative. An accurately completed Commercial Building Form 502 or FlaComCheck printout shall be submitted to the building official for to demonstrate code compliance by this method.

103.2.1.2.2 Simulated performance alternative, commercial and high-rise residential. An accurately completed Commerical Building Form 506 (generated by the EnergyGauge Summit Fla/Com computer program Commission approved software ) demonstrating that code compliance has been achieved shall be submitted to the building official for compliance by Section 506.

EN4646

TABLE 103.2.1

INDEX TO CODE COMPLIANCE FORMS

| FORM | WHERE FOUND |
| --- | --- |
| Chapter 4 compliance Form 402 Alternate Form 402 (FlaResCheck printout) Form 405 (Commission approved software printout) (EnergyGauge USA Fla/Res) Chapter 5 compliance Form 502 Alternate Form 502 (Fla/Com prescriptive printout) Form 506 (Commission approved software printout) (EnergyGauge Summit Fla/Com) | Appendix C Online: www.energygauge.com Online: www.energygauge.com Appendix C Online: www.energygauge.com Online: www.energygauge.com |

EN4766  (related to 4646)

110.0 Reporting to entity representing the  Florida Building Commission the Department of Community Affairs.    A reporting form shall be submitted to the local building department by the owner or owner’s agent with the submittal certifying compliance with this code. Reporting forms shall be a copy of the front page of the form applicable for the code chapter under which compliance is demonstrated.

110.1 Reporting schedule. It shall be the responsibility of the local building official to forward the reporting section of the proper form to the entity representing the Florida Building Commission Department of Community Affairs on a quarterly basis as per the reporting schedule in Table 110.1.

[No change to Table 110.1.]

COMMENT AFTER GLITCH

Chapter 2 – DEFINITIONS

AIR CONDITIONING – add to read as shown. AIR CONDITIONING. The treatment of air so as to control simultaneously the temperature, humidity, cleanness and distribution of the air to meet the requirements of a conditioned space.

EN4647

AIR DISTRIBUTION SYSTEM – add to read as shown.

AIR DISTRIBUTION SYSTEM. Any system of ducts, plenums and air-handling equipment that circulates air within a space or spaces and includes systems made up of one or more air-handling units.

EN4648

Integrated Energy Efficiency Ratio (IEER):    add to read as shown.

Integrated Energy Efficiency Ratio (IEER): a single-number figure of merit expressing cooling part-load EER efficiency for commercial unitary air-conditioning and heat pump equipment on the basis of weighted operation at various load capacities for the equipment.

EN4825

WATER HEATER – add to read as shown.

WATER HEATER. Any heating appliance or equipment that heats potable water and supplies such water to the potable hot water distribution system.

EN4649

Chapter 3 – DESIGN CRITERIA

Table 301.1 – Change to read as shown.

TABLE 301.1

CLIMATE ZONES, MOISTURE REGIMES, AND WARM-HUMID DESIGNATIONS

BY STATE, COUNTY AND TERRITORY

Key: A – Moist, Asterisk (*) indicates a warm-humid location.

[No change to Table 301.1 except delete asterisks from all county climate zone columns]

EN4650

304.1 Building material thermal properties, general. – Change to read as shown.

304.1.1 Commerical and residential high rise.  R-values for building materials used to demonstrate code compliance with Chapter 5 shall be taken from ASHRAE 90.1 Normative Appendix A, from the EnergyGauge Summit Fla/Com computer program, from manufacturer’s product literature or from other nationally recognized engineering sources. Assembly U-factor calculations shall follow the procedure(s) detailed in section 304.3 or be tested in accordance with procedures(s) described in section 304.2.

Concrete block R-values shall be calculated using the isothermal planes method or a two-dimensional calculation program, thermal conductivities from ASHRAE 90.1 Normative Appendix A, from the EnergyGauge Summit Fla/Com program and dimensions from ASTM C90. The parallel path calculation method is not acceptable.

Exception: R-values for building materials or thermal conductivities determined from testing in accordance with Section 304.2.

EN4651

Section 304.3.1.4 – change to read as shown.

304.3.1.4 The R-value for cavity airspaces included in the EnergyGauge Summit Fla/Com program are shall be taken from ASHRAE 90.1 Normative Appendix A. No credit shall be given for airspaces in cavities that contain any insulation or less than 0.5 inch (12.7 mm). The values for 3.5 inch (84 mm) cavities shall be used for cavities of that width and greater.

EN4652, EN4767

Section 304.3.2.1 – change to read as shown.

304.3.2.1 Pre-calculated assembly U-factors, C-factors, F-factors, or heat capacities. The U-factors, C-factors, F-factors, and heat capacities for typical construction assemblies included in the EnergyGauge Summit Fla/Com computer program are taken from ASHRAE 90.1 Normative Appendix A. These values shall be used for all calculations unless otherwise allowed by applicant-determined assembly U-factors, C-factors, F-factors, or heat capacities. Interpolation between values for rated R-values of insulation, including insulated sheathing is allowed; extrapolation beyond values in the ASHRAE 90.1 Normative Appendix A tables is not allowed.

EN4768 (related to 4767)

Chapter 4 – RESIDENTIAL ENERGY EFFICIENCY

Section 402.1.1 – change to read as shown: 402.1.1 Component Insulation and fenestration criteria. The building thermal envelope and air distribution system shall meet the requirements of Table 402.1.1 based on the climate zone specified in Chapter 3.

EN4844, COMMENT AFTER GLITCH

Table 402.1.1.3 – change to read as shown.

TABLE 402.1.1.3

EQUIVALENT U-FACTORSa,f,g

[No change to table except footnotes b, d and f as shown below.]

b. When more than half the insulation is on the exterior interior, the mass wall U-factors shall be a maximum of 0.165.

COMMENT AFTER GLITCH

d. Foundation U-factor requirements shown in Table 402.1.1.3 include wall construction and interior air films but exclude soil conductivity and exterior air films.  U-factors for determining code compliance in accordance with Section 402.1.1.3 2 (total UA alternative) of Section 405 (Simulated Performance Alternative) shall be modified to include soil conductivity and exterior air films.

f. Limitations to compliance by Section 402 found in Section 402.1.2 shall be met.

402.1.1.2.U-factor alternative. An assembly with a U-factor equal to or less than that specified in Table 402.1.1.3 shall be permitted as an alternative to the corresponding component R-value in Table 402.1.1. All other prescriptive criteria of Table 402.1.1, the prescriptive criteria in Section 402.1.2.4 5 and footnotes to Table 402.1.1.3 shall be met.

402.1.1.3  Total UA alternative. If the total building thermal envelope UA (sum of U-factor times assembly area) is less than or equal to the total UA resulting from using the U-factors in Table 402.1.1.3 (multiplied by the same assembly area as in the proposed building), the building shall be considered in compliance with Table 402.1.1.3. All other prescriptive criteria of Table 402.1.1, the prescriptive criteria in Section 402.1.2.4 5 and footnotes to Table 402.1.1.3 shall be met. The UA calculation shall be done using a method consistent with the ASHRAE Handbook of Fundamentals and shall include the thermal bridging effects of framing materials. The SHGC requirements of Table 402.1.1 shall be met in addition to UA compliance.

EN4847

Section 402.1.2.5 – change section number as shown.

402.1.2.4 5 Equipment efficiencies.  [No change to text]

EDITORIAL

402.5 – Maximum fenestration SHGC (Mandatory) -  change to read as shown.

402.5 Maximum fenestration SHGC (Mandatory). The area-weighted average maximum fenestration SHGC permitted using trade-offs from Section 405 in Zones 1 through 3 shall be 0.50.

Exception:  If the window area-weighted average overhang depth for the entire dwelling unit is 4.0 feet or greater, the area-weighted average maximum SHGC requirement of 0.50 does not need to be met.

EN4653

403.2.2.1 Duct tightness – change to read as shown:

403.2.2.1 Duct tightness.  Duct tightness shall be verified by testing to ASHRAE Standard 152. All ducts and air handlers shall be either located in conditioned space or tested by a Class 1 BERS rater to be “substantially leak free” by one of the following methods:

1. Post construction test: Leakage to outdoors shall be less than or equal to 3 8 cfm (84.9 226.5 L/min) per 100 ft2 (9.29 m2) of conditioned floor area or a total leakage less than or equal to 9 12 cfm (254 12 L/min) per 100 ft2 (9.29 m2) of conditioned floor area when tested at a pressure differential of 0.1 inches w.g. (25 Pa) across the entire system, including the manufacturer’s air handler enclosure. All register boots shall be taped or otherwise sealed during the test. 2. Rough-in test: Total leakage shall be less than or equal to 4 6 cfm (113.3 169.9 L/min) per 100 ft2 (9.29 m2) of conditioned floor area when tested at a pressure differential of 0.1 inches w.g. (25 Pa) across the roughed-in system, including the manufacturer’s air handler enclosure. All register boots shall be taped or otherwise sealed during the test. If the air handler is not installed at the time of the test, total leakage shall be less than or equal to 2 4 cfm (56.3 113.3 L/min) per 100 ft2 (9.29 m2) of conditioned floor area. Exception: Duct testing is not mandatory for buildings complying by Section 405 of this code. COMMENTS AFTER GLITCH

Section 403.6.2.2 – change to read as shown:

403.6.2.2 Minimum efficiencies for cooling equipment.  Cooling equipment installed in residential units shall meet the minimum efficiencies of Tables 503.2.3(1) through 503.2.3(3) and 503.2.3(6) through 503.2.3(8) in Chapter 5 of this code for the type of equipment installed. Equipment used to provide water heating functions as part of a combination system shall satisfy all stated requirements for the appropriate space heating or cooling category.

Exception:  Existing mechanical systems undergoing alteration need not meet the minimum equipment efficiencies of this section except to preserve the original approval or listing of the equipment.

EN4798

Section 403.9 – change to read as shown:

403.9 Swimming pPools, inground spas, and portable spas (Mandatory). The energy requirements for residential pools and inground spas shall be as specified in Sections 403.9.1 through 403.9.4 and ANSI/APSP-15.  The energy requirements for portable spas shall be in accordance with Section 403.9.5 and ANSI/APSP-14. Pools shall be provided with energy-conserving measures in accordance with Sections 403.9.1 through 403.9.43 and compliance criteria found in Appendix D—Florida Standards, Florida Standard No. 1 2 (FL-1 2), Florida regulatory requirements for energy efficiency for residential inground swimming pools and spas, and Florida Standard No. 2 3  (FL-2 3), Florida regulatory requirements for portable spa energy efficiency.

403.9.1 Pool and spa heaters. All pool heaters shall be equipped with a readily accessible on-off switch that is mounted outside the heater to allow shutting off the heater without adjusting the thermostat setting.

403.9.1.1 Gas and oil-fired pool and spa heaters. All gas- and oil-fired pool and spa heaters shall have a minimum thermal efficiency of 78 percent for heaters manufactured before April 16, 2013 and not less than 82 percent for heaters manufactured on or after April 16, 2013 when tested in accordance with ANSI Z 21.56.  Pool heaters fired by natural gas shall not have continuously burning pilot lights.

403.9.1.2 Heat pump pool heaters.  Heat pump pool heaters shall have a minimum COP of 4.0 when tested in accordance with AHRI 1160, Table 2, Standard Rating Conditions-Low Air Temperature. A test report from an independent laboratoryies is required to verify procedure compliance.

403.9.2 Time switches. Time switches shall be installed to control on swimming pool heaters and pumps that can automatically turn the heaters and pumps off and on according to a preset  schedule.

Exceptions:

1. Where public health standards require 24-hour pump operation.

2. Where pumps are required to operate solar- and waste-heat-recovery pool heating systems.

3. Where pumps are powered exclusively from on-site renewable generation.

403.9.3 Covers. Heated swimming pools and  inground permanently installed spas shall be equipped with a vapor-retardant cover on or at the water surface or a liquid cover or other means proven to reduce heat loss.

Exception: Outdoor pools deriving over 70 percent of the energy for heating from site-recovered energy or solar energy source computed over an operating season.

403.9.4 Residential pool pumps and pump motors. Pool filtration pump motors shall meet the following requirements, along with the compliance criteria provided for in FL-1 2, Appendix D.

403.9.4.1 Pool pump motors. Pool pump motors shall meet the following criteria:

1. Pool pump motors shall not be split-phase, shaded-pole or capacitor start-induction run types.

2. Pool pumps and pool pump motors with a total horsepower (HP) of = 1 HP shall have the capability of operating at two or more speeds. The low speed shall have a rotation rate of no more than ½ of the motor’s maximum rotation rate.

3. Pool pumps motor controls shall have the capability of operating the pool pump at a minimum of two speeds. The default circulation speed shall be the residential filtration speed, with a higher speed override capability for a temporary period not to exceed one normal cycle or 24 hours, whichever is less.

Exception:  Solar pool heating systems shall be permitted to run at higher speeds during periods of usable solar heat gain.

403.9.5 Portable spa standby power. Portable electric spa standby power shall not be greater than 5 (V2/3) watts where V = the total volume, in gallons, when spas are measured in accordance with the spa industry test protocol provided in ANSI/APSP-14 FL-2, Appendix D.

EN4869, 4790

405.4.3 Additional documentation. The code official shall require the following documents: 1.2. An EPL Display Card signed by the builder providing the building component characteristics of the proposed design shall be provided to the purchaser of the home at time of title transfer. 2. 3. Documentation of the component efficiencies used in the software calculations for the proposed design.

EN4654

Chapter 5 – COMMERCIAL ENERGY EFFICIENCY

502.1 General (Prescriptive).

502.1.1 Insulation and fenestration criteria.

502.1.1.1 Shell buildings, renovations and alterations. The building thermal envelope shall meet the requirements of Table 502.1.1.1(1) or Table 502.1.1.1(2), as applicable. See Section 101.4.3.

502.1.1.1.2 U-factor alternative. An assembly with a U-factor, C-factor, or F-factor equal or less than that specified in Table 502.1.1.1 Tables 502.1.1.1(1) or Table 502.1.1.1(2) shall be permitted as an alternative.

EN4745

Section 502.2 - Change to read as shown.

502.2 Specific insulation requirements (Prescriptive).

502.2.1 Roof assembly.

502.2.1.1 Shell buildings, renovations and alterations. The sum of the installed insulating material installed R-Values shall meet the minimum thermal resistance requirements as specified in Table 502.1.1.1 Table 502.1.1.1(1) or Table 502.1.1.1(2).

502.2.1.2 – 502.2.1.3 [No change to text]

EN4746

502.2.2 Walls. –  change to read as shown.

502.2.2.1 Shell buildings, renovations and alterations.

502.2.2.1.1 Above-grade walls. The minimum thermal resistance (R-value) of the insulating material(s) installed in the wall cavity between the framing members and continuously on the walls shall be as specified in Table 502.1.1.1 Table 502.1.1.1(1) or Table 502.1.1.1(2), based on framing type and construction materials used in the wall assembly. The R-value of integral insulation installed in concrete masonry units (CMU) shall not be used in determining compliance with Table 502.1.1.1 Table 502.1.1.1(1) or Table 502.1.1.1(2).

502.2.2.1.2 Below-grade walls. The minimum thermal resistance (R-value) of the insulating material installed in, or continuously on, the below-grade walls shall be as specified in Table 502.1.1.1 Tables 502.1.1.1(1) or Table 502.1.1.1(2), and shall extend to a depth of 10 feet (3048 mm) below the outside finished ground level, or to the level of the floor, whichever is less.

EN4747

502.2.3 Floors. –   Change to read as shown.

502.2.3.1 Shell buildings, renovations and alterations.

502.2.3.1.1 Floors over outdoor air or unconditioned space. The minimum thermal resistance (R-value) of the insulating material installed either between the floor framing or continuously on the floor assembly shall be as specified in Table 502.1.1.1 Table 502.1.1.1(1) or Table 502.1.1.1(2), based on construction materials used in the floor assembly.

502.2.3.1.2 Slabs on grade. The minimum thermal resistance (R-value) of the insulation around the perimeter of heated slab-on-grade floors shall be R-7.5 for 12 inches below the top of the slab or to the top of the footing, whichever is less, or downward to at least the bottom of the slab and then horizontally to the interior or exterior for the total distance.

EN4748

502.2.4 Doors. – Change to read as shown.

502.2.4.1 Shell buildings, renovations and alterations.

502.2.4.1 Opaque doors. Opaque doors (doors having less than 50 percent glass area) shall meet the applicable requirements for doors as specified in Table 502.1.1.1 Table 502.1.1.1(1) or Table 502.1.1.1(2).

EN4749

502.2.5 Fenestration (Prescriptive).         Change to read as shown.

502.2.5.1 Shell buildings, renovations and alterations. Fenestration shall comply with Table 502.1.1.1 Table 502.1.1.1(1) or Table 502.1.1.1(2).

502.2.5.1.1 Maximum area. The vertical fenestration area (not including opaque doors) shall not exceed the percentage of the gross wall area specified in Table 502.1.1.1 Table 502.1.1.1(1) or Table 502.1.1.1(2). The skylight area shall not exceed 3 percent of the gross roof area.

502.2.5.1.2 Maximum U-factor and SHGC. For vertical fenestration, the maximum U-factor and solar heat gain coefficient (SHGC) shall be as specified in Table 502.1.1.1 Table 502.1.1.1(1) or Table 502.1.1.1(2), based on the window projection factor. For skylights, the maximum U-factor and solar heat gain coefficient (SHGC) shall be as specified in Table 502.1.1.1 Table 502.1.1.1(1) or Table 502.1.1.1(2). The window projection factor shall be determined in accordance with Equation 5-1.

PF = A/B             (Equation 5-1)

where:

PF = Projection factor (decimal).

A = Distance measured horizontally from the furthest continuous extremity of any overhang, eave, or permanently attached shading device to the vertical surface of the glazing.

B = Distance measured vertically from the bottom of the glazing to the underside of the overhang, eave, or permanently attached shading device.

Where different windows or glass doors have different PF values, they shall each be evaluated separately, or an area-weighted PF value shall be calculated and used for all windows and glass doors.

EN4750

Section 503.2.3 – Change to read as shown:

503.2.3 HVAC equipment performance requirements. Equipment shall meet the minimum efficiency requirements of Tables 503.2.3(1), 503.2.3(2), 503.2.3(3), 503.2.3(4), 503.2.3(5), 503.2.3(6), and 503.2.3(7), and 503.2.3(8) and 503.2.3(9) when tested and rated in accordance with the applicable test procedure. The efficiency shall be verified through certification under an approved certification program or, if no certification program exists, the equipment efficiency ratings shall be supported by data furnished by the manufacturer. Where multiple rating conditions or performance requirements are provided, the equipment shall satisfy all stated requirements. Where components, such as indoor or outdoor coils, from different manufacturers are used, calculations and supporting data shall be furnished by the designer that demonstrates that the combined efficiency of the specified components meets the requirements herein.

Exception: Water-cooled centrifugal water-chilling packages listed in Table 503.2.3(7) not designed for operation at AHRI Standard 550/590 test conditions of 44°F (7°C) leaving chilled water temperature and 85°F (29°C) entering condenser water temperature with 3 gpm/ton (0.054 I/s.kW) condenser water flow shall have maximum full load and NPLV ratings adjusted using the following equations:

Adjusted maximum full load kW/ton rating = [full load kW/ton from Table 503.2.3(7)]/Kadj

Adjusted maximum NPLV rating = [IPLV from Table 503.2.3(7)]/Kadj

where:

Kadj = 6.174722 - 0.303668(X) + 0.00629466(X)2 - 0.000045780(X)3

X =DTstd + LIFT

DTstd = {24+[full load kW/ton from Table 503.2.3(7)] × 6.83}/Flow

Flow = Condenser water flow (GPM)/Cooling Full Load Capacity (tons)

LIFT = CEWT – CLWT (°F)

CEWT = Full Load Condenser Entering Water Temperature (°F)

CLWT = Full Load Leaving Chilled Water Temperature (°F)

The adjusted full load and NPLV values are only applicable over the following full-load design ranges:

Minimum Leaving Chilled Water Temperature: 38°F (3.3°C)

Maximum Condenser Entering Water Temperature: 102°F (38.9°C)

Condensing Water Flow: 1 to 6 gpm/ton 0.018 to 0.1076 1/s . kW) and X  =39 and =60

Chillers designed to operate outside of these ranges or applications utilizing fluids or solutions with secondary coolants (e.g., glycol solutions or brings) with a freeze point of 27oF (-2.8oC) or lower for freeze protection are not covered by this code.

EN4826

Table 503.2.3(1) and Table 503.2.3(2) – change to read as shown.

TABLE 503.2.3(1)

UNITARY AIR CONDITIONERS AND CONDENSING UNITS,

ELECTRICALLY OPERATED,

MINIMUM EFFICIENCY REQUIREMENTS

| Equipment Type | Size Category | Sub-Category or Rating Condition | Minimum Efficiencyb | Test Procedurea |
| --- | --- | --- | --- | --- |
| Air Conditioners, Air Cooled | <65,000 Btu/hd | Split System | 13.0 SEER | AHRI 210/240 |
|  |  | Single Package | 13.0 SEER |  |
|  | ≥65,000 Btu/h and <135,000 Btu/h | Split System and Single Package | 11.2 EERc 11.4 IEERc |  |
|  | ≥135,000 Btu/h and <240,000 Btu/h | Split System and Single Package | 11.0 EERc 11.2 IEERc | AHRI 340/360 |
|  | ≥240,000 Btu/h and <760,000 Btu/h | Split System and Single Package | 10.0 EERc, 10.1 IEERc 9.7 IPLVg |  |
|  | ≥760,000 Btu/h | Split System and Single Package | 9.7 EERc, 9.8 IEERc 9.4 IPLVc |  |
| Through-the Wall, Air-cooled | <30,000 Btu/hd | Split System | 12.0 SEER | AHRI 210/240 |
|  |  | Single Package | 12.0 SEER |  |
| Space constrained products, air conditioners | <65,000 Btu/hc | Split system or Single Package | 12.0 SEERe |  |
| Air Conditioners, Water and Evaporatively Cooled | <65,000 Btu/h | Split System and Single Package | 12.1 EER 12.3 IEER | AHRI 210/240 |
|  | ≥65,000 Btu/h and <135,000 Btu/h | Split System and Single Package | 11.5 EERc 11.7 IEERc |  |
|  | ≥135,000 Btu/h and <240,000 Btu/h | Split System and Single Package | 11.0 EERc 11.2 IEERc | AHRI 340/360 |
|  | ≥240,000 Btu/h | Split System and Single Package | 11.05 EERc 11.1 IEERc |  |
| Condensing Units, Air Cooled | =135,000 Btu/h |  | 10.1 EER, 11.2 IPLV | AHRI 365 |
| Condensing Units, Water or Evaporatively Cooled | =135,000 Btu/h |  | 13.1 EER, 13.1 IPLV |  |

For SI:   1 British thermal unit per hour = 0.2931 W.

a Chapter 6 contains a complete specification of the reference test procedure, including the referenced year version of the test procedure.

b IPLVs and part load rating conditions are only applicable to equipment with capacity modulation.

c Deduct 0.2 from the required EERs and IEERs IPLVs for units with a heating section other than electric resistance heat.

dSingle-phase, air-cooled air-conditioners <65,000 Btu/h are regulated by NAECA. SEER values are those set by NAECA.

eAs granted by U.S. Department of Energy letter of exception, specific to individual companies, SDHV products without a letter of exception shall have the same efficiency as air-cooled air-conditioners.

EN4825

Table 503.2.3(2) – Change to read as shown:

TABLE 503.2.3(2)

UNITARY AND APPLIED HEAT PUMPS, ELECTRICALLY OPERATED,

MINIMUM EFFICIENCY REQUIREMENTS

| Equipment Type | Size Category | Sub-Category or Rating Condition | Minimum Efficiencyb | Test Procedurea |
| --- | --- | --- | --- | --- |
| Air Cooled (Cooling mode) | <65,000 Btu/hd | Split System | 13.0 SEER | AHRI 210/240 |
|  |  | Single Package | 13.0 SEER |  |
|  | ≥65,000 Btu/h and <135,000 Btu/h | Split System and Single Package | 11.0 EERc 11.2 IEERc |  |
|  | ≥135,000 Btu/h and <240,000 Btu/h | Split System and Single Package | 10.6 EERc 10.7 IEERc | AHRI 340/360 |
|  | ≥240,000 Btu/h | Split System and Single Package | 9.5 EERc, 9.6 IEERc 9.2 IPLVc |  |
| Through-the Wall, Air-cooled cooling mode | <30,000 Btu/hd | Split System | 12.0 SEER | AHRI 210/240 |
|  |  | Single Package | 12.0 SEER |  |
| Space constrained products, heat pumps, cooling mode | <65,000 Btu/hc | Split system or Single Package | 12.0 SEERe |  |
| Space constrained products, heat pumps, heating mode | <65,000 Btu/h | Split system or Single Package | 7.4 HSPF |  |
| Air Water Source (Cooling Mode) | <17,000 Btu/h | 86oF entering water | 11.2 EER | AHRI/ASHRAE 13256-1 |
|  | ≥17,000 Btu/h and <135,000 Btu/h | 86oF entering water | 12.0 EER |  |
| Groundwater Source (cooling mode) | <135,000 Btu/h | 59oF entering water | 16.2 EER |  |
| Ground source (Cooling mode) | <135,000 Btu/h | 77oF entering water | 13.4 EER |  |
| Air cooled (Heating mode) | <65,000 Btu/hd (Cooling capacity) | Split system | 7.7 HSPF | AHRI 210/240 |
|  |  | Single package | 7.7 HSPF |  |
|  | ≥65,000 Btu/h and < 135,000 Btu/h (Cooling capacity) | 47oF db/43oF wb Outdoor air | 3.3 COP |  |
|  | ≥135,000 Btu/h (Cooling capacity) | 47oF db/43oF wb Outdoor air | 3.2 COP | AHRI 340/360 |
| Through the wall (Air cooled, heating mode) | <30,000 Btu/h | Split system | 7.4 HSPF | AHRI 210/240 |
|  |  | Single package | 7.4 HSPF |  |
| Water source (Heating mode) | <135,000 Btu/h (Cooling capacity) | 68oF entering water | 4.2 COP | AHRI/ASHRAE 13256-1 |
| Groundwater source (Heating mode) | <135,000 Btu/h (Cooling capacity) | 50oF entering water | 3.6 COP | AHRI/ASHRAE 13256-1 |
| Ground source (Heating mode) | <135,000 Btu/h (Cooling capacity) | 32oF entering water | 3.1 COP | AHRI/ASHRAE 13256-1 |

For SI: oC – [(oF) – 32]/1.8 British thermal unit per hour – 0.2931 W.   db = dry-bulb temperature, oF      wb = wet-bulb temperature, oF

a Chapter 6 contains a complete specification of the reference test procedure, including the referenced year version of the test procedure.

b IPLVs and part load rating conditions are only applicable to equipment with capacity modulation.

c Deduct 0.2 from the required EERs and IEERs IPLVs for units with a heating section other than electric resistance heat.

dSingle-phase, air-cooled air-conditioners <65,000 Btu/h are regulated by NAECA. SEER values are those set by NAECA.

eAs granted by U.S. Department of Energy letter of exception, specific to individual companies, SDHV products without a letter of exception shall have the same efficiency as air-cooled air-conditioners.

EN4825

TABLE 503.2.3(3) – change to read as shown.

TABLE 503.2.3(3)

PACKAGED TERMINAL AIR CONDITIONERS AND PACKAGED TERMINAL HEAT PUMPS,

SINGLE PACKAGED VERTICAL AIR CONDITIONERS AND HEAT PUMPS,

ROOM AIR CONDITIONERS, AND ROOM AIR CONDITIONER HEAT PUMPS

MINIMUM EFFICIENCY REQUIREMENTS

| EQUIPMENT TYPE | SIZE CATEGORY (INPUT) | SUBCATEGORY OR RATING CONDITION | MINIMUM EFFICIENCYb | TEST PROCEDUREa |
| --- | --- | --- | --- | --- |
| PTAC (Cooling mode) Standard size New construction | All capacities | 95oF db outdoor air | 12.5 – (0.213 x Cap/1000) EER | AHRI 310/380 |
| PTAC (Cooling mode) Nonstandard size Replacementsc | All capacities | 95oF db outdoor air | 10.9 – (0.213 x Cap/1000) EER |  |
| PTHP (Cooling mode) Standard size New construction | All capacities | 95oF db outdoor air | 12.3 – (0.213 x Cap/1000) EER |  |
| PTHP (Cooling mode) Nonstandard size Replacementsc | All capacities | 95oF db outdoor air | 10.8 – (0.213 x Cap/1000) EER |  |
| PTHP (Heating mode) Standard size New construction | All capacities | --- | 3.2 – (0.026 x Cap/1000) COP |  |
| PTHP (Heating mode) Nonstandard size Replacementsc | All capacities | --- | 2.9 – (0.026 x Cap/1000) COP |  |
| SPVAC (Cooling mode) | <65000 Btu/h ≥65000<135000 Btu/h ≥135000<240000 Btu/h | 95oF db/75oF wb outdoor Air | 9.0 EER 8.9 EER 8.6 EER | AHRI 390 |
| SPVHP (Cooling mode) | <65000 Btu/h ≥65000<135000 Btu/h ≥135000<240000 Btu/h | 95oF db/75oF wb outdoor Air | 9.0 EER 8.9 EER 8.6 EER |  |
| SPVHP (Heating mode) | <65000 Btu/h ≥65000<135000 Btu/h ≥135000<240000 Btu/h | 47oF db/43oF wb outdoor Air | 3.0 COP 3.0 COP 2.9 COP |  |
| Room air conditioners with louvered sides | <6000 Btu/h ≥6000<8000 Btu/h ≥8000<14000 Btu/h ≥14000<20000 Btu/h =20000 Btu/h |  | 9.7 EER 9.7 EER 9.8 EER 9.7 EER 8.5 EER | ANSI/AHAM RAC-1 |
| Room air conditioners without louvered sides | <8000 Btu/h ≥8000<20000 Btu/h |  | 9.0 EER 8.5 EER |  |
| Room air conditioner heat pumps with louvered sides | <20000 ≥20000 Btu/h |  | 9.0 EER 8.5 EER |  |
| Room air conditioner heat pumps without louvered sides | <14000 ≥14000 Btu/h |  | 8.5 EER 8.0 EER |  |
| Room air conditioner, casement only | All capacities |  | 8.7 EER |  |
| Room air conditioner, casement-Slider | All capacities |  | 9.5 EER |  |
| For SI: oC – [(oF) – 32]/1.8 British thermal unit per hour – 0.2931 W. db = dry-bulb temperature, oF wb = wet-bulb temperature, oF a Chapter 6 contains a complete specification of the reference test procedure, including the referenced year version of the test procedure. b Cap means the rated cooling capacity of the product in Btu/h. If the unit’s capacity is less than 7,000 Btu/h, use 7,000 Btu/h in the calculation. If the unit’s capacity is greater than 15,000 Btu/h, use 15,000 Btu/h in the calculation. c Nonstandard size Replacements units must be factory labeled as follow: “MANUFACTURED FOR NONSTANDARD SIZE REPLACEMENT APPLICATIONS ONLY: NOT TO BE INSTALLED IN NEW CONSTRUCTION PROJECTS.” Nonstandard size Replacements efficiencies apply only to units being installed in with existing sleeves having an external wall opening of less than 16 inches (406 mm) high or and less than 542 inches (1067 mm) wide and having a cross-sectional area less than 670 in2. |  |  |  |  |

EN4840

TABLE 503.2.3(4) – change to read as shown..

TABLE 503.2.3(4)

WARM AIR FURNACES AND COMBINATION WARM AIR FURNACES/AIR-CONDITIONING UNITS,

WARM AIR DUCT FURNACES AND UNIT HEATERS

Minimum Efficiency Requirements

| Equipment Type | Size Category | Subcategory or Rating Condition | Minimum Efficiencyd,e | Test Procedurea |
| --- | --- | --- | --- | --- |
| Warm Air Furnace, Gas-Fired | <225,000 Btu/h | --- | 78% AFUE or 80% Etc | DOE 10 CFR, Part 430 or Section 2.39, Thermal Efficiency, of ANSI Z 21.47 |
|  | ≥225,000 Btu/h | Maximum Capacityc | 80% Ecf | Section 2.39, Thermal Efficiency, of ANSI Z21.47 |
| Warm Air Furnace, Oil-Fired | <225,000 Btu/h | --- | 78% AFUE or 80% Etc | DOE 10 CFR, Part 430 or Section 42, Combustion, of UL 727 |
|  | ≥225,000 Btu/h | Maximum Capacityb | 81% Etg | Section 42, Combustion, of UL 727 |
| Warm Air Duct Furnaces, Gas-Fired | All Capacities | Maximum Capacityb | 80% Ec | Section 2.10, Efficiency, of ANSI Z83.8 |
| Warm Air Unit Heaters, Gas-Fired | All Capacities | Maximum Capacityb | 80% Ec | Section 2.10, Efficiency, of ANSI Z83.8 |
| Warm Air Unit Heaters, Oil-Fired | All Capacities | Maximum Capacityb | 80% Ec | Section 40, Combustion, of UL 731 |

[No change to footnotes]

EN4843

Delete Table 503.2.3(7) in its entirety.

TABLE 503.2.3(7)

MINIMUM EFFICIENCIES FOR CENTRIFUGAL CHILLERS <150 TONS1

COPstd = 5.00; IPLVstd = 5.25

Delete Table 503.2.3(8) in its entirety.

TABLE 503.2.3(8)

MINIMUM EFFICIENCIES FOR CENTRIFUGAL CHILLERS >150 TONS, <300 TONS1

COPstd = 5.55; IPLVstd = 5.90

Delete Table 503.2.3(9) in its entirety.

TABLE 503.2.3(9)

MINIMUM EFFICIENCIES FOR CENTRIFUGAL CHILLERS > 300 TONS1

COPstd = 6.10; IPLVstd = 6.40

Table 503.2.3(7) – add new table as shown:

TABLE 503.2.3(7)

WATER CHILLING PACKAGES, EFFICIENCY REQUIREMENTSa

| Equipment Type | Size Category | Units | Path A |  | Path B |  | Test Procedure |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Full Load | IPLV | Full Load | IPLV | AHRI 550/590 |
| Air-cooled chillers | < 150 tons | EER | ≥ 9.562 | ≥ 12.500 | NAd | NAd |  |
|  | ≥ 150 tons | EER | ≥ 9.562 | ≥ 12.750 | NAd | NAd |  |
| Air cooled without condenser, electrical operated | All capacities | EER | Air-cooled chillers without condensers must be rated with matching condensers and comply with the air-cooled chiller efficiency requirements |  |  |  |  |
| Water cooled, electrically operated, reciprocating | All capacities | kW/ton | Reciprocating units must comply with water cooled positive displacement efficiency requirements. |  |  |  |  |
| Water cooled, electrically operated, positive displacement | < 75 tons | kW/ton | ≤ 0.780 | ≤ 0.630 | ≤ 0.800 | ≤ 0.600 |  |
|  | ≥ 75 tons and < < 150 tons | kW/ton | ≤ 0.775 | ≤0.615 | ≤ 0.790 | ≤ 0.586 |  |
|  | ≥ 150 tons and < 300 tons | kW/ton | ≤0.680 | ≤ 0.580 | ≤ 0.718 | ≤ 0.540 |  |
|  | ≥ 300 tons | kW/ton | ≤ 0.620 | ≤ 0.540 | ≤ 0.639 | ≤ 0.490 |  |
| Water cooled, electrically operated, centrifugal | < 300 tons | kW/ton | ≤ 0.634 | ≤ 0.596 | ≤0.639 | ≤ 0.450 |  |
|  | ≥ 300 tons and < 600 tons | kW/ton | ≤0.576 | ≤ 0.549 | ≤ 0.600 | ≤ 0.400 |  |
|  | ≥ 600 tons | kW/ton | ≤0.570 | ≤0.539 | ≤ 0.590 | ≤0.400 |  |
| Air cooled, absorption single effect | All capacities | COP | ≥ 0.600 | NRe | NAd | NAd | AHRI 560 |
| Water-cooled, absorption single effect | All capacities | COP | ≥0.700 | NRe | NAd | NAd |  |
| Absorption double effect, indirect-fired | All capacities | COP | ≥1.000 | ≥ 1.050 | NAd | NAd |  |
| Absorption double effect, direct-fired | All capacities | COP | ≥ 1.000 | ≥ 1.000 | NAd | NAd |  |

For SI: 1 British thermal unit per hour = 0.2931 W.

a. The chiller equipment requirements do not apply for chillers used in low-temperature applications where the design leaving fluid temperature is < 40oF.

b. Section 12 contains a complete specification of the referenced test procedure, including the referenced year version of the test procedure.

c. Compliance with this standard can be obtained by meeting the minimum requirements of Path A or B. However, both the full load and IPLV must be met to fulfill the requirements of Path A or B.

d. NA means that this requirement is not applicable and cannot be used for compliance.

e. NR means that there are no minimum requirements for this category.

EN4826

TABLE 503.2.3(810)

PERFORMANCE REQUIREMENTS FOR HEAT REJECTION EQUIPMENT

| Equipment Type | Total System Heat Rejection Capacity at Rated Conditions | Sub-Category or Rating Condition | Performance Required1,2,3 | Test Procedure3,4 |
| --- | --- | --- | --- | --- |
| Propeller or Axial Fan Open-Circuit Cooling Towers | All | 95oF Entering Water | ≥38.2 gpm/hp | CTI ATC-105 and CTI STD-201 |
|  |  | 85oF Leaving Water |  |  |
|  |  | 75oF Entering wbOutdoor Air |  |  |
| Centrifugal Fan Open-Circuit Cooling Towers | All | 95oF Entering Water | ≥20.0 gpm/hp | CTI ATC-105 and CTI STD-201 |
|  |  | 85oF Leaving Water |  |  |
|  |  | 75oF Entering wbOutdoor Air |  |  |
| Propeller or Axial Fan Closed-Circuit Cooling Towers | All | 102oF Entering Water | ≥14.0 gpm/hp | CTI ATC-105S and CTI STD-201 |
|  |  | 90oF Leaving Water |  |  |
|  |  | 75oF Entering wb |  |  |
| Centrifugal Closed-Circuit Cooling Towers | All | 102oF Entering Water | ≥7.0 gpm/hp | CTI ATC-105S and CTI STD-201 |
|  |  | 90oF Leaving Water |  |  |
|  |  | 75oF Entering wb |  |  |
| Air Cooled Condensers | All | 125oF Condensing Temperature R-22 Test Fluid 190oF Entering Gas Temperature 15oF Subcooling 95oF Entering db | ≥176,000 Btu/h-hp | AHRI 460 |

1 For purposes of this table, open-circuit cooling tower performance is defined as the water maximum flow rating of the tower at the thermal rating condition listed in Table 503.2.3 (8) divided by the fan nameplate rated motor nameplate power.

2For the purposes of this table, closed-circuit cooling tower performance is defined as the process water flow rating of the tower at the thermal rating condition listed in Table 505.2.3(8) divided by the sum of the fan motor nameplate power and the integral spray pump motor nameplate power.

32For purposes of this table, air-cooled condenser performance is defined as the heat rejected from the refrigerant divided by the fan nameplate rated motor nameplate power.

4 3Chapter 6 contains a complete specification of the referenced test procedure, including the referenced year version of the test procedure.

5 The efficiencies and test procedures for both open- and closed-circuit cooling towers listed in Table 503.2.3(8) are not applicable to hybrid cooling towers that contain a combination of separate wet and dry heat exchange sections.

EN4826

Table 503.2.7.2 – Change “Mechanical closet” requirements to read as shown:

TABLE 503.2.7.2

DUCT SYSTEM CONSTRUCTION AND SEALING

[in part]

| DUCT TYPE/CONNECTION | SEALING REQUIREMENTS | MECHANICAL ATTACHMENT |
| --- | --- | --- |
| Mechanical closets | All joints between the air barriers of walls, ceiling, floor and door framing and all penetrations of the air barrier shall be sealed to the air barrier with approved closure systems. Through-wall, through-floor and through-ceiling air passageways into the closet shall be framed and sealed to form an air-tight passageway. Exception: Air passageways into the closet from conditioned space that are specifically designed for return air flow. The following air barriers are approved for use in mechanical closets: 1. One-half-inch-thick (12.7 mm) or greater gypsum wallboard, taped and sealed with joint compound over taped joints between gypsum wallboard panels. 2. Other panelized materials having inward facing surfaces with an air porosity no greater than that of a duct product meeting Section 22 of UL 181 which are sealed on all interior surfaces to create a continuous air barrier by one of the following: - Sealants complying with the product and application standards of this table for fibrous glass ductboard or - A suitable long-life caulk or mastic for all applications.. | The following closure systems are approved for use in mechanical closets: 1. Gypsum wallboard joint compound over taped joints between gypsum wallboard panels. 2. Sealants complying with the product and application standards of Table 503.2.7.2 for fibrous glass ductboard. 3. A suitable long-life caulk or mastic compliant with the locally adopted mechanical code for all applications. |

COMMENT AFTER GLITCH

Table 503.2.8 – change to add footnotes as shown:

TABLE 503.2.8

MINIMUM PIPE INSULATION

[No change to table except add footnotes as shown]

- Piping insulation is not required between the control valve and coil on run-outs when the control valve is located within 4 feet of the coil and the pipe size is 1 inch or less.

- These thicknesses are based on energy efficiency considerations only. Issues such as water vapor permeability or surface condensation sometimes require vapor retarders or additional

COMMENT AFTER GLITCH

Section 503.4.3.3.2 – Change to read as shown:

503.4.3.3.2 Heat rejection. Reserved. Heat rejection equipment shall comply with Table 503.2.3(8).

Exception: Where it can be demonstrated that a heat pump system will be required to reject heat throughout the year.

EN4769

TABLE 504.2 – change to read as shown.

TABLE 504.2

Minimum Performance of Water-Heating Equipment

| Equipment Type | Size Category (input) | Subcategory or Rating Condition | Performance Required1,2 | Test Procedure |
| --- | --- | --- | --- | --- |
| Electric table top water heaters | ≤ 12kW | Resistance = 20 gal | 0.93 – 0.00132V EF | DOE 10 CFR Part 430 |
| Water heaters, Electric | > 12kW | Resistance | 0.97-0.00132V, EF | DOE 10 CRF Part 4303 |
|  | >12 kW | Resistance | 1.73V + 155 SL, Btu/h | Section G.2 of ANSI Z21.10.3 |
|  | ≤24 Amps & ≤ 250Volts | Heat Pump | 0.93-0.00132V, EF | DOE 10 CFR Part 4303 |
| Storage water heaters, Gas | ≤75,000 Btu/h | ≥20 gal | 0.67-0.0019V, EF | DOE 10 CFR Part 4303 |
|  | >75,000 Btu/h and = 155,000 Btu/h | <4,000 (Btu/h)/gal | 80% Et (Q/800+110/V) SL, Btu/h | Section G.1 and G.2 of ANSI Z21.10.3 |
|  | >155,000 Btu/h | <4,000 (Btu/h)/gal | 80% Et (Q/800+110/V) SL, Btu/h |  |
| Instantaneous water heaters, gas | >50,000 Btu/h and <200,000 Btu/h4 | ≥4,000 (Btu/h)/gal and < 2 gal | 0.62-0.0019V, EF | DOE 10 CFR Part 430 |
|  | ≥200,000 Btu/h | ≥4,000 (Btu/h)/gal and <10 gal | 80% Et | Section G.1 and G.2 of ANSI Z21.10.3 |
|  | ≥200,000 Btu/h | >4,000 (Btu/h)/gal and <10 gal | 80% Et (Q/800+110/V) SL, Btu/h |  |
| Storage water heaters, Oil | ≤ 105,000 Btu/h | ≥ 20 gal | 0.59-0.0019V, EF | DOE 10 CFR Part 4303 |
|  | >105,000 Btu/h | < 4,000 (Btu/h)/gal | 78% Et (Q/800+100/V) SL,Btu/h | Section G.1 and G.2 of ANSI Z21.10.3 |
| Instantaneous water heaters, Oil | ≤210,000 Btu/h | ≥4,000 (Btu/h)/gal and <2 gal | 0.59-0.0019V, EF | DOE 10 CFR Part 430 |
|  | >210,000 Btu/h | ≥4,000 (Btu/h)/gal and <10 gal | 80% Et | Section G.1 and G.2 of ANSI Z21.10.3 |
|  | >210,000 Btu/h | ≥4,000 (Btu/h)/gal and ≥10 gal | 78% Et (Q/800+110/V) SL, Btu/h |  |
| Hot water supply boilers, Gas and Oil | ≥300,000 Btu/h and <12,500,000 Btu/h | ≥4,000 (Btu/h)/gal and <10 gal | 80% Et | Section G.1 and G.2 of ANSI Z21.10.3 |
| Hot water supply boilers, Gas | ≥300,000 Btu/h and <12,500,000 Btu/h | ≥4000 (Btu/h)/gal and =10 Gal | 80% Et (Q/800+110/V) SL, Btu/h |  |
| Hot Water Supply Boilers, Oil | ≥300,000 Btu/h and <12,500,000 Btu/h | >4000 (Btu/h)/gal and >10 Gal | 78% Et (Q/800+110/V) SL, Btu/h |  |
| Pool heaters, Gas and Oil | All | -- | 78% Et before 4/16/2013 82% Et after 4/16/2013 | ASHRAE 146 |
| Heat pump pool heaters | All | --- | 4.0 COP At low air temperature | AHRI 1160d |
| Unfired storage tanks | All |  | Minimum insulation requirement R-12.5 (h.ft2.oF)/Btu | (none) |

For SI: 1 Btu/h=.2931W, oC=[(oF) – 32]/1.8

[No change to footnotes]

EN4839, EN 4790

506.4 Documentation – change to read as shown.

506.4 Documentation. The EnergyGauge Summit Fla/Com Commission approved compliance software tools shall be utilized to conform to the provisions of this section. Compliance software provisions and overall stringency shall be as described in Normative Appendix B.

EN4751

Table 505.6.2.  Delete table except title, Reserve.

TABLE 505.6.2

LIGHTING POWER DENSITIES FOR BUILDING EXTERIORS

Reserved.

| Applications | Lighting Power Densities |
| --- | --- |
| Tradable Surfaces (Lighting Power Densities for uncovered parking areas, building grounds, building entrances and exits, canopies and overhangs, and outdoor sales areas may be traded.) |  |
| Uncovered Parking Areas |  |
| Parking lots and drives | 0.15 W/ft2 |
| Building Grounds |  |
| Walkways less than 10 feet wide | 1.0 watts per linear foot |
| Walkways 10 feet wide or greater, plaza areas, and special feature areas | 0.2 W/ft2 |
| Stairways | 1.0 W/ft2 |
| Building Entrances and Exits |  |
| Main entries | 30 watts per linear foot of door width |
| Other doors | 20 watts per linear foot of door width |
| Canopies and Overhangs |  |
| Canopies (freestanding and attached and overhangs) | 1.25 W/ft2 |
| Outdoor Sales |  |
| Open areas (including vehicle sales lots) | 0.5 W/ft2 |
| Street frontage for vehicle sales lots in addition to “open area” allowance | 20 watts per linear foot |
| Non-Tradable Surfaces (Lighting Power Density calculations for the following applications can be used only for the specific application and cannot be traded between surfaces or with other exterior lighting. The following allowances are in addition to any allowance otherwise permitted in the “Tradable Surfaces” section of this table.) |  |
| Building facades | 0.2 W/ft2 for each illuminated wall or surface or 5.0 watts per linear foot for each illuminated wall or surface length |
| Automated teller machines and night depositories | 270 watts per location plus 90 watts per additional ATM per location |
| Entrances and gatehouse inspection stations at guarded facilities | 1.25 W/ft2 of uncovered area (covered areas are included in the “Canopies and Overhangs” section of “Tradable Surfaces”) |
| Loading areas for law enforcement, fire, ambulance, and other emergency service vehicles | 0.5 W/ft2 of uncovered area (covered areas are included in the Canopies and Overhangs” section of “Tradable Surfaces”) |
| Drive-up windows at fast food restaurants | 400 watts per drive-through |
| Parking near 24-hour retail entrances | 800 watts per main entry |

EN4743

Chapter 6 – REFERENCED STANDARDS

Add or change the following referenced standards as shown:

APSP

Association of Pool & Spa Professionals

2211 Eisenhower Ave

Alexandria, VA 22314

Standard referenced number        Title                                           Reference in code section number

ANSI/APSP-14—11     Portable Electric Spa Energy Efficiency Standard . . . . . . . . . .  . . . .......403.9

ANSI/APSP-15—11     Residential Swimming Pool and Spa Energy Efficiency Standard..............403.9

EN 4864

CTI

Cooling Technology Tower Institute

2611 FM 1960 West, Suite H-200

Houston, TX 77068-3730

Standard referenced number                    Title                                               Reference in code section number

CTI ATC-105-(00)2000          Acceptance Test Code for Water Cooling Towers                                Table 503.2.3(8 10)

CTI ATC-105S-96                  Acceptance Test Code for Closed Circuit Cooling Towers                     Table 503.2.3(8)

CTI Std. 201-04 2002           Certification Standard for Water Cooling Tower Thermal Performance  Table 503.2.3(8 10)

EN4826

FSEC

Florida Solar Energy Center

1679 Clearlake Road

Cocoa, FL 32922-5703

Standard referenced number                    Title                                Reference in code section number

FSEC-RR-54-00       "The HERS Rating Method and the Derivation of the Normalized Modified Loads Method",

October 11, 2000,    Fairey, P., J. Tait, D. Goldstein, D. Tracey, M. Holtz, and R. Judkoff    Appx.B: B-1.1.3,

Available online at:   http://www2.fsec.ucf.edu/en/publications/html/FSEC-RR-54-00/index.htm

2010                        EnergyGauge USA Fla/Res          103.2.1.2, 405.4.1, Appendix B B-1.2

2010                        EnergyGauge Summit Fla/Com   103.2.2.2, 506.4, Appendix B B-2.3, Table B-2.2

EN4770

NORMATIVE APPENDIX B – CRITERIA FOR COMPUTER MODELING….

B-1.1.3 Equipment calculation…  - Change to read as shown:

B-1.1.3 Equipment calculation of End Use Energy Loads for Code Compliance Determination. The energy loads for heating, cooling and hot water in the Proposed Design home shall be normalized to account for the differences in improvement potential that exist across equipment types using the following formula in accordance with the paper "The HERS Rating Method and the Derivation of the Normalized Modified Loads Method," Research Report No. FSEC-RR-54-00, Florida Solar Energy Center.

nMEUL = REUL * (nEC_x /EC_r) where:

nMEUL = normalized Modified End Use Loads (for heating, cooling or hot water) as computed using EnergyGauge USA Fla/Res Commission approved compliance software.

REUL = Standard Reference Design Home End Use Loads (for heating, cooling or hot water) as computed using EnergyGauge USA Fla/Res Commission approved compliance software.

EC_r =           estimated Energy Consumption for the Standard Reference Design Home’s end uses (for heating, including auxiliary electric consumption, cooling or hot water) as computed using EnergyGauge USA Fla/Res Commission approved compliance software.

and where:          nEC_x = (a* EEC_x – b)*(EC_x * EC_r * DSE_r) / ( EEC_x * REUL)  where:

nEC_x = normalized Energy Consumption for Proposed Design’s end uses (for heating, including auxiliary electric consumption, cooling or hot water) as computed using EnergyGauge USA Fla/Res Commission approved compliance software.

EC_r = estimated Energy Consumption for Standard Reference Design home’s end uses (for heating, including auxiliary electric consumption, cooling or hot water) as computed using EnergyGauge USA Fla/Res Commission approved compliance software.

EC_x = estimated Energy Consumption for the Proposed Design home’s end uses (for heating, including auxiliary electric consumption, cooling or hot water) as computed using EnergyGauge USA Fla/Res Commission approved compliance software.

EEC_x = Equipment Efficiency Coefficient for the Standard Reference Design home’s equipment, such that

EEC_x equals the energy consumption per unit load in like units as the load, and as derived from the Manufacturer’s Equipment Performance Rating (MEPR) such that

EEC_x equals 1.0 / MEPR for AFUE, COP or EF ratings, or such that EEC_x equals 3.413 / MEPR for HSPF, EER or SEER ratings.

DSE_r = REUL/EC_r * EEC_r

For simplified system performance methods, DSE_r equals 0.80 for heating and cooling systems. However, for detailed modeling of heating and cooling systems, DSE_r may be less than 0.80 as a result of part load performance degradation, coil air flow degradation, improper system charge and auxiliary resistance heating for heat pumps. Except as otherwise provided by these Standards, where detailed systems modeling is employed, it must be applied equally to both the Standard Reference Design and the Proposed Design homes.

EEC_r = Equipment Efficiency Coefficient for the Standard Reference Design home’s equipment, such that EEC_r equals the energy consumption per unit load in like units as the load, and as derived from the Manufacturer’s Equipment Performance Rating (MEPR) such that EEC_r equals 1.0 / MEPR for AFUE, COP or EF ratings, or such that EEC_r equals 3.413 / MEPR for HSPF, EER or SEER ratings.

REUL = Standard Reference Design home End Use Loads (for heating or cooling) as 
computed using EnergyGauge USA Fla/Res Commission approved compliance software.

EN4752

PARTIAL TABLE B-2.2 shown:

Table B-2.2

SPECIFICATIONS FOR THE STANDARD REFERENCE AND PROPOSED DESIGNS

| BUILDING COMPONENT/ CHARACTERISTICS | STANDARD REFERENCE DESIGN | PROPOSED DESIGN |
| --- | --- | --- |
| Building envelope | In 3 locations make the following change: EnergyGauge Summit Fla/Com Commission approved compliance software | No change |
| Miscellaneous loads | In 1 location make the following change: EnergyGauge Summit Fla/Com Commission approved compliance software | No change |

1 Specifications utilized in the EnergyGauge Summit Fla/Com Commission approved computer program are those specified by Chapter 11 of ASHRAE Standard 90.1-2004.

EN4753

APPENDIX C - FORMS

EPL Display Card - Change to read as shown.

ENERGY PERFORMANCE LEVEL (EPL) DISPLAY CARD

[No change to form except the Note as shown:]

*NOTE: The home's estimated Energy Performance Index is available through the EnergyGauge USA FLA/RES computer program. This is not a Building Energy Rating.  If your index is below 70 100 your home may qualify for energy efficiency mortgage (EEM) incentives if you obtain a Florida Building EnergyGauge Rating.  Contact the EnergyGauge Hotline at (321) 638-1492 or see the EnergyGauge web site at www.energygauge.com for information and a list of certified Raters. For information about Florida's Energy Efficiency Code For BuildingConstruction, contact the Florida Building Commission's support staff Department of Community Affairs at (850) 487-1824.

EN4865

FORM 402-2010

Page 1

Scope - Change to read as shown:

Florida Building Code, Energy Conservation

Residential Building Thermal Envelope Approach

FORM 402-2010                                                                                 		                    All climate zones

Scope: Compliance with Section 402 of the Florida Building Code, Energy Conservation, shall be demonstrated by the use of Form 402 for single- and multiple-family residences of three stories or less in height, additions to existing residential buildings, renovations to existing residential buildings, new heating, cooling, and water heating systems in existing buildings, and site-added components of manufactured homes and manufactured buildings, as applicable. To comply, a building must meet or exceed all of the energy efficiency requirements on Table 402A and all applicable mandatory requirements summarized in Table 402B of this form. If a building does not comply with this method or Alternate Form 402, the printout from FlaResCheck, it may still comply under Section 405 of the Florida Building Code, Energy Conservation.

[No other changes to page 1]

EN4791

PAGE 2

Table 402A – Change footnotes (2), (3) and (5) to table as shown:

(2) Windows and doors qualifying as glazed fenestration areas must comply with both the maximum U-Factor and the maximum SHGC (Solar Heat Gain Coefficient) criteria and have a maximum total window area equal to or less than 20% of the conditioned floor area (CFA); otherwise Section 405 must be used for compliance.

Exceptions: 1. Additions of 600 square feet (56 m2) or less may have a maximum glass to CFA of 50 percent.

2. Renovations with new windows under ≥2 foot overhang whose lower edge does not extend further than 8 feet from the overhang may have tinted glazing or double-pane clear glazing. Replacement skylights installed in renovations shall be double paned or single paned with a diffuser.

(3) R-values are for insulation material only as applied in accordance with manufacturers’ installation instructions. For mass walls, the “interior of wall” requirement must be met except if at least 50% of the R-6 insulation required for the “exterior of wall” is installed exterior of, or integral to, the wall.

(5) For all conventional units with capacities greater than 30,000 Btu/hr. For other types of equipment, see Tables 503.2.3(1-8 10).

Exception: [No change to exception]

COMMENT AFTER GLITCH

Table 402B – Change as shown:

| TABLE 402B MANDATORY REQUIREMENTS |  |  |
| --- | --- | --- |
| Component | Section | Summary of Requirement(s) |
| Air distribution system | 403.2 | Ducts in attics or on roofs insulated to R-8; other ducts R-6. Ducts tested to Qn=0.03 by a Class 1 BERS rater. |
| Swimming pools & spas | 403.9 | Spas and heated pools must have vapor-retardant covers or a liquid cover or other means proven to reduce heat loss except if 70% of heat from site-recovered energy. Off/timer switch required. Gas heaters minimum thermal efficiency=78% (82% after 4/16/13). Heat pump pool heaters minimum COP= 4.0. |

[No other changes to table]4

EN4791, COMMENT AFTER GLITCH

No other changes to page 2.

APPENDIX D – FLORIDA STANDARDS

Delete Appendix D in its entirety:

APPENDIX D

FLORIDA STANDARDS

FLORIDA STANDARD NO. 12(FL-12)

FLORIDA REGULATORY REQUIREMENTS FOR ENERGY EFFICIENCY FOR RESIDENTIAL INGROUND SWIMMING POOLS & SPAS

The following regulatory requirements shall constitute Florida Standard FL-12 and will provide compliance criteria for section 403.9 of the Florida Building Code, Energy Conservation Code. These requirements follow an Association of Pool & Spa Professional (APSP) a draft national standard for energy efficiency for residential in-ground swimming pools and spas.

SECTION 1

SCOPE

1.1.      Energy efficiency requirement for permanently installed residential aboveground/onground and inground swimming pool filtration and permanently installed swimming pool and spa heating systems used for bathing and are operated by an owner. This standard is intended to cover certain aspects of the swimming pool filtration and heating system design, equipment, installation, and operation for the purpose of consuming less energy while maintaining water quality and temperature.

1.2.       This standard does not cover swimming pool safety requirements, including, but not limited to, suction entrapment, structural, thermal, or electrical hazards.

1.3.      This standard does not cover Portable Electric Spas, which are covered by FL-2, APSP-14 Standard for Portable Electric Spa Energy Efficiency.

1.4        This standard provides specifications for energy efficient filtration systems, but does not specify sanitizer, daily turnover flow rates, or pool-cleaning technologies needed to establish and maintain swimming pool water quality.

1.5 1.2.  This standard provides specifications for energy efficient, permanently installed residential aboveground/onground and inground swimming pool and spa heating systems.

1.6 1.5.              Other standards are referenced in this standard for items not covered.

SECTION 2

NORMATIVE REFERENCES

AHRI 1160, Standard For Performance Rating of Heat Pump Pool Heaters

APSP-4, Standard For Aboveground/Onground Residential Swimming Pools.[1]

APSP-5, Standard For Residential Inground Swimming Pools.1

APSP-7, Standard for Suction Entrapment Avoidance in Swimming Pools, Wading Pools, Spas, Hot Tubs, and Catch Basins.1

HI 1.6, Centrifugal Pump Test.[2]

IEEE 114-2001, Standard Test Procedure for Single-Phase Induction Motors.[3]

NFPA 70, National electrical code, Article 680, Swimming pools, fountains, and similar installations.[4]

NSF 50, Equipment for Swimming Pools, Spas, Hot Tubs and Other Recreational Water Facilities.[5]

SECTION 3

DEFINITIONS

Auxiliary Pool Loads. Features, functions, or devices that need higher head and flow rates than that required for pool filtration, including, but not limited to, solar pool heating systems, filter backwashing, pool cleaners, waterfalls, fountains, and spas.

Backwash Valve. A diverter valve designed to reverse the flow of water through a filter. The valve is located between the circulation pump and the filter, including, but not limited to, slide, push-pull, multi-port, and full-flow valves.

Brake Horsepower. A term historically used in the pool, spa, and whirlpool bath industries, a term which conflicts with Total Horsepower and Service Factor Horsepower, and if used would not conform to this standard.

Capacity of the Motor. The Total Horsepower, or product of the rated horsepower and the service factor of a motor used on a pool pump (also known as SFHP) based on the maximum continuous duty motor power output rating allowable for nameplate ambient rating and motor insulation class.

Elbow (fittings). Also called ell, el. a plumbing pipe or pipe connection having a right-angled bend.

Energy Factor. The measure of overall pool filter pump efficiency in units of gallons per watt-hour, as determined using the applicable test method in Section 4.1.2. Energy Factor is analogous to other energy factors such as Miles Per Gallon. Energy Factor (EF) is calculated as:

EF (gal/Wh) = Flow (gpm) x 60 / Power (watts)

Filtration Flow Rate. A flow rate that will turn over the pool water volume in six hours or more (must be equal to or less than the maximum filtration flow rate).

Flow Rate. Flow rate is the volume of water flowing through the filtration system in a given time, usually measured in gallons per minute (gpm).

Full-Rated. A term used to describe pool pump motors with a Service Factor greater than 1.25 (typically). The term is generally used for marketing purposes and is not used within the scope this standard.

Head. The water pressure necessary to move fluid through pipes and inlets, push water through filters,and heaters, and other equipment and project it through fountains and jets.

Maximum Filtration Flow Rate. The flow rate needed to turn over the pool water volume in six hours or 36 gpm, whichever is greater.

Maximum Flow Rate. The flow rate for the auxiliary pool loads or the filtration flow rate, whichever is greater.

Max-Rated. A term used to describe pool pump motors with a Service Factor between 1.0 and 1.25 (typically). The term is generally used for marketing purposes and is not within the scope this standard.

Multi-Speed. A pump motor capable of operating at two (2) or more speeds and includes two-speed, three-speed and variable-speed pumps.

Nameplate Horsepower. The nameplate power is the motor horsepower listed on the pumpnameplate and the horsepower by which a pump is typically sold (also known as rated horsepower).

NSF/ANSI 50 is the NSF International (formerly National Sanitation Foundation) Standard and American National Standards Institute document entitled “Circulation System Components and Related Materials for Swimming Pools, Spas/Hot Tubs”

Peak Horsepower. A term historically used in the pool, spa, and whirlpool bath industries, a term which conflicts with Total Horsepower and Service Factor Horsepower, and if used would not conform to this standard.

Permanently Installed Swimming Pool. A pool constructed in such a manner that it cannot be disassembled for storage.

Pipe and Pipe Fittings. The PVC pipe and fittings intended for use in the transport of swimming pool filtration water. Fittings include elbows, tees, and flow control valves. Pipe and fittings do not include backwash valves, which are addressed separately, and equipment connections, or internal equipment piping.

Pool Pump Motor Capacity. See Total Horsepower.

Pumps. Pool and spa pumps usually come with a leaf strainer before the impeller. The pumps contain an impeller to accelerate the water through the housing. The motors for residential pumps are included in the pump purchase but can be replaced separately. The pumps increase the “head” and “flow” of the water.

Rated Horsepower. The motor power output designed by the manufacturer for a rated RPM, voltage and frequency. May be less than Total Horsepower where the Service Factor is > 1.0, or equal to Total Horsepower where the Service Factor = 1.0

Residential Swimming Pools. Permanently installed residential inground and aboveground/onground swimming pools intended for use by a single-family home for noncommercial purposes and with dimensions as defined in ANSI/NSPI-5, Standard for Residential Inground Swimming Pools and ANSI/APSP-4 Standard for Aboveground/Onground Residential Swimming Pools.

Return. The return refers to the water in the filtration system returning to the pool. The return lines or return side, relative to the pump, can also be defined as the pressure lines or the pressure side of the pump. Water in the returns is delivered back to the pool at the pool inlets.

Service Factor. A multiplier applied to rated horsepower of a motor to indicate the percent above nameplate horsepower at which a pump motor may operate continuously without exceeding its allowable insulation class temperature limit, provided the other design parameters such a rated voltage, frequency and ambient temperature are within limits. Full-rated pool motor service factors can be as high as 1.65. A 1.5 hp pump with a 1.65 service factor produces 2.475 hp (total horsepower) at the maximum service factor point.

Service Factor Horsepower (SFHP). The maximum continuous duty motor power output rating allowable for nameplate ambient rating and motor insulation class. Commonly, service factor horsepower = rated horsepower x service factor (also known as total horsepower).

Special Horsepower. A term historically used in the pool, spa, and whirlpool bath industries, a term which may conflict with Rated Horsepower, Total Horsepower and Service Factor Horsepower, and if used would not conform to this standard.

Suction. Suction created by the pump is how the pool water gets from the skimmers and suction outlets to the filtration system. The suction side and suction lines refer to the vacuum side of the pump. It is at negative atmospheric pressure relative to the pool surface.

System Curve. A graphical representation of the relationship between Flow Rate and Total Dynamic Head, where TDH increases proportional to the square of the flow and plotting the relationship results in a parabolic shape. Each system will have a unique curve with the starting point, (zero flow) being the same for all systems. The generic expression for a system curve is H = C X F2, where H = Total Dynamic Head, C = is a coefficient based on the resistance of the system, and F = flow rate. As TDH increases, for example, as the filter collects debris and system pressure increases, coefficient C will also increase.

Sweep Elbow. Sweep elbows orare a type of elbow that has a pressure drop less than the pressure drop of straight pipe with a length of 30 pipe diameters. For example, a 2 inch elbow must have a pressure drop less than a 5-foot length of 2 inch straight pipe.

Total Dynamic Head. Total dynamic head, or TDH, refers to the sum of all the friction losses and pressure drops in the filtration system from the pool’s suction outlets and skimmers to the returns. It is a measure of the system’s total pressure drop and is given in units of either psi or feet of water column (sometimes referred to as “feet”, or “feet of head” or “head”).

Total Horsepower. The product of the rated horsepower nameplate power and the service factor of a motor used on a pool pump(also known as SFHP) based on the maximum continuous duty motor power output rating allowable for nameplate ambient rating and motor insulation class.

Total Horsepower = Rated Horsepower x Service Factor.

Turnover. A turnover is the act of filtering one volume of water in the pool.

Turnover Time (also called Turnover Rate). The time required to circulate the entire volume of water in the pool or spa through the filter. e.g. A turnover time of 6-hours means an entire volume of water equal to that of the pool will be passed through a filter system in six hours.

Turnover Time = Volume of the pool / Flow rate

Up-Rated. A term used to describe pool pump motors with a Service Factor between 1.0 and 1.25 (typically). The term is generally used for marketing purposes and is not within the scope this standard.

SECTION 4

APPLIANCES

4.1   Pool filter pumps

4.1.1          Motors

4.1.1.1    Motor efficiency
Pool filter pump motors shall not be split-phase, shaded-pole, or capacitor start – induction run type.

EXCEPTION: Pool pump motors that are powered exclusively from on-site renewable generation. For example: solar photovoltaic and wind generation. Grid-tied generation systems are not exempt since the pump is powered from the traditional utility grid when the alternate power source is not available.

4.1.1.2    Two-speed, multi-speed, or variable-speed capability
Pool filter pump motors with a capacity of 1.0 total horsepower or greater shall have the capability of operating at two or more speeds with a low speed having a rotation rate that is no more than one-half of the motor’s maximum rotation rate.

4.1.1.3    Test methods for pool filter pump motors

4.1.1.3.1  Reported motor efficiency shall be verifiable by test method IEEE 114-2001 (corrected), or most recent version.

NOTE- Section 5.2.4.2.1 of IEEE 114-2001 lists formula for dynamometer correction factor. Formula inadvertently omits a component of the equation. Section 5.2.1.3.2 of the 1982 version of the standard lists formula correctly. Therefore, “corrected” shall mean using the 1982 version of the formula within the 2001 standard

4.1.2          Pumps

4.1.2.1    Test methods for pool pumps
4.1.2.1.1 ANSI/HI 1.6-2000 shall be used for the measurement of pump performance and efficiency.

4.1.2.1.2 4.1.2.1.1  Tests shall be conducted using unmodified, manufactured and fully assembled pump, including strainer baskets when applicable.

4.1.2.1.3 4.1.2.1.2   Three system curves shall be calculated:

Curve A: H = 0.0167 x F2 (approximately Curve 2.0” pipe)
Curve B: H = 0.050 x F2 (approximately Curve 1.5” pipe)
Curve C: H = 0.0082 x F2 (approximately Curve 2.5” pipe)

Where:
H is the total system head in feet of water.
F is the flow rate in gallons per minute (gpm).

4.1.2.1.4. 4.1.2.1.3  For each curve (A, B, and or C), the pump head shall be adjusted until the flow and head lie on the curve. The following shall be tested and reported for the intersect point of the pump performance curve with each system curve.:

1.       Motor nominal speed (RPM)

2.       Flow (gallons per minute)

3.       Power (watts)

4.       Energy Factor (gallons per watt hour)

Where the Energy Factor (EF) is calculated as:

EF = Flow (gpm) x 60 / Power (watts)

4.1.2.1.5 4.1.2.1.4 . For two-speed, three-speed, or other multi-speed pumps with fixed, non-adjustable speeds, test and report the intersect point of the pump performance curve with each system curve. Intersect data required in Section 4.1.2.1.4 shall be reported for each at both high and low speeds and each system curve s.

4.1.2.1.6  For variable-speed pumps, test and reportthe intersect point of the pump performance curve with each system curve. Intersect data required in Section 4.1.2.1.4 shall be reported for the highest, lowest, and the best efficiency speedsas determined by the manufacturer.

4.1.3          Labeling

4.1.3.1    Motors
Each pool filter pump motor shall be marked, permanently and legibly on an accessible and conspicuous place on the unit, in characters no less than ¼", the capacityTotal Horsepower of the motor.

4.1.3.2    Pumps
Each pool filter pump shall be marked, permanently and legibly on an accessible and conspicuous place on the unit, in characters no less than ¼", the Nnameplate Hhorsepower of the pump.

4.1.3.3    Two-speed, multi-speed, or variable-speed pool filter pumps shall be marked permanently and legibly on an accessible and conspicuous place on the unit, in characters no less than ¼", “This pump, when used as a filter pump, must be installed with a two-, multi-, or variable-speed pump motor controller.”

EXCEPTION: Pool filter pumps with integrated and/or included timer and motor control without which the motor will not run and which comply with Section 4.2.1.

4.2   Pump controllers

4.2.1     Pool pump motor controls for use with a two-speed, multi-speed, or variable-speed pumps shall have the capability of operating the pool pump at least at two speeds. The control’s default filtration speed setting shall be no more than one-half of the motor’s maximum rotation rate. Any high-speed override capability shall be for a temporary period not to exceed one 24-hour cycle without resetting to default settings.

4.3   Heaters

4.3.1          Energy design

4.3.1.1    Gas-fired pool heaters shall not be equipped with constant burning pilots.

4.3.1.2    All pool heaters shall have a readily accessible on-off switch that is mounted on the outside of the heater and that allows shutting off the heater without adjusting the thermostat setting.

4.3.1.3    Electric resistance hearing is prohibited.

4.3.2          Heater efficiency

4.3.2.1    Gas-fired pool heaters and oil-fired pool heaters shall have a thermal efficiency of not less than 78 percent for heaters manufactured before April 16, 2013 and not less than 82 percent for heaters manufactured on or after April 16, 2013.

4.3.2.2    There is no energy efficiency standard for electric resistance pool heaters.

4.3.2.3    Electric heat pump pool heaters shall have a coefficient of performance (COP) of not less than 4.0 at the low temperature conditions when tested in accordance with AHRI Standard 1160.

4.3.3          Test methods

4.3.3.1    ANSI Z21.56 – 1994 shall be used for the measurement of gas-fired and oil-fired pool heater efficiency.

4.3.3.2    ANSI/ASHRAE 146-1998 shall be used for the measurement of electric resistance pool heater efficiency.

4.3.3.3    AHRI 1160 - 2008, Table 2, Standard Rating Conditions – Low Air Temperature, shall be used for the measurement of heat pump pool heater efficiency.

AHRI 1160 – 2008: Table 2. Standard Rating Conditions Air Temperature Surrounding Unit; Water Temperature Entering Unit; Water Flow Rate (or Less if Specified by the Manufacturer). Dry-bulb °F [°C]; Wet-bulb °F [°C]; °F [°C]; GPM; L/s. High Air Temperature -Mid Humidity (62% RH); 80.6 [27.0]; 70.7 [21.5]; 80.0 [26.7]; 0.450 per 1000 Btu/h; 0.028 per 293.1 Watts. Low Air Temperature -Mid Humidity (63% RH); 50.0 [10.0]; 44.2 [6.78]; 80.0 [26.7]; Same flow rate as established in High Air Temperature - Mid Humidity (62% RH).

To comply with this standard, measured test results for Heating Capacity and Coefficient of Performance shall not be less than 95% of Published Ratings

SECTION 5

POOL SYSTEMS

5.1   General

5.1.1    All filter pumps and filter pump motors installed shall be listed in the California Energy Commission’s Appliance Efficiency Database for Residential Pool Pumps, or the APSP Appliance Efficiency Pool Pump Database and shall comply with Section 4.1.

5.1.2    For maximum energy efficiency, pool filtration should be operated at the lowest possible flow rate for a time period that provides sufficient water turnover for clarity and sanitation.

5.1.3    For maximum hydraulic efficiency, sweep elbows or elbow-type fittings that have a pressure drop of less than the pressure drop of straight pipe with a length of 30 pipe diameters are recommended.

5.1.4    Auxiliary pool loads that require high flow rates such as spas, pool cleaners, and water features, should be operated separately from the filtration system to allow the maximum filtration flow rate to be kept to a minimum.

5.1.5    Pool controls are a critical element of energy efficient pool design. Modern pool controls allow for auxiliary loads such as cleaning systems, solar heating, and temporary water features without compromising energy savings.

5.2   Maximum filtration flow rate

5.2.1     Depending on the size (volume) of the pool, the pool filtration flow rate may not be greater than the rate needed to turn over the pool water volume in six hours or 36 gpm, whichever is greater. This means that for pools of less than 13,000 gallons the pump must be sized to have a flow rate of 36 gpm or less and for pools of greater than 13,000 gallons, the pump must be sized using the following equation:

Maximum Filtration Flow Rate (gpm) = Pool Volume (gallons) / 360

5.2.2     These are maximum flow rates. Lower filtration flow rates and longer filtration times are encouraged and will result in added energy savings.

5.2.3     Pools with auxiliary pool loads must use either a multi-speed pump or a separate pump for each auxiliary pool load. For example, if a spa shares the pool filtration system, either a multi-speed pump must be used or a separate pump must be provided to operate the spa. If the pool system can be served by one pump of less than 1.0 total horsepower in capacity, the pump may be single speed.

5.3   Pool filter pump sizing, flow rate, and filter pump control.

5.3.1   Filtration pump motors with a capacity of 1.0 total horsepower or more shall be multi-speed.

5.3.2. Select a pool filtration pump from the California Energy Commission’s Appliance Efficiency Database for Residential Pool Pumps, or the APSP Appliance Efficiency Pool Pump Database.

5.3.2.1.For pools equal to or less than 17,000 gallons, a filter pump shall be chosen such that the flow rate listed for Curve A is less than the maximum filtration flow rate calculated according to Section 5.2.1 (six-hour turnover rate). For multi-speed and variable-speed filter pumps, at least one speed shall have the flow listed for Curve A that is less than the maximum filtration flow rate calculated according to Section 5.2.1 (six-hour turnover rate).

5.3.2.2 5.3.3  For pools greater than 17,000 gallons, a filter pump shall must be chosen such that the listed flow rate at Curve C is less than the maximum filtration flow rate calculated according to Section 5.2.1 (six-hour turnover rate). For multi-speed and variable-speed filter pumps, at least one speed shall have the flow listed for Curve C that is less than the maximum filtration flow rate calculated according to Section  5.2.1 (six-hour turnover rate).

5.3.3 5.3.2.. The maximum filter pump performance limits in Sections 5.3.2.1 and 5.3.2.2 are calculated based on pool gallons, where the filter pump performance increases proportional to the size of the pool. In the same way, pipe, filter and backwash valve (when used) will increase in size proportional to pool volume.

5.3.4. 5.3.3.1 System equation used by pool filter pump manufacturers: The pool filter pump head and flow rate shall be calculated using the following system equation:

H = C X F2

Where:

H is the total system head in feet of water.

F is the Maximum Filtration Flow Rate in gallons per minute (gpm) calculated according to Section 5.2.1 (six-hour turnover rate).

C is a coefficient based on the volume of the pool:

C = 0.0167 for pools less than or equal to 17,000 gallons.

C = 0.0082 for pools greater than 17,000 gallons.

and;

5.3.4    Filtration pumps shall be sized, or if programmable, shall be programmed, so that the filtration flow rate is not greater than the rate needed to turn over the pool water volume in 6 hours or 36 gpm, whichever is greater; and

5.3.5    Pump motors used for filtration with a capacity of 1 total horsepower or more shall be multi-speed; and

5.3.6    Each auxiliary pool load shall be served by either separate pumps or the system shall be served by a multi-speed pump; and

EXCEPTION: Filter pumps if less than 1 total horsepower may be single speed.

5.3.5 5.3.7     Multi-speed pumps must have controls that default to the filtration flow rate when no auxiliary pool loads are operating. The controls must also default to the filtration flow rate setting within 24 hours and must have a temporary override capability for servicing.

5.3.65.3.8     A time switch or similar control mechanism must be installed as part of the pool water filtration control system that will allow all pumps to be set or programmed to run only during the off-peak electric demand period and for the minimum time necessary to maintain the water in the condition required by applicable public health standards.

EXCEPTION: Pool filter pumps with integrated and/or included timer and motor control without which the motor will not run and which comply with Section 4.2.1.

5.4   System equipment

5.4.1   Filters sizing.
Filters shall be at least the size specified in NSF/ANSI 50 for public pool intended applications based on the maximum flow rate through the filter.

5.4.1.1    The filter factors that must be used are (in ft2/gpm):

§ Cartridge                              0.375 (gpm/ft2)

§ Sand                                     15 (gpm/ft2)

§ Diatomaceous Earth               2 (gpm/ft2)

5.4.2    Backwash valves. 
Minimum diameter of backwash valves shall be 2 inches or the diameter of the return pipe, whichever is greater.

5.5   System piping and circulation.

5.5.1    Pool piping and pipe fittings shall be sized so that the velocity of the water at the maximum flow rate does not exceed 8 feet per second in the return line and 6 feet per second in the suction line. Velocity calculations for branch piping flow shall allow variations in pipe sizes.

EXCEPTION: Equipment connections and internal piping, including, but not limited to, suction safety systems, pumps, heaters, and sanitizing devices.

5.5.1.1. Velocity calculations for branch piping flow shall allow variations in pipe sizes provided there are no valves capable of isolating flow through one branch. Branch piping is shown as the thin line in Figure 1.

Figure 1

5.5.2 5.5.1. For pool filtration pumps without an integrated strainer basket, a length of straight pipe that is at least 4 pipe diameters shall be installed before the pump.

5.5.3 5.5.2    Solar heating.  At least 18 inches of horizontal or vertical pipe shall be installed between the filter and the heater or dedicated suction and return lines, or built-in or built-up connections shall be installed to allow for the future addition of solar heating equipment.

5.6    Directional inlets.
         The pool shall have directional inlets that adequately mix the pool water.

[1] Association of Pool and Spa Professionals (APSP) [formerly National Spa and Pool Institute (NSPI)], 2111 Eisenhower Avenue, Alexandria, VA 22314

[2] Hydraulic Institute, 6 Campus Drive, First Floor North, Parsippany NJ, 07054-4406, (973) 267-9700, www.pumps.org

[3] IEEE Corporate Office, 3 dark Avenue, 17th Floor, New York, NY 10016-5997, (212) 419-7900, www.ieee.org

[4] National Fire Protection Association (NFPA) 1 Batterymarch Park, Quincy, MA 02169-7471, (617) 770-3000, www.nfpa.org

[5] NSF International, 789 Dixboro Road, Ann Arbor, MI 48113-0140, (734) 769-8010, www.nsf.org

FLORIDA STANDARD NO. 2 3 (FL-2 3)

FLORIDA REGULATORY REQUIREMENTS FOR PORTABLE ELECTRIC SPA ENERGY EFFICIENCY

The following regulatory requirements shall constitute Florida Standard FL-2 3 and provide compliance criteria for section 403.9.5 of the Florida Building Code, Energy Conservation Code. These requirements follow an Association of Pool & Spa Professional (APSP)a draft national standard for portable electric spa energy efficiency that is currently obtaining ANSI approval.

SECTION 1.

SCOPE

1.1           These requirements apply to factory built residential portable electric spas that are used for bathing and are operated by a private an owner.

1.2           This standard is meant to establish minimum energy efficiency requirements for portable electric spas. This standard shall be met notwithstanding certain variations in equipment, materials, and design (Refer to ANSI/NSPI-6).

1.3           These requirements do not apply to public spas, permanently installed residential spas or other spas, such as those operated for medical treatment, physical therapy or other purposes. Swim-spas and portions of combination spas/swim-spas are included in this standard.

1.4           Other standards are referenced in this standard for items not covered.

SECTION 2.

NORMATIVE REFERENCES

APSP-6 Standard for Portable Spas1

ISO/IEC 17025General Requirements for the Competence of Calibration and Testing Laboratories

ISO/IEC Guide 65 General Requirements for Bodies Operating Product Certification Systems

SECTION 3.

DEFINITIONS

AMBIENT TEMPERATURE – Air temperature inside testing chamber.

ANCILLARY EQUIPMENT – Additional components used in the construction of the spa beyond pumps, heaters and control systems.

CERTIFICATION BODY (CB) – An independent third party that operates a product, process or service certification system.

CHAMBER – A controlled environment suitable for conducting energy efficient testing Climate controlled test room.

COVER, SPECIFIED – The cover that is provided or specified by the spa manufacturer.

ENERGY EFFICIENCY STANDARD – A performance standard expressed in numerical form, such as energy factor, EER, or thermal efficiency. Using less energy to provide the same level of energy service.

FILL VOLUME - The halfway point between the bottom of the skimmer opening and the overflow level top of the spa. In the absence of a If there is no wall skimmer, the fill volume is six inches below the overflow level of the spa. the spa shall be filled with water to six inches below the top of the spa.

FILTER CYCLE - The period when the control system activates a pump intended to move water through a filter media.

GALLON – Means U.S. liquid gallon

HEATING CYCLE – The period when the temperature regulating system activates the heating component for the purpose of increasing the water temperature.

HOT TUB – See Spa

INGROUND SPA - Non-portable, non-self-contained spa (Refer to ANSI/NSPI -3 Permanent Inground Spas)

NORMALIZE – Calculation of power consumption to eliminate temperature bias.

NRTL – Nationally Recognized Test Laboratory

POWER FACTOR – The ratio of watts to volt-amperes of an AC circuit.

PURGE CYCLE - The period when the control system activates a pump intended to rapidly move water throughout the spa.

SKIMMER, VENTED – A suction opening intended to remove floating debris from the water surface and to be installed where part of the water intake opening is open to atmospheric pressure.

SPA – A product intended for the immersion of persons in heated water circulated in a closed system, and not intended to be drained and filled with each use. A spa usually includes a filter, a heater (electric, solar, or gas), a pump or pumps, and a control, and may also include other equipment, such as lights, blowers, and water sanitizing equipment.

Permanent Residential Spa- A spa in which the water heating and water circulating equipment is not an integral part of the product. The spa shall be intended as a permanent plumbing fixture and shall not be intended to be moved. (Refer to ANSI/NSPI-3 1999 Standard For Permanently Installed Residential Spas.)

Public Spa - Any spa other than a permanent residential spa or residential portable spa which is intended to be used for bathing and is operated by an owner, licensee, concessionaire, regardless of whether a fee is charged for use. (Refer to ANSI/NSPI-2 1999 Standard for Public Spas.)

Residential Portable Spa - Either Self-Contained or Non-Self-Contained (Refer to ANSI/NSPI-6 1999 Standard For Residential Portable Spas.):

Self Contained Spa - A factory built spa in which all control, water heating and water circulating equipment is an integral part of the product. Self-contained spas may be permanently wired or cord connected.

Non-Self-Contained Spa - A factory built spa in which the water heating and circulating equipment is not an integral part of the product. Non-self-contained spas may employ separate components such as an individual filter, pump, heater and controls, or they may employ assembled combinations of various components.

STANDARD COVER – The cover that is provided or specified by the spa manufacturer.

STANDBY MODE - All settings at default as shipped by the manufacturer, except water temperature which may be adjusted to meet the test conditions. No manual operations are enabled.

SWIMSPA –Variant of a Residential Portable Spa which consists of a large unobstructed volume of water primarily designed for, and constructed with specific equipment required to produce a water flow intended to allow recreational physical activity including, but not limited to, swimming in place.

Swim spas may include peripheral jetted seats intended for water therapy, heater, circulation and filtration system, or may be a separate distinct portion of a combination spa/swim spa with separate controls.

SWIM SPA - Variant of a factory built residential portable spa consistingwhich consists of a large unobstructed volume of water that allows the 99% male/femalepopulation to swim. The design and construction of a swim spa includes specific features and equipmentutilizing swim jets for a treadmill-like workout, primarily designed for, and constructed with specific equipment required to produce a water flow intended to allow recreational physical activity including, but not limited to, swimming in place.

Swim spas may include peripheral jetted seats intended for water therapy, heater, circulation and filtration system, or may be a separate distinct portion of a combination spa/swim spa and may have with separate controls.

WATT HOUR – Energy consumed over a period of one hour.

SECTION 4

QUALIFICATION OF TESTING LABORATORIES

AND CERTIFICATION BODIES

4.1 All Certification Bodies (CB) shall be accredited by a member of IAF (International Accreditation Forum) using ISO/IEC Guide 65, General Requirements for Bodies Operating Product Certification Systems.

4.2 All testing laboratories shall be qualified by a CB.

4.2.1 The CB shall assess the testing laboratory’s quality system to determine that it satisfies applicable requirements of ISO/IEC 17025.

NOTE: Different parts of ISO/IEC 17025 are applicable to first-party, second-party and third-party laboratories.

4.2.2 Where a laboratory is accredited to ISO/IEC 17025 by a member of ILAC (International Laboratory Accreditation Council) the CB is permitted to accept such accreditation as evidence of conformity to ISO/IEC 17025, in whole or in part.

4.2.3 The CB shall additionally assess the laboratory’s facilities, test equipment, testing personnel and test procedures, to establish that the laboratory is competent to perform the tests in this standard.

4.2.4 The CB shall provide a copy of the assessment report to the testing laboratory, and retain a record of the assessment. Any discrepancies identified in the assessment report shall be cleared before the laboratory is deemed qualified.

4.3 Testing laboratories shall demonstrate qualification on a continuing basis.

4.3.1 The CB shall audit the testing laboratory for ISO/IEC 17025 compliance and testing competence on a regular basis.

4.3.1.1 Laboratories accredited by an ILAC member shall be audited at intervals not exceeding three (3) years.

4.3.1.2 Non-accredited laboratories shall be audited annually by the CB.

4.3.2 The CB shall provide a copy of the audit report to the testing laboratory, and retain a record of the audit. Any discrepancies identified in the audit report shall be cleared before the laboratory is deemed re-qualified.

SECTION 54.

TEST METHOD

54.1 Purpose: To measure the energy consumption of a portable electric spa in standby mode, using a repeatable and reproducible test procedure. The results will be used to calculate the standby power demand.

5.2 The test facility and equipment will be audited as indicated in 4.3 of this standard to confirm they meet the requirements of this standard. Documentation showing facility and test equipment compliance to this standard from the CB will be maintained on side by the test facility and made available as required (See Appendix B).

5.3 All equipment shall be calibrated at intervals not to exceed eighteen months, and traceable to NIST or other national standard.

5.4 4.2 Test Equipment

Note: All equipment shall be calibrated and traceable to the National Institute of Standards and Technology (NIST).  The test facility and equipment will be evaluated by a NRTL to confirm they meet the requirements of this standard.   Documentation showing facility and test equipment compliance to this standard from the NRTL will be maintained on site by the test facility and made available as required.

5.4.1.4.2.1 Recording Watt Hour meter – Accuracy: Class-2 or better.

5.4.2.4.2.2 Temperature measurement system - Accuracy: +/- 1°F

5.4.3.4.2.3 Water meter to measure fill water in gallons – Accuracy: +/- 1.5%

5.5.4.3 Test Conditions

The test method for portable electric spas is as follows:

5.5.1.4.3.1 Minimum continuous testing time shall be 72 hours.

5.5.2.4.3.2 The spa shall be filled with water to the halfway point between the bottom of the skimmer opening and the top of the spa. In the absence of a If there is no wall skimmer, the fill volume is six inches below the overflow level  spa shall be filled with water to six inches below the top of the spa.

5.5.2.1 4.3.2.1 Measure and record fill volume (V) while filling according to 4.3.2.

5.5.3.4.3.3 The water temperature of the spa or spa portion of a combination swim spa shall be a minimum of 100°F, for the duration of the test. The water temperature of the swim spa or swim portion of a combination swim spa shall be a minimum of 85°F, for the duration of the test.

5.5.4.4.3.4 The ambient air temperature shall be a maximum of 63°F for the duration of the test.

5.5.5.4.3.5 The manufacturer’s specified standard cover that comes with the unit shall be used during the test.

5.6 4.4 Test Procedure

5.6.1 4.4.1 The test shall start when the water temperature has been at 102°F, ±2°F, (at 87°F, ± 2°F for swim spas) for at least a four hour stabilizing period.

5.6.2 4.4.2 Record water temperature.

5.6.2.1 4.4.2.1 The thermocouple shall be located three to five inches below the water level and centrally located relative to the shape of the spa.

5.6.3 4.4.3 Record ambient air temperature at one point located twelve to eighteen inches a maximum of one to one and a half feet above spa cover level and six to eight inches from the chamber wall . The temperature probe will be positioned and out of direct airflow from the chamber temperature control system and/or circulation fan.

5.6.4 4.4.4  Data Recording

5.6.4.1 4.4.4.1 Record temperatures at a maximum interval of 5  4 minutes.

5.6.4.2 4.4.4.2 Measure voltage, current, and power factor (OPTIONAL) at a maximum interval of 5 4 minutes.

5.6.4.3 4.4.4.3 Record watt-hours, voltage and current used during entire Test Period.

5.6.4.4 4.4.4.4 Record elapsed time during Test Record.

5.6.5 4.4.5 Record the total energy use for the period of test, starting at the end of the first heating cycle after the stabilization period and finishing at the end of the first heating cycle after 72 hours has elapsed.

Exception: For spas without heaters, substitute heating cycle with filter or purge cycle.

5.6.6 4.4.6 The unit shall remain covered and in the default operation mode during the test. Energy-conserving circulation functions, if present, must not be enabled if not appropriate for continuous, long-term use. The minimum filtration rate shall be 12 water turns within a 24 hour period. Ancillary equipment including, but not limited to lights, audio systems, and water treatment devices, shall remain connected to the mains but may be turned off during the test if their controls are user accessible.

SECTION 6 5

FORMULAS

6.1 5.1 The measured standby power (Pmeas) shall be determined by E/t:

Pmeas = E/t

Where:

E = total energy use during the test (Wh)

t = length of test (hr)

6.2 5.2 The measured standby power (Pmeas) shall be normalized (Pnorm) to a temperature difference of 37°F using the equation:

Pnorm = Pmeas (? Tideal / ? Tmeas)

Where:

? Tideal = 37°F

? Tmeas = Twater avg – Tair avg

Twater avg = Average water temperature during test

Tair avg = Average air temperature during test.

6.3 5.3 The normalized standby power (Pnorm) shall not be greater than maximum standby power (Pmax):

Pmax = 5(V²/³)

Where:

V = fill volume in gallons

SECTION 7 6.

LABEL REQUIREMENTS

7.1 6.1 The manufacturer shall include either on or in close proximity to the spa’s product label the standby watts rating.

7.2 6.2 Wording to be in the following format:

Per ANSI-14   Measured Standby Power Consumption XXXX watts/hr (Maximum Allowable Standby Power Consumption XXXX watts/hr)

APPENDIX A (Informative)

This appendix is not part of the American National Standard and is included for information only.

Minimum Chamber Requirements

Chamber internal dimensions:

Minimum 7 feet high

Minimum 1 foot from spa to chamber wall or other internal barrier.

Air flow: If air circulation from the air temperature control equipment is intermittent, install 1 fan in one corner of the chamber, 6 feet from the floor. Direct toward the center of the floor. The fan should move at least 80 CFM of air, and not more than 100 CFM. If the air temperature control equipment continuously circulates air in the chamber, no fan is required.

Chamber Insulation: Walls shall be insulated adequately to maintain proper ambient temperatures.

Chamber Floor: The floor may be insulated with 2” thick R-13 polisocyanurate with radiant barrier on both sides. This insulation shall be laid directly on a level concrete floor or slab or other firm, level surface created for it. The insulating layer shall be sheeted with minimum 1/2” thick plywood to protect the insulation layer and provide a smooth surface to properly position the spas to be tested.

APPENDIX B (Informative)

This appendix is not part of the American National Standard and is included for information only.

Procedure for Establishing Test Facility and Equipment Compliance

This section provides an evaluation procedure to qualify a test facility for the sole purpose of testing to the requirements outlined in ANSI/APSP 14 Portable Spa Energy Efficiency Standard.

All evaluations are to be conducted by a CB as defined in Section 3 of this standard.

Any testing performed, data and results obtained, or facility and equipment used prior to the adoption of ANSI/APSP 14 is exempt from the requirements of Appendix B.

1. Test Chamber

1.1 The test chamber will be evaluated to establish compliance with the construction requirements outlined in Appendix A.

1.2 The test chamber must demonstrate the capability to maintain the test environment(s) called for in Section 4 of this standard.

1.2.1 The test chamber will be evaluated operating at the test parameters for a minimum of three hours.

2. Data Measuring and Recording Equipment

2.1. The operator of the test facility will provide proof of calibration traceable to NIST or other national standard for all equipment used to measure and collect data as outlined in Section 4 of this standard. 2.2 The maximum period before equipment recalibration is required will be eighteen months from its previous calibration date.

2.2.1 If the test equipment comes from the manufacturer with a Certificate of Calibration, the time frame for recalibration will be a maximum of eighteen months from date of purchase.

2.3 Calibration records (electronic or hard copy), will be kept by the test facility and made available upon request by the evaluating CB.

3. Training of Personnel

3.1 The test facility will designate the person, and alternates, responsible for training other employees in the requirements of performing the ANSI 14 Portable Spa Energy Efficiency Testing.

3.1.1 Training records will include:

The person(s) doing the training

Date(s) the training took place

Facility and chamber used

3.2 The test facility will keep employee training records and provide them to the CB upon request.

4. Record Maintenance

4.1 Upon request of the CB, the test facility will provide a copy of all forms used, (electronic or hard copy), to record the required test data.

4.2 The CB may review previous testing performed for compliance to this standard.

5. Documentation of Test Facility Compliance

5.1 If the test facility successfully completes the evaluation, the CB will issue the appropriate document(s) indicating compliance with Appendix B of this standard.

5.2 If found non-conforming, the CB will issue a report of corrective actions the test facility must address to be compliant.

5.2.1 A second site visit to verify the corrective actions will be at the discretion of the CB.

5.3 Upon the test facility addressing and providing the necessary documentation, the CB will issue the appropriate document(s) indicating compliance with Appendix B of this standard.

[1] Association of Pool & Spa Professionals (APSP) (formerly National Spa and Pool Institute (NSPI), 2111 Eisenhower Avenue, Alexandria, VA 22314

EN4864