Transition Guide

to the

2004 Florida Codes

Changes to the State Agency Regulations in Chapter 4

The following table outlines the changes that occurred to the state agency regulations from the 2001 Florida Building Code, Building to the 2004 Florida Building Code, Building (including the 2005 Supplement) in Chapter 4 as a result of Florida-Specific Amendments.  The changes are shown in legislative format to provide the most benefit in understanding the nature of the changes that occurred.

| 2001 FBCB Section | 2004 FBCB Modifications |
| --- | --- |
|  | Hospitals |
| 419.2.1.1 | 419.2.1.1 The fire codes described in Chapter 69A 4A-53 Uniform Fire Safety Standards for Hospitals and Nursing Homes, F.A.C. |
| 419.3.1 | 419.3.1 In addition to the codes and standards referenced in Section 419.2 of the Code, the following minimum standards of construction and specified minimum essential facilities, shall apply to all new hospitals, all additions, alterations or renovations to an existing hospital and to outpatient facilities owned or operated by a hospital as described in Chapter 395.0163 Florida Statues, on the effective date of the Code. |
| 419.3.2.1 | 419.3.2.1 For planning purposes, a full-size bed is assumed to be measure 3 feet 6 inches (1.05 m) by 7 8 feet 0 inches (2.10 2.44 m). |
| 419.3.3.1 | 419.3.3.1 Toilet facilities are required for each Critical Care Bed. When portable or built-in toilets are utilized in lieu of individual toilet rooms room toilets, provisions shall be made for user privacy, and the storage, servicing and odor control of the toilet units. In addition to these provisions, when a permanently built in toilet is located inside of the critical care room, there shall be a toilet exhaust fan located directly above the fixture and a permanently installed washable partition at least 5 feet high (1.52 m) located between the toilet fixture and the bed. |
| 419.3.3.2 | 419.3.3.2 Sliding doors used for access to critical care rooms shall be equipped with a break away feature, that shall breakaway in the open or closed position of the door, shall either be manual or power operated, shall have a fully recessed track or be trackless, and shall be smoke resistant if located on an exit access corridor. |
| 419.3.5.1 | 419.3.5.1 When outpatient surgery is provided in the Surgical Suite of the General Hospital, it shall comply with the requirements for outpatient surgery in Section 7.7 and Section 9.5 of The Guidelines. When outpatient surgery is provided in a separate unit surgical suite of the General Hospital or in a separate facility, it shall comply with the requirements for outpatient surgery in Section 9.5 of The Guidelines. |
| 419.3.8.2 | 419.3.8.2 When the mobile facility unit is located in a roadway or a parking lot or structure, there shall be sturdy walls, fences or bollards around the immediate site to prevent collisions with the unit by other vehicles. |
| 419.3.8.8 | 419.3.8.8 The electrical systems in the mobile unit facility shall comply with the requirements of Chapter 27 of the Florida Building Code, Building, Section 7.32 of The Guidelines for the type of service to be provided and with Section 419.3.15 of the code. |
| 419.3.8.9 | 419.3.8.9 The mechanical systems in the mobile unit facility shall comply with the requirements of Section 7.31 of the Guidelines for the type of service to be provided and with Section 419.3.11 and Section 419.3.13 of the code. |
| 419.3.9.3 | 419.3.9.3 Soap dispensers shall be provided at all hand washing facilities. If soap dishes are used, Oonly fully recessed soap dishes shall be permitted in patient tubs or showers. |
| 419.3.9.8 | 419.3.9.8 Where electrical conduits, cable trays, ducts and utility pipes pass through the smoke partition, the utilities shall be located so that access is maintained to adjacent wall surfaces and to all damper access panels. The details shall show the studs and reinforcing half studs so that proper support is provided for the wall surfacing material. There shall be a minimum clearance of 6 inches (152 mm) between all conduits, piping and duct work that are parallel or adjacent to at corridor all fire and fire/smoke rated walls to facilitate the inspection of these walls. |
| 419.3.16 | 419.3.16 Electrical Requirements. (See Section 7.32 of The Guidelines for other requirements) All material, including equipment, conductors, controls, and signaling devices, shall be installed to provide a complete electrical system with the necessary characteristics and capacity to supply the electrical facility requirements as shown in the specifications and as indicated on the plans. All materials and equipment shall be factory listed or field labeled as complying with the applicable standards of Underwriter’s Laboratories, Inc., or other established standards . Field labeling of equipment and materials will be permitted only when provided by a Nationally Recognized Testing Laboratory (NRTL) that has been certified by the Occupational Safety & Health Administration (OSHA) for that referenced standard |
| 419.4.2.7.1 | 419.4.2.7.1 There shall be an independent on-site supply (i.e., water well) or on-site storage capability (i.e. empty water storage containers or bladders) of potable water at a minimum quantity of 3 gallons (14 L) per in-patient in the new facility or wing or floor addition to an existing facility per day during and immediately following a disaster. For planning purposes the number of in -patients shall be determined in writing by the facility. Hot water in boilers or tanks shall not be counted to meet this requirement. |
| 419.4.2.7.2 | 419.4.2.7.2 There shall be an independent onsite supply or storage capability of potable water at a minimum quantity of 1 gallon per facility staff, and other personnel in the new facility or wing or floor addition to an existing facility per day during and immediately following a disaster. For planning purposes, the number of these personnel shall be estimated determined in writing by the facility. Hot water in boilers or tanks shall not be counted to meet this requirement. |
|  | Nursing Homes |
| 420.4.2.7 | 420.4.2.7 There shall be an independent on-site supply (i.e. water well) or on-site storage capability (i.e. empty water storage containers or bladders) of potable water at a minimum quantity of 3 gallons per resident served per day during and immediately following a disaster. For planning purposes the number of residents shall be determined in writing by the facility. Hot water in boilers or tanks shall not be counted to meet this requirement. |
| 420.4.2.7.2 | 420.4.2.7.2 There shall be an independent on-site supply or storage capability of potable water at a minimum quantity of 1 gallon per facility staff, and other personnel in the facility per day during and immediately following a disaster. For planning purposes, the number of these personnel shall be estimated determined in writing by the facility. Hot water in boilers or tanks shall not be counted to meet this requirement. |
|  | Ambulatory Surgical Centers |
| 421.3.4.2 | 421.3.4.2 No doors shall swing into the corridor except those to small closets or small mechanical or electrical rooms that cannot be usefully occupied with the doors in the closed position. doors and doors to small mechanical or electrical rooms. |
| New | 421.3.4.8 The use of sliding pocket doors to patient use toilets shall not be permitted. |
|  | State Requirements for Educational Facilities |
| 423.1 | 423.1 Scope: Public educational facilities. Public educational facilities shall comply with the Florida Building Code and the Uniform Fire Safety Standards as adopted by the State Fire Marshal. These are minimum standards; boards may impose more restrictive requirements. Additional requirements for public educational facilities in Florida, including public schools and public community/junior colleges, are found in these standards. Note: Other administrative and programmatic provisions may apply. See Department of Education Rule 6-2 and Chapter 1013 235, Florida Statutes |
| 423.3.2 | 423.3.2 Owner Review and Inspection. A school board or community college board which undertakes the construction, remodeling, renovation, lease, or lease-purchase of any educational plant or ancillary facility, or day labor project, regardless of cost or fund source, shall review construction documents as required by law in Sections 1013.38 235.017, Florida Statutes., and Section 553.80(6), Florida Statutes, and shall ensure compliance with requirements of law, rule, and the Florida Building Code and the Uniform Fire Safety Standards as adopted by the State Fire Marshal. Section 553.80(6), Florida Statutes, states that district school boards and community college boards shall provide for plan review and inspection for their projects. They shall use personnel certified under Part XII of Chapter 468, Florida Statutes, to perform the plan reviews and inspections or use one of the options provided in Section 1013.38 235.017, Florida Statutes. Under this arrangement, school boards and community college boards are not subject to local government permitting, plan review, and inspection fees. |
| 423.4.2 | 423.4.2 FEMA. Federal Emergency Management Agency Rules and Regulations 44 CFR, Part 59 and 60, Revised as of October 1, 1995. In Flood Zones A1 through A30, AE, AH, and AO (one-hundred-year flood plain) the finished floor at the lowest entry level shall be a minimum one (1) foot above the base flood elevation. |
| 423.4.3 | 423.4.3 Florida Statutes and State Rules. Including, but not limited to, Chapters 1013 235, 240, 255, 468, 471, 481, 489, 553, 633, and Section 287.055, F.S., and various state rules as applicable to specific projects. |
| 423.5.5.2 | 423.5.5.2 Enclosed Courtyard. A courtyard which is not roofed by more than 50% of the courtyard area and which is substantially surrounded by a building(s) on two sides or more and each opening to the exterior is less than 40 feet in width. The courtyard area shall be calculated for maximum occupancy as an assembly space and the number and size of remotely located exits shall be calculated for the maximum possible load. The maximum possible load is greater of the calculated capacity of the courtyard or the load imposed by the surrounding spaces. An enclosed courtyard may be used as a component of exit access provided that the walls and wall openings meet the requirements of the Florida Building Code, Building Tables 601 and 602 and the maximum travel to the exit discharge does not exceed 150 feet from any point within the enclosed courtyard. An enclosed courtyard cannot serve as the exterior for exiting or for emergency rescue openings. |
| 423.5.5.3 | 423.5.5.3 Roofed Courtyard. A courtyard which is roofed by more than 50% of the courtyard area in any manner. Courtyards may be used for assembly spaces and may not be used as a component of exiting from adjacent spaces. |
| 423.7.3 | 423.7.3 Location of Fire Extinguishers and Blankets. Fire extinguishers may be located inside student-occupied spaces provided they are placed adjacent to the primary exit door, and the room door remains unlocked when the facility is occupied, and a permanently affixed sign, with a red background and white letters (raised letters and braille), reading "FIRE EXTINGUISHER INSIDE" is placed on the outside adjacent to the door. Fire extinguisher cabinets shall not be locked. Fire blankets shall be located in each laboratory and each shop where a fire hazard may exist. Fire extinguishers and fire blankets shall be readily accessible and suitable for the hazard present and shall not be obstructed or obscured from view. Extinguishers and blankets shall be on hangers or brackets, shelves, or cabinets so that the top of the extinguisher or blanket is not more than 54 inches above finish floor (AFF) and complies with state and federal accessibility requirements. All extinguishers shall be installed and maintained in accordance with NFPA. Extinguishers shall remain fully charged and operable at all times and have a current tag to indicate compliance. |
| 423.7.5 | 423.7.5 Fire Alarm Sending Stations. Sending stations may be located inside student-occupied spaces, adjacent to the primary exit door only if the door to the occupied space is unlocked at all times while the facility is occupied. When located inside a student occupied space, a permanently affixed sign reading "FIRE ALARM PULL STATION INSIDE" shall be placed outside that space adjacent to the door. This sign shall have a red background with white letters (raised letters and braille). Sending stations shall be mounted to meet accessibility requirements. |
| 423.7.7 | 423.7.7 Unoccupied Rooms and Concealed Spaces. Rooms or spaces for storage, custodial closets, mechanical rooms, spaces under stages with wood structures and other unoccupied or unsupervised spaces in a building shall have automatic smoke or heat detector devices installed. Any concealed space with exposed materials having a flame spread rating greater than Class A, including crawl spaces under floors, interstitial spaces between ceiling and floor or roof above and attic spaces, shall be equipped with heat detector devices. Smoke and heat detector devices shall be installed in accordance with NFPA 72. In fully sprinklered buildings, heat detectors are not required. Smoke detectors, where required by the Florida Fire Prevention Code, must remain. |
| 423.8.1.1 | 423.8.1.1 Educational Occupancy. School board educational facility projects whether owned, lease-purchased or leased shall comply with the Educational Occupancy and Assembly Occupancy portions of the above referenced codes as applicable, except where in conflict with this section. The support spaces such as media centers, administrative offices, auditoriums, gymnasiums, and cafeterias and kitchens, located within educational facilities are not separate occupancies. |
| 423.8.2 | 423.8.2 Space Standards. School board and community college board facility sizes shall use standards in the "Size of Space and Occupant Design Criteria Table" found in the Department of Education document. State Requirements for Educational Facilities (SREF). Exiting from occupied spaces shall comply with Table 1004.1.2 of the Florida Building Code, Building. |
| 423.8.3.1 | 423.8.3.1 Non-combustible Type I, II, or IV. The minimum construction Type for one-and two-story public educational facilities shall be non-combustible Type I, II or IV construction or better. |
| 423.8.3.2 | 423.8.3.2 Type II I. Facilities three stories or more shall be Type II I construction or better. |
| 423.8.3.3 | 423.8.3.3 Type III IV. When Type III IV construction is used, wood shall be exposed and not covered by ceilings or other construction. |
| 423.8.3.4 | 423.8.3.4 Exceptions to types of construction: 1. Covered walkways open on all sides may be Type V or Type VI construction. 2. Single story dDugouts, press boxes, concession stands, related public toilet rooms, detached covered play areas, and non-flammable storage buildings which are detached from the main educational facility by at least 60 feet, may be Type V or Type VI construction. |
| 423.8.7 | 423.8.7 Life Cycle Cost Guidelines for Materials and Building Systems. An analysis shall be included, as required by Section 1013.37(1), Florida Statutes, which evaluates building materials and systems, life cycle costs for maintenance, custodial, operating, and life expectancy against initial costs, as described in Section 1013.(1)(e)4., Florida Statutes, Standards for evaluation of materials are available from the Department in a publication entitled "Life Cycle Cost Guidelines for Materials and Building Systems for Florida's Public Educational Facilities." |
| 423.8.8 | 423.8.8 Safe School Design. School boards should shall design educational facilities and sites including pre-K through 12, vocational and community colleges to enhance security and reduce vandalism through the use of "safe school design" principles. Safe School design strategies are available from DOE/Educational Facilities and include but not limited to the following: |
| 423.10.1.1 | 423.10.1.1 Required Locations. Fencing is required to separate students from potential harm, and shall be provided in the following locations: at school board kindergarten through grade 5 12 facilities: 423.10.1.1.1 Kindergarten through grade 12. Exposed mechanical, plumbing, gas, or electrical equipment located on ground level. 423.10.1.1.2 Kindergarten through grade 5. Special hazards as identified by the authority having jurisdiction including retention ponds whose permanent water depth or whose water depth over a 24 hour period exceeds 1 foot, deep drainage ditches, canals, highways, play fields adjacent to roadways. 423.10.1.1.3 Kindergarten through grade 12. All child care and kindergarten play areas. |
| 423.10.2.1 | 423.10.2.1 Covered Walks. All buildings in K-12 educational facilities shall be connected by paved walks and accessible under continuous roof cover. New relocatable classroom buildings shall be connected to permanent buildings by paved covered walks where applicable. Roofs for covered walks shall extend 1 foot beyond each side of the designated walkway width. Gutters or other water funneling devices shall prevent storm water from pouring onto or draining across walks. |
| 423.10.4 | 423.10.4 Building Setbacks. Building Setbacks from the property line, including relocatables, shall comply with local setback requirement minimums, but shall, at a minimum be 25 feet (7620 mm) where site size permits or shall comply with local setback requirements if less than 25 feet (7620 mm). |
| 423.11 | 423.11 Wood: Fire-Retardant Treated Wood (FRTW). Fire-retardant treated wood shall not be used in permanent educational facilities. Only FRTW which does not contain ammonium phosphate, sulfates, or halides may be used in roof structures of non-combustible Type IV II ancillary facilities as allowed by the Florida Building Code, but only under the following conditions: |
| New | 423.11.7 Wood Studs. Interior non-load-bearing wood studs or partitions shall not be used in permanent educational and auxiliary facilities or relocatable buildings. Exception: Historic buildings to maintain the fabric of the historic character of the building. |
| 423.13.1.1 | 423.13.1.1 Doors for steam rooms, locker rooms, shower rooms, individual and group toilet rooms shall swing in the direction of exit travel, and shall always be operable for exitings from the inside. |
| 423.13.6 | 423.13.6 Hardware. Doors and gates shall be equipped with hardware which will allow egress at all times without assistance. Projecting hardware on doors swinging into a means of egress is not considered an obstruction if the door opens flat against the wall. No padlock, chain, hasp, lock, deadbolt, or other device shall be installed at any time on any door used for exiting. Doors which by code require closers and other door subject to wind exposure shall be equipped with closers to prevent slamming and uncontrolled opening. All doors opening into smoke tight exit access corridors shall be self-closing or automatic-closing. |
| 423.13.8 | 423.13.8 Windows. Natural light and ventilation requirements for new construction shall be satisfied by windows with operable glazing, providing a net free open area equivalent to 5 percent of the floor area, in all classrooms on the perimeter of buildings, where required by Chapter 1013, Florida Statutes. Auxiliary spaces, music rooms, gyms, locker and shower facilities, laboratories requiring special climate control, and large group instructional spaces having a capacity of more than 100 persons need not have operable windows for the purpose of providing natural light and ventilation. Emergency access, emergency rescue, and secondary means of egress windows may be included in the calculation to comply with this requirement. Projecting and awning windows shall not be located below door head height if in, or adjacent to, a corridor or walkway. If a security/storm screen or grille is installed on the outside of an emergency access, rescue, or egress window assembly then that security/storm screen or grille together with the emergency rescue window assembly, shall be operable from the inside by a single operation without the use of tools to allow for exit under emergency conditions. The emergency rescue window shall be identified by signage and the release device shall be readily identifiable. |
| 423.14.2.1 | 423.14.2.1 Emergency Rescue windows: Windows for emergency rescue shall comply with NFPA 101, shall be operable from the inside by a single operation, and shall be labeled “EMERGENCY RESCUE - KEEP AREA CLEAR”. |
| New | 423.14.9 Interior Finishes 423.14.9.1 Floors. Floors in instructional spaces shall be covered with resilient material or carpet. Floors in gymnasium locker rooms, showers, drying areas, toilet rooms, kitchens, scullerys, food storage areas and can wash areas shall be impervious. 423.14.9.2 Walls. Walls in toilet rooms shall be impervious to a height of at least 4 feet (1219 mm) above the floor. Walls in kitchens, scullerys, can wash areas, shower rooms shall be impervious to a height of at least 6 feet (1829 mm) above the floor. Toilet and shower partitions shall be impervious. 423.14.9.3 Ceilings. Ceilings in group toilet rooms, kitchens, scullerys, can wash areas, showers and locker rooms shall be impervious. |
| New | 423.15.4 Toilet rooms shall be continuously ventilated during building occupancy. Exception: Individual toilet rooms shall be ventilated continuously during building occupancy or ventilation shall turn off with the light switch and run for at least 10 minutes after the light has been turned off. |
| 423.16.9 | 423.16.9 Shower Facilities. Showers shall be provided only where required by the district's educational program and, where provided, shall utilize energy saving concepts for hot water as required by Section 1013.44(2) 235.212, Florida Statutes. When provided, shower areas shall comply with the following: |
| New | 423.17.8 Ground Fault Interrupter (GFI) Receptacles. GFI receptacles shall be installed as required by NFPA 70 of Chapter 27 and in the following locations: 1. All elementary special needs classrooms receptacles. 2. All building entry vestibules receptacles. 3. All mechanical, boiler and electrical rooms receptacles. |
| 423.18.1.4 | 423.18.1.4 Classrooms and labs—Exiting capacity for classrooms shall be calculated at 20 net square feet (2 m2) per occupant. Exiting capacity for laboratories shall be calculated at 50 net square feet (5 m2) per occupant. the main floor area of a single space at the design capacity. If spaces are combined through the use of folding partitions, the capacity and exiting shall be based on the capacity of all the spaces joined. |
| 423.19.1 | 423.19.1 General. Shade/green houses shall be of Type I or II IV Construction (metal frame) capable of withstanding the appropriate wind load. |
| 423.25.5 | 423.25.5 Electrical and Standby Emergency Power System. The EHPA shall be provided with an a standby emergency electrical power system, per NFPA 70 Article 700 and 701, which shall have an outlet for coupling the capability of being connected to a backup generator or other optional power source. Where economically feasible, an equivalent photovoltaic system may be provided. The EHPA’s emergency systems includes but are not limited to: (1) an emergency lights lighting system, (2) illuminated exit signs, and fire alarm systems in the EHPA (3) fire protection system(s), alarm (campus wide) and sprinkler, and (4) minimum ventilation for health/safety purposes. The fire alarm panel shall be located in the EHPA manager’s office. A remote annunciator panel shall be located in or adjacent to the schools administrator’s office. When generators are installed, the facility housing the generator, permanent or portable, shall include be an enclosed area designated to protect the generators from wind and missile impact. Air intakes and exhausts shall be designed and installed to meet the wind load and missile impact criteria. Generators hardened by the manufacturer to withstand the area’s design wind and missile impact criteria shall be exempt from enclosed area criteria requirement. |
| 423.25.5.1 | 423.25.5.1 EHPA Lighting. Standby Emergency lighting shall be provided within the EHPAs EHPA area, EHPA manager’s office , toilet rooms, main electrical room and generator spaces and shall be should provide at least 10 footcandles (100 lux) of general illumination which can be reduced to ½ footcandle (5 lux) in the sleeping areas during the night. |
| 423.25.5.2 | 423.25.5.2 Optional Standby Circuits. Selected ventilation, fans, intercom system, and other standby circuits Additional non-life safety systems, as defined by Chapter 27 NFPA 70 Article 702 (optional standby circuits), may be supplied power, if available, by the Standby Emergency Power System. These systems shall be connected to the sStandby Emergency pPower sSystem per NFPA70, Article 702 (optional standby circuits) via an electrical sub-panel to the Standby Electrical Power System’s main electrical panel. This will allow selective or total load shedding of power if required. The fire alarm, emergency lighting, and illuminated exit signs throughout the entire campus shall remain operational and shall receive first priority to power provided by the facility Standby eEmergency pPower sSystem per Chapter 27, NFPA 70 Article 700. The systems listed are not all encompassing but are in order of priority. Local officials may request additional non-life safety systems they deem necessary for health, welfare and safety of the public during occupancy. 1. Remainder of the school’s campus security lighting (building and site) 2. Additional ventilation systems within the EHPA including heat 3. Intercom system 4. Food storage equipment 5. Additional electric receptacles, other than those required by 423.25.5.3. |
| 423.27.1 | 423.27.1 Relocatables. ..... For code requirements and other standards applicable to relocatables constructed prior to this code, which may be Type V or Type VI (wood) relocatables, see Existing Relocatables, Volume 1, Section 5(2), State Requirements for Educational Facilities as referenced in the Uniform Fire Safety Standards as adopted by the State Fire Marshal. |
| 423.27.3 | 423.27.3 Construction Type. All new relocatables constructed, purchased or otherwise acquired by a board shall be non-combustible Type I, II, or IV construction. |
| 423.27.5.4 | 423.27.5.4 Separation of Units. Type I, II, or IV, (non-combustible) relocatable units shall be separated as required by the Florida Building Code and the school site plan. |
| 423.27.7 | 423.27.7 Fire Retardant Treated Wood. Only fire retardant treated wood (FRTW) which does not contain ammonium phosphate, sulfates, or halides may be used in the roof structure of Type III IV construction, as authorized by other sections of the Florida Building Code. (no change to remainder of section) |
| 423.27.5.3.4 | 423.27.5.3 4 Separation of Units. |
| 423.27.9.1 | 423.27.9.1 Rescue. Windows for emergency rescue shall comply with NFPA 101, shall be operable from the inside by a single operation, and shall be labeled “EMERGENCY RESCUE - KEEP AREA CLEAR.” |
| 423.27.9.1 | 423.27.9.1 Rescue. Windows for emergency rescue shall comply with NFPA 101, shall be operable from the inside by a single operation, and shall be labeled “EMERGENCY RESCUE - KEEP AREA CLEAR.” |
| 423.28.2.2 | 423.28.2.2 Non-combustible. Type I, II or IV (non-combustible) construction shall be used where several relocatable units are joined under a single roof to create multi-classroom or other use spaces in excess of two thousand (2,000) square feet. |
| 423.28.2.3 | 423.28.2.3 Wood Frame. Type III or V or Type VI (wood frame) construction shall be used only for a single classroom unit of one thousand 1,000 gross square feet (93 m2) or less. Two classroom units of Type III or V or Type VI construction may be joined together, if for a single use such as exceptional education, TAP, or science, provided the single classroom does not exceed two thousand 2,000 gross square feet (186 m2), is without interior partitions (not including office, storage, and toilet) and has at least two 2 remotely located exit doors. |
| 423.28.2.5.2 | 423.28.2.5.2 Separation of Units. Type III or V or Type VI (wood frame) relocatable units are separated from each other and any permanent buildings by sufficient distance, in each direction to prevent the spread of fire and located to allow access by emergency vehicles. The locations are determined jointly by the local fire fighting authority that services the site. Type I, II or IV (non-combustible) relocatables shall be separated as required by the code. |
| 423.28.2.5.3 | 423.28.2.5.3 Minimum Setbacks. The minimum setback for wood relocatable units is at least twenty-five 25 feet (7620 mm) from the property line, unless a greater setback is required by local zoning. The minimum setback for Type I, II, or IV (non-combustible) relocatables is 25 (7620 mm) feet unless a smaller setback is permitted as required by local zoning. |
| 423.28.2.9.1 | 423.28.2.9.1 Two Doors. Single classroom units of Type III or V or Type VI (wood) construction shall have two remotely located doors opening directly to the outside. |
| 423.28.9.2 | 423.28.9.2 Door and Rescue Window. Multi-classroom units of Type I, II or IV (non-combustible) construction have a primary exit door and an emergency rescue opening in each space occupied by ten or more students, or by six or more students for relocatables designed after October 18, 1994. |
| 423.28.2.12.1 | 423.28.2.12.1 Emergency Rescue. Each multi-classroom unit of Type I, II, or IV (non-combustible) construction has a single action operable window available for emergency rescue for each classroom or student occupied space. |
| 423.28.2.15 | 423.28.2.15 Child Care/TAP. Standard classroom units of Type III or VI (wood) construction housing birth to age three 3 children, including Teenage Parent Programs (TAP), are less than two thousand 2,000 gross square feet (186 m2), and comply with additional safety requirements outlined in this section. (no change to reminder of section) |
| 423.28.2.19.1 | 423.28.2.19.1 Heat and Smoke Detectors in Wood Construction. In Type III, IV, or V and Type VI (wood) construction, heat or smoke detectors are installed in every classroom, unsupervised spaces, storage space, and custodial closets, and can activate the fire alarm. |
| 423.28.2.19.2 | 423.28.2.19.2 Heat and Smoke Detectors in Non-Combustible Construction. In Type I, or II IV (non-combustible) construction, heat or smoke detectors are installed in storage and custodial closets, and can activate the fire alarm. |
|  | Swimming Pools and Bathing Spaces (Public and Private) |
| New | 424.1.3.1.9 All public pools shall be surrounded by a minimum 48 inch (1219 mm) in height fence. The fence shall be continuous around the perimeter of the pool area that is not otherwise blocked or obstructed by adjacent buildings or structures and shall adjoin with itself or abut to the adjacent members. Access through the barrier other than from doored exits of adjacent building(s) shall be through self-closing self-latching lockable gates of 48 inch (1219 mm) minimal height with the latch located near the top. Consideration shall be given to the U.S. Consumer Product Safety Commission (CPSC) Pub. No. 362 guidelines. Safety Covers that comply with ASTM Standard F1346 do not satisfy this requirement. |
| Table 424.1.6.1 | Table 424.1.6.1 Public Swimming Pool Fixtures Required Size of Pool Men’s Restroom Women’s Restroom Urinals WC Lavatory WC Lavatory 0 – 2,500 sq.ft. 1 1 1 1 1 2,501-5,000 sq.ft 2 1 2 1 2 5 6 1 2 5,001-7,500 sq.ft. 2 3 2 3 2 3 6 9 2 3 7,501-10,000 sq.ft. 3 4 3 4 3 4 9 12 3 4 |
| 424.1.6.1 | 424.1.6.1 Sanitary Facilities. Separate sanitary facilities shall be provided and labeled for each sex and shall be located within a 200 foot (60 960 mm) radius of the nearest water’s edge of each pool served by the facilities. Exception: Where a swimming pool serves only a designated group of residential dwelling units and not the general public, poolside sanitary facilities are not required if all living units are within a 200 foot (60 960 mm) radius of the nearest water’s edge, are not over three stories in height and are each equipped with private sanitary facilities. |
| 424.1.6.1.3 | 424.1.6.1.3 Sanitary facility floors. Floors of sanitary facilities floors shall be constructed of concrete or other nonabsorbent materials, shall have a smooth, slip-resistant finish, and shall slope to floor drains. Carpets, duckboards and footbaths are prohibited. The intersection between the floor and walls shall be covered. |
| 424.2.6.1 | 424.2.6.1 Conformance standard. Design, construction and workmanship shall be in conformity with the requirements of ANSI/NSPI 3-99; ANSI/NSPI 4-99; ANSI/NSPI 5-03; and ANSI/NSPI 6-92. |
| 424.2.6.3 | 424.2.6.3 Water velocity. Pool piping shall be designed so the water velocity will not exceed 10 feet per second (mm/s) for pressure piping and 8 feet per second (mm/s) for suction piping, except that the water velocity shall not exceed 8 feet per second (3048 mm/s) in copper tubing. |
| 424.2.6.5 | 424.2.6.5 Piping installation. All piping materials shall be installed in strict accordance with the manufacturer's installation standards. Exception: Primer and glue on exposed aboveground piping not required to be colored. |
| 424.2.7.2 | 424.2.7.2 Mounting Installation. Pumps shall be installed mounted on a substantial base in a manner that will eliminate strain on piping in accordance with manufacturer recommendations. |
| 424.2.8.3 | 424.2.8.3 Check valves. Where check valves are installed they shall be of the swing, spring or vertical check patterns. |
| 424.2.12.1 | 424.2.12.1 Pressure test. All pool piping shall be inspected and approved before being covered or concealed. It shall be tested and proved tight to the satisfaction of the administrative authority, under a static water or air pressure test of not less than 35 psi ((241 kPa) for 15 minutes. |
| 424.2.17.1.9 | 424.2.17.1.9 Where a wall of a dwelling serves as part of the barrier, one of the following shall apply: All doors and windows providing direct access from the home to the pool shall be equipped with an exit alarm complying with UL 2017 that has a minimum sound pressure rating of 85 dBA at 10 feet (3048 mm) and is either hardwired or of the plug-in type. The exit alarm shall produce a continuous audible warning when the door and its screen are opened. The alarm shall sound immediately after the door is opened and be capable of being heard throughout the house during normal household activities. The alarm shall be equipped with a manual means to temporarily deactivate the alarm for a single opening. Such deactivation shall last no more than 15 seconds. The deactivation switch shall be located at least 54 inches (1372 mm) above the threshold of the door. Separate alarms are not required for each door or window if sensors wired to a central alarm sound when contact is broken at any opening. (no change to remainder of section) |
| New | 424.2.17.1.15 A mesh safety barrier meeting the requirements of Section 424.2.17 and the following minimum requirements shall be considered a barrier as defined in this section: 1. Individual component vertical support posts shall be capable of resisting a minimum of 52 pounds (24 kg) of horizontal force prior to breakage when measured at a 36 inch (914 mm) height above grade. Vertical posts of the child safety barrier shall extend a minimum of 3 inches (76 mm) below deck level and shall be spaced no greater than 36 inches (914 mm) apart. 2. The mesh utilized in the barrier shall have a minimum tensile strength according to ASTM D 5034 of 100 lbf, and a minimum ball burst strength according to ASTM D 3787 of 150 lbf. The mesh shall not be capable of deformation such that a 1/4-inch (6.4 mm) round object could not pass through the mesh. The mesh shall receive a descriptive performance rating of no less than “trace discoloration” or “slight discoloration” when tested according to ASTM G 53, Weatherability, 1,200 hours. 3. When using a molding strip to attach the mesh to the vertical posts, this strip shall contain, at a minimum, #8 by ½ inch (12.7 mm) screws with a minimum of two screws at the top and two at the bottom with the remaining screws spaced a maximum of 6 inches (152 mm) apart on center. 4. Patio deck sleeves (vertical post receptacles) placed inside the patio surface shall be of a nonconductive material. 5. A latching device shall attach each barrier section at a height no lower than 45 inches (1143 mm) above grade. Common latching devices that include, but are not limited to, devices that provide the security equal to or greater than that of a hook-and-eye-type latch incorporating a spring actuated retaining lever (commonly referred to as a safety gate hook). 6. The bottom of the mesh safety barrier shall not be more than 1 inch (25 mm) above the deck or installed surface (grade). |
| 424.2.18 | 424.2.18 Ladders and Steps. All pools whether public or private shall be provided with a ladder or steps in the shallow end where water depth exceeds 24 inches (610 mm). In private pools where water depth exceeds 5 ft (1524 mm), there shall be ladders, stairs or underwater benches/swimouts in the deep end. Where manufactured diving equipment is to be used, benches or swimouts shall be recessed or located in a corner. Exception: In private pools having more than one shallow end, only one set of steps are required. A bench, swim-out or ladder may be used at all additional shallow ends in lieu of an additional set of steps. |
| 424.2.21.2 | 424.2.21.2 Skimmers. Approved surface skimmers are required and shall be installed in strict accordance with the manufacturer's installation instructions. Skimmers shall be installed on the basis of one per 800 1000 sq ft (74 m2) of surface area or fraction thereof, and shall be designed for a flow rate of at least 25 gpm (94 L/m) per skimmer. |
| 424.2.21.5 | 424.2.21.5 Inlet fittings. Approved manufactured inlet fittings for the return of recirculated pool water shall be provided on the basis of at least one per 15,000 gal of pool capacity 300 square feet (28 m2) of surface area. Such inlet fittings shall be designed and constructed to insure an adequate seal to the pool structure and shall incorporate a convenient means of sealing for pressure testing of the pool circulation piping. Where more than one inlet is required, the shortest distance between any two required inlets shall be at least 10 feet (3048 mm). |
| 424.2.22 | 424.2.22 Equipment Foundations and Enclosures. All mechanical pool motors and equipment shall be set on a single concrete base or slab installed in compliance with the manufacturer’s recommendations. All heating and electrical equipment, unless approved for outdoor installation, shall be adequately protected against the weather or installed within a building. |
|  | Public Food Service Establishments |
| 426.1 | 426.1 Public food service establishments or food establishments shall comply with design and construction standards as described in the 1999 Food Code and Chapter 509 Part I or Chapter 500 Florida Statutes as applicable. Note: Other administrative and programmatic provisions may apply. See Department of Business and Professional Regulation [DBPR] Rule 61Cj-4, Florida Administrative Code and Chapter 500 and Chapter 509, Florida Statutes. |
| New | Food Establishment. See Section 500.03, Florida Statutes. |
|  | Day Care Occupancies |
| 418.8 | 436.8 418.8 Corridors. Every interior corridor shall be constructed of walls having not less than a 1-hr fire resistance rating. Exceptions: 1. In buildings protected throughout by an approved, supervised automatic sprinkler system in accordance with Sections 901.6 and 903.3.1 corridor walls shall not be required to be rated, provided that such walls form smoke partitions in accordance with Section 710. 2. Where the corridor ceiling is an assembly having a 1-hour fire resistance rating where tested as a wall, the corridor walls shall be permitted to terminate at the corridor ceiling. 3. Lavatories in unsprinklered buildings shall not be required to be separated from corridors, provided that they are separated from all other spaces by walls having not less than a 1-hour fire resistance rating in accordance with Section 709. 4. Lavatories shall not be required to be separated from corridors, provided the building is protected throughout by an approved, supervised automatic sprinkler system in accordance with Sections 901.6 and 903.1.1. |