Supplement to the 8th Edition (2023) FBC, Mechanical

Note 1:  Throughout the document, change International Building Code to Florida Building Code, Building; Energy Conservation Code to the Florida Building Code, Energy Conservation; change the International Existing Building Code to Florida Building Code, Existing Building; change the International Fire code to Florida Fire Prevention Code; change International Fuel Gas Code to Florida Building Code, Fuel Gas; change the International Mechanical Code to Florida Building Code, Mechanical; change the International Plumbing Code to Florida Building Code, Plumbing; change the International Residential Code to Florida Building Code, Residential.

CHAPTER 2 DEFINITIONS

[BG] AMBULATORY CARE FACILITY

Buildings or portions thereof used to provide medical, surgical, psychiatric, nursing or similar care on a less than 24-hour basis to persons who are rendered incapable of self-preservation by the services provided or staff has accepted responsibility for care recipients already incapable.

(M10928 / G3-21 Part IV AS)

NONCOMBUSTIBLE MATERIALS. A material that passes ASTM E136. Materials that, when tested in accordance with ASTM E136, have not fewer than three of four specimens tested meeting all of the following criteria:

1.	The recorded temperature of the surface and interior thermocouples shall not at any time during the test rise more than 54ºF (30ºC) above the furnace temperature at the beginning of the test.

2.	There shall not be flaming from the specimen after the first 30 seconds.

3.	If the weight loss of the specimen during testing exceeds 50 percent, the recorded temperature of the surface and interior thermocouples shall not at any time during the test rise above the furnace air temperature at the beginning of the test, and there shall not be flaming of the specimen.

(M11266 / M6-21 AS)

Delete and substitute as follows:

REFRIGERANT. A substance utilized to produce refrigeration by its expansion or vaporization.

REFRIGERANT.

The fluid used for heat transfer in a refrigeration system that undergoes a change of state to absorb heat

(M11267 / M8-21 Part I AS)

###### REFRIGERATION REFRIGERATING SYSTEM

A combination of interconnected parts in which a refrigerant is enclosed and refrigerant-containing parts constituting one closed refrigerant circuit in which a refrigerant is circulated for the purpose of extracting then rejecting heat.

(M11289 / M10-21 Part I AS)

STEAM BATH EQUIPMENT

Includes steam bath generators, combination room and steam generator systems, and steam bath cabinets intended for high-humidity concentrated heating at elevated temperatures for personal bathing

(M11327 / M62-21 AS)

DRAFTSTOP

.

A material, device or construction installed to restrict the movement of air within open spaces of concealed areas of building components such as crawl spaces, floor/ceiling assemblies, roof/ceiling assemblies and attics.

(M11228 / FS47-21 Part III AS)

CONDENSING UNIT. A specific refrigerating machine combination for a given refrigerant, consisting of one or more power-driven compressors, condensers and, where required, liquid receivers, and the regularly furnished accessories.

A factory-made assembly of refrigeration components designed to compress and liquefy a specific refrigerant. The unit consists of one or more power-driven compressors, condensers, liquid receivers (where required) and factory-supplied accessories.

(M11232 / M2-21 AS)

FLAMMABILITY CLASSIFICATION (REFRIGERANT). The alphabetical/numerical designation used to identify the flammability of refrigerants.

Class 1. Indicates a refrigerant with no flame propogation.

Class 2. Indicates a refrigerant with low flammability.

Class 2L. Indicates a refrigerant with low flammability and low burning velocity.

Class 3. Indicates a refrigerant with high flammability.

MACHINERY ROOM. A room meeting prescribed safety requirements and in which refrigeration systems or components thereof are located (see Sections 1105 and 1106). An enclosed space that is required by Chapter 11 to contain refrigeration equipment and to comply with Sections 1105 and 1106.

REFRIGERANT SAFETY GROUP CLASSIFICATION. The alphabetical/numerical designation that indicates both the toxicity and flammability classifications of refrigerants in accordance with ASHRAE 34.

Flammability. See Flammability classification (Refrigerant).

Toxicity. See Toxicity classification (Refrigerant).

Flammability classification (refrigerant). The alphanumeric designation used to identify the flammability of refrigerants.

Class 1. Indicates a refrigerant with no flame propagation.

Class 2. Indicates a refrigerant with low flammability.

Class 2L. Indicates a refrigerant with low flammability and low burning velocity.

Class 3. Indicates a refrigerant with high flammability.

Toxicity classification (refrigerant). An alphabetical designation used to identify the toxicity of refrigerants. Class A indicates a refrigerant with low toxicity. Class B indicates a refrigerant with high toxicity.

TOXICITY CLASSIFICATION (REFRIGERANT). An alphabetical designation used to identify the toxicity of refrigerants. Class A indicates a refrigerant with lower toxicity. Class B indicates a refrigerant with higher toxicity.

Class A. Refrigerants that have an occupational exposure limit (OEL) of 400 parts per million (ppm) or greater.

Class B. Refrigerants that have an OEL of less than 400 ppm.

(Step 2 – M12145 AS)

GYPSUM BOARD

. A type of gypsum panel product consisting of a noncombustible core primarily of gypsum with paper surfacing.

GYPSUM WALLBOARD

A gypsum board used primarily as an interior surfacing for building structures.

(M11233 / M3-21 AS)

HEAT PUMP. A refrigeration system that extracts heat from one substance and transfers it to another portion of the same substance or to a second substance at a higher temperature for a beneficial purpose.

HEAT PUMP.

A refrigeration system or factory-made appliance that utilizes refrigerant to transfer heat into a space or substance.

(M11235 / M4-21 Part I AS)

LOWER FLAMMABLE LIMIT (REFRIGERANT) (LFL). The minimum concentration of refrigerant that is at which a flame is capable of propagating a flame through a homogeneous mixture of refrigerant and air under specific test conditions in accordance with ASHRAE 34.

(M11239 / M5-21 AS)

Revise as follows:

[A] LISTED. Equipment, materials, products or services included in a list published by an organization acceptable to the code official and concerned with evaluation of products or

services that maintains periodic inspection of production of listed equipment or materials or periodic evaluation of services and whose listing states either that the equipment, material, product or service meets identified standards or has been tested and found suitable for a specified purpose. Terms that are used to identify listed equipment, products, or materials include “listed”, “certified”, “classified” or other

terms as determined appropriate by the listing organization.

(M10930 / ADM1-22 Part I AS)

GREASE DUCT

A duct serving a Type I hood, or cooking appliances equipped with integral down-draft exhaust systems that produce grease, to convey grease-laden air from the hood or cooking appliance directly to the outdoors.

(M11308 / M35-21 AS)

Add new definition as follows:

Refrigerant Designation. The unique identifying alphanumeric value or refrigerant number assigned to an individual refrigerant and published in ASHRAE Standard 34.

(M11369 / M73-21 AMPC1)

CHAPTER 3 GENERAL REGULATIONS

301.16 Flood hazard. For structures located in flood hazard areas, mechanical systems, equipment and appliances shall be located at or above the elevation required by Section 1612 of the International Building Code for utilities and attendant equipment.

Exceptions:

1. Unless part of substantial improvement, replacement of exterior equipment and exterior appliances that are damaged by flood shall meet one of the following:

1.1. Be elevated to or above the same height above grade as the first floor of the building, or 4 ft above grade, whichever is higher.

1.2. For nonresidential buildings and nonresidential portions of buildings, be elevated in accordance with 1.1 or located in an enclosure that is dry floodproofed to 4 ft above grade, or the same height above grade as the first floor of the building, whichever is higher, in accordance with the dry floodproofing requirements of ASCE 24 for attendant utilities and equipment.

2. Mechanical systems, equipment and appliances are permitted to be located below the elevation required by Section 1612 of the International Building Code for utilities and attendant equipment provided that they are designed and installed to prevent water from entering or accumulating within the components and to resist hydrostatic and hydrodynamic loads and stresses, including the effects of buoyancy, during the occurrence of flooding up to such elevation.

(Step 2 – SP12019 AM/A1 – 2nd comment period)

[BS]302.5 Cutting, and notching and boring in cold-formed steel framing. The cutting, and notching and boring of holes in cold-formed steel framing members shall be in accordance with AISI S240 for structural members and AISI S220 for non-structural members. The cutting, notching and boring of steel framing members shall comply with Sections 302.5.1 through 302.5.3.

(P11086/S196-22)

[BS] 302.3 Cutting, notching and boring in wood framing. The cutting, notching and boring of wood framing members shall comply with Sections 2301.4.1 of the Florida Building Code, Building. 302.3.1 through 302.3.4.

Delete without substitution:

[BS] 302.3.1 Joist notching. Notches on the ends of joists shall not exceed one-fourth the joist depth. Holes bored in joists shall not be within 2 inches (51 mm) of the top or bottom of the joist, and the diameter of any such hole shall not exceed one-third the depth of the joist. Notches in the top or bottom of joists shall not exceed one-sixth the depth and shall not be located in the middle third of the span.

[BS] 302.3.2 Stud cutting and notching. In exterior walls and bearing partitions, a wood stud shall not be cut or notched in excess of 25 percent of its depth. In nonbearing partitions that do not support loads other than the weight of the partition, a stud shall not be cut or notched in excess of 40 percent of its depth.

[BS] 302.3.3 Bored holes. The diameter of bored holes in wood studs shall not exceed 40 percent of the stud depth. The diameter of bored holes in wood studs shall not exceed 60 percent of the stud depth in nonbearing partitions. The diameter of bored holes in wood studs shall not exceed 60 percent of the stud depth in any wall where each stud is doubled, provided that not more than two such successive doubled studs are so bored. The edge of the bored hole shall be not closer than 5/8 inch (15.9 mm) to the edge of the stud. Bored holes shall be not located at the same section of stud as a cut or notch.

(M11451 / S224-22 AS)

TABLE 305.4 PIPING SUPPORT SPACINGa

| PIPING MATERIAL | MAXIMUM HORIZONTAL SPACING (feet) | MAXIMUM VERTICAL SPACING (feet) |
| --- | --- | --- |
| ABS pipe | 4 | 10c |
| Aluminum pipe and tubing | 10 | 15 |
| Cast-iron pipeb | 5 | 15 |
| Copper or copper-alloy pipe | 12 | 10 |
| Copper or copper-alloy tubing | 8 | 10 |
| CPVC pipe or tubing, 1 inch and smaller | 3 | 10c |
| CPVC pipe or tubing, 11/4-inches and larger | 4 | 10c |
| Lead pipe | Continuous | 4 |
| PB pipe or tubing | 22/3 (32 inches) | 4 |
| PE-RT 1 inch and smaller | 22/3 (32 inches) | 10c |
| PE-RT 11/4 inches and larger | 4 | 10c |
| PEX tubing 1 inch and smaller | 22/3 (32 inches) | 10c |
| PEX tubing 11/4 inches and larger | 4 | 10c |
| Polypropylene (PP) pipe or tubing, 1 inch and smaller | 22/3 (32 inches) | 10c |
| Polypropylene (PP) pipe or tubing, 11/4 inches and larger | 4 | 10c |
| PVC pipe | 4 | 10c |
| Steel pipe | 12 | 15 |
| Steel tubing | 8 | 10 |

For SI: 1 inch = 25.4 mm, 1 foot = 304.8 mm.

a.	See Section 301.18.

b.	The maximum horizontal spacing of cast-iron pipe hangers shall be increased to 10 feet where 10-foot lengths of pipe are installed.

c.	Mid-story guide.

(M11291 / M12-21 AS)

306.1 Access. Appliances, controls devices, heat exchangers and HVAC system components that utilize energy shallbe accessible provide access for inspection, service, repair and replacement without disabling the function of a fire-resistance-rated assembly or removing permanent construction, other appliances, venting systems or any other piping or ducts not connected to the appliance being inspected, serviced, repaired or replaced. A level working space not less than 30 inches deep and 30 inches wide (762 mm by 762 mm) shall be provided in front of the control side to service an appliance.

(M11229 / G1-21 Part V AS)

306.5 Equipment and appliances on roofs or elevated structures. Where equipment requiring access or appliances are located on an elevated structure or the roof of a building such that personnel will have to climb higher than 16 feet (4877 mm) above grade to access such equipment or appliances, an interior or exterior means of access shall be provided. Such access shall not require climbing over

obstructions greater than 30 inches (762 mm) in height or walking on roofs having a slope greater than four units vertical in 12 units horizontal (33-percent slope). Such access shall not require the use of portable ladders. Where access involves climbing over parapet walls, the height shall be measured to the top of the parapet wall. Permanent ladders installed to provide the required access shall comply with the following minimum design criteria:

1.	The side railing shall extend above the parapet or roof edge or landing platform not less than 30 inches (762 mm). 42 inches (1067 mm)

2.	Ladders shall have rung spacing not less than 10 inches ( 254 mm) and not to exceed 14 inches (356 mm) on center. The uppermost rung shall be not greater than 24 inches (610 mm) below the upper edge of the roof hatch, roof or parapet, as applicable.

3.	Ladders shall have a toe spacing not less than6 inches (152 mm) 7 inches (178 mm) and not more than 12 inches (305 mm) deep

4.	There shall be not less than18 inches (457 mm) 16 inches (406 mm) between rails.

5.	Rungs shall have a diameter not less than 0.75-inch (19.1 mm) and be capable of withstanding a 300-pound (136 kg) load.

6.	Ladders over 30 feet (9144 mm) in height shall be provided with offset sections and landings capable of withstanding 100 pounds per square foot (488 kg/m2). Landing dimensions shall be not less than 18 inches (457 mm) and not less than the width of the ladder served. A guard rail shall be provided on all open sides of the landing.

7.	Climbing clearance. The distance from the centerline of the rungs to the nearest permanent object on the climbing side of the ladder shall be not less than 30 inches (762 mm) measured perpendicular to the rungs. This distance shall be maintained from the point of ladder access to the bottom of the roof hatch. A minimum clear width of 15 inches (381 mm) shall be provided on both sides of the ladder measured from the midpoint of and parallel with the rungs except where cages or wells are installed.

8.	Landing required. The ladder shall be provided with a clear and unobstructed bottom landing area having a minimum dimension of 30 inches (762 mm) by 30 inches (762 mm) centered in front of the ladder.

9.	Ladders shall be protected against corrosion by approved means.

10.	Access to ladders shall be provided at all times.

11.	Top landing required. The ladder shall be provided with a clear and unobstructed landing on the exit side of the roof hatch having a minimum space of 30 inches deep and be of the same width as the hatch.

Catwalks installed to provide the required access shall be not less than 24 inches (610 mm) wide and shall have railings as required for service platforms.

Exception: This section shall not apply to Group R-3 occupancies.

(M11292 / M13-21 AM)/ (M11293 / M14-21 AS)

307.2.2 Drain pipe materials and sizes.

Components of the condensate disposal system shall be ABS, cast iron, copper and copper alloy, CPVC, cross-linked polyethylene, galvanized steel, PE-RT, polyethylene, polypropylene, PVC or PVDF pipe or tubing. Components shall be selected for the pressure and temperature rating of the installation. Joints and connections shall be made in accordance with the applicable provisions of Chapter 7 of the Florida Building Code, Plumbing relative to the material type. Condensate waste and drain line size shall be not less than 3/4-inch (19.1 mm) pipe size and shall not decrease in size from the drain pan connection to the place of condensate disposal. Where the drain pipes from more than one unit are manifolded together for condensate drainage, the pipe or tubing shall be sized in accordance with Table 307.2.2. Drain pipes conveying condensate from cooling coils and evaporators shall be insulated with a minimum of R-3 when located inside a building’s unconditioned space.

(Step 2 – M11775 AS)

CHAPTER 4 VENTILATION

401.4 Intake opening location. Air intake openings shall comply with all of the following:

1.	Intake openings shall be located not less than 10 feet (3048 mm) from lot lines or buildings on the same lot.

2.	Mechanical and gravity outdoor air intake openings shall be located not less than 10 feet (3048 mm) horizontally from any hazardous or noxious contaminant source, such as vents, streets, alleys, parking lots and loading docks, except as specified in Item 3 or Section 501.3.1. Outdoor air intake openings shall be permitted to be located less than 10 feet (3048 mm) horizontally from streets, alleys, parking lots and loading docks provided that the openings are located not less than 25 feet (7620 mm) vertically above such locations. Where openings front on a street or public way, the distance shall be measured from the closest edge of the street or public way.

3.	Intake openings shall be located not less than 3 feet (914 mm) below contaminant sources where such sources are located within 10 feet (3048 mm) of the opening. Separation is not required between intake air openings and living space exhaust air openings of an individual dwelling unit or sleeping unit where an approved factory-built intake/exhaust combination termination fitting is used to separate the air streams in accordance with the fan manufacturer's instructions.

4.	No change

(M11294 / M16-21 AMPC1)

403.3.1	Other buildings intended to be occupied. The design of local exhaust systems and ventilation systems for outdoor air for occupancies other than Group R-2, R-3 and R-4 three stories and less above grade plane shall comply with Sections 403.3.1.1 through 403.3.1.4.

403.3.2	Group R-2, R-3 and R-4 occupancies, three stories and less. The design of local exhaust systems and ventilation systems for outdoor air in Group R-2, R-3 and R-4 occupancies three stories and less in height above grade plane shall comply with Sections 403.3.2.1 through 403.3.2.5.

403.3.2.1	Outdoor air for dwelling units. An outdoor air ventilation system consisting of a mechanical exhaust system, supply system or combination thereof shall be installed for each dwelling unit. Local exhaust or supply systems, including outdoor air ducts connected to the return side of an air handler, are permitted to serve as such a system. The outdoor air ventilation system shall be designed to provide the required rate of outdoor air continuously during the period that the building is occupied. The minimum continuous outdoor airflow rate shall be determined in accordance with Equation 4-9.

QOA= 0.01 0.03 Afloor +7.5(Nbr+1)

where:

QOA= outdoor airflow rate, cfm

Afloor = conditioned floor area, ft2

Nbr = number of bedrooms; not to be less than one

Exceptions:

        - The outdoor air ventilation system is not required to operate continuously where the system has controls that enable operation for not less than 1 hour of each 4-hour period. The average outdoor airflow rate over the 4-hour period shall be not less than that prescribed by Equation 4-9.

        - The minimum mechanical ventilation rate determined in accordance with Equation 4-9 shall be reduced by 30 percent provided that both of the following conditions apply:

          - A ducted system supplies ventilation air directly to each bedroom and to one or more of the following rooms:

            - Living room.

            - Dining room.

            - Kitchen.

          - The whole-house ventilation system is a balanced ventilation system.

(M11295 / M19-21 AM)

###### TABLE 403.3.1.1 MINIMUM VENTILATION RATES

Portions of table not shown remain unchanged.

| OCCUPANCY CLASSIFICATION | OCCUPANT DENSITY #/1000 FT 2 a | PEOPLE OUTDOOR AIRFLOW RATE IN BREATHING ZONE, R p CFM/PERSON | AREA OUTDOOR AIRFLOW RATE IN BREATHING ZONE, R a CFM/FT 2 a | EXHAUST AIRFLOW RATE CFM/FT 2 a |
| --- | --- | --- | --- | --- |
| Public spaces |  |  |  |  |
| Corridors | — | — | 0.06 | — |
| Courtrooms | 70 | 5 | 0.06 | — |
| Elevator car | — | — | — | 1.0 |
| Legislative chambers | 50 | 5 | 0.06 | — |
| Libraries | 10 | 5 | 0.12 | — |
| Museums (children’s) | 40 | 7.5 | 0.12 | — |
| Museums/galleries | 40 | 7.5 | 0.06 | — |
| Places of religious worship | 120 | 5 | 0.06 | — |
| Shower room (per shower head) g | — | — | — | 50/20 f |
| Smoking lounges b | 70 | 60 | — | — |
| Toilet rooms — public g | — | — | — | 50/70 e |
| Room with adult changing |  |  | , | 50/70e |
| station |  |  |  |  |

For SI: 1 cubic foot per minute = 0.0004719 m3 /s, 1 ton = 908 kg, 1 cubic foot per minute per square foot = 0.00508 m 3 /(s • m 2 ), °C = [(°F) – 32]/1.8, 1 square foot = 0.0929 m 2 .

a.	Based on net occupiable floor area.

b.	Mechanical exhaust required and the recirculation of air from such spaces is prohibited. Recirculation of air that is contained completely within such spaces shall not be prohibited (see Section 403.2.1, Item 3).

c.	Spaces unheated or maintained below 50°F are not covered by these requirements unless the occupancy is continuous.

d.	Ventilation systems in enclosed parking garages shall comply with Section 404.

e.	Rates are per water closet, or urinal or adult changing station. The higher rate shall be provided where the exhaust system is designed to operate intermittently. The lower rate shall be permitted only where the exhaust system is designed to operate continuously while occupied.

f.	Rates are per room unless otherwise indicated. The higher rate shall be provided where the exhaust system is designed to operate intermittently. The lower rate shall be permitted only where the exhaust system is designed to operate continuously while occupied.

g.	Mechanical exhaust is required and recirculation from such spaces is prohibited. For occupancies other than science laboratories, where there is a wheel - type energy recovery ventilation (ERV) unit in the exhaust system design, the volume of air leaked from the exhaust airstream into the outdoor airstream within the ERV shall be less than 10 percent of the outdoor air volume. Recirculation of air that is contained completely within such spaces shall not be prohibited (see Section 403.2.1, Items 2 and 4).

h.	For nail salons, each manicure and pedicure station shall be provided with a source capture system capable of exhausting not less than 50 cfm per station. Exhaust inlets shall be located in accordance with Section 502.20. Where one or more required source capture systems operate continuously during occupancy, the exhaust rate from such systems shall be permitted to be applied to the exhaust flow rate required by Table 403.3.1.1 for the nail salon.

(M11296 / M20-21 AS)

###### TABLE 403.3.1.1 MINIMUM VENTILATION RATES

| OCCUPANCY CLASSIFICATION | OCCUPANT DENSITY #/1000 FT 2 a | PEOPLE OUTDOOR AIRFLOW RATE IN BREATHING ZONE, R p CFM/PERSON | AREA OUTDOOR AIRFLOW RATE IN BREATHING ZONE, R a CFM/FT 2 a | EXHAUST AIRFLOW |
| --- | --- | --- | --- | --- |
|  |  |  |  | RATE CFM/FT 2 a |
| Animal Facilities |  |  |  |  |
| Animal exam room (veterinary office) | 20 | 10 | 0.12 | - |
| Animal imaging (MRI/CT/PET) | 20 | 10 | 0.18 | 0.9 |
| Animal operating rooms | 20 | 10 | 0.18 | 3.00 |
| Animal postoperative recovery room | 20 | 10 | 0.18 | 1.50 |
| Animal preparation rooms | 20 | 10 | 0.18 | 1.50 |
| Animal procedure room | 20 | 10 | 0.18 | 2.25 |
| Animal surgery scrub | 20 | 10 | 0.18 | 1.50 |
| Large-animal holding room | 20 | 10 | 0.18 | 2.25 |
| Necropsy | 20 | 10 | 0.18 | 2.25 |
| Small-animal cage room (static cages) | 20 | 10 | 0.18 | 2.25 |
| Small-animal-cage room (ventilated cages) | 20 | 10 | 0.18 | 1.50 |
| Correctional facilities |  |  |  |  |
| Booking/waiting | 50 | 7.5 | 0.06 | — |
| Cells without plumbing fixtures with plumbing fixtures g | 25 25 | 5 5 | 0.12 0.12 | — 1.0 |
| Day room | 30 | 5 | 0.06 | — |
| Dining halls (see “Food and beverage service”) | — | — | — | — |
| Guard stations | 15 | 5 | 0.06 | — |
| Dry cleaners, laundries |  |  |  |  |
| Coin-operated dry cleaner | 20 | 15 | — | — |
| Coin-operated laundries | 20 | 7.5 | 0.12 | — |
| Commercial dry cleaner | 30 | 30 | — | — |
| Commercial laundry | 10 | 5 | 0.12 | — |
| Storage, pick up | 30 | 7.5 | 0.12 | — |
| Education |  |  |  |  |
| Art classroom g | 20 | 10 | 0.18 | 0.7 |
| Auditoriums | 150 | 5 | 0.06 | — |
| Classrooms (ages 5–8) | 25 | 10 | 0.12 | — |
| Classrooms (age 9 plus) | 35 | 10 | 0.12 | — |
| Computer lab | 25 | 10 | 0.12 | — |
| Corridors (see “Public spaces”) | — | — | — | — |
| Day care (through age 4) | 25 | 10 | 0.18 | — |
| Lecture classroom | 65 | 7.5 | 0.06 | — |
| Lecture hall (fixed seats) | 150 | 7.5 | 0.06 | — |
| Locker/dressing rooms g | — | — | — | 0.25 |
| Media center | 25 | 10 | 0.12 | — |
| Multiuse assembly | 100 | 7.5 | 0.06 | — |
| Music/theater/dance | 35 | 10 | 0.06 | — |
| Science laboratories g | 25 | 10 | 0.18 | 1.0 |
| Smoking loungesb | 70 | 60 | — | — |
| Sports locker rooms g | — | — | — | 0.5 |
| Wood/metal shops g | 20 | 10 | 0.18 | 0.5 |
| Food and beverage service |  |  |  |  |
| Bars, cocktail lounges | 100 | 7.5 | 0.18 | — |
| Break rooms | 25 | 5 | 0.06 | - |
| Cafeteria, fast food | 100 | 7.5 | 0.18 | — |
| Coffee stations | 20 | 5 | 0.06 | - |
| Corridors | - | - | 0.06 | - |
| Dining rooms | 70 | 7.5 | 0.18 | — |

| OCCUPANCY CLASSIFICATION | OCCUPANT DENSITY #/1000 FT | PEOPLE OUTDOOR AIRFLOW RATE IN BREATHING ZONE, R CFM/PERSON | AREA OUTDOOR AIRFLOW RATE IN BREATHING ZONE, R CFM/FT | EXHAUST AIRFLOW |
| --- | --- | --- | --- | --- |
|  |  |  |  | RATE CFM/FT |
| Kitchens (cooking) b | 20 | 7.5 | 0.12 | 0.7 |
| Occupiable storage rooms for liquids or gels | 2 | 5 | 0.12 | - |
| Hotels, motels, resorts and dormitories |  |  |  |  |
| Bathrooms/toilet—private g | — | — | — | 25/50 f |
| Bedroom/living room | 10 | 5 | 0.06 | — |
| Conference/meeting | 50 | 5 | 0.06 | — |
| Dormitory sleeping areas | 20 | 5 | 0.06 | — |
| Gambling casinos | 120 | 7.5 | 0.18 | — |
| Laundry rooms, central | 10 | 5 | 0.12 | - |
| Laundry rooms within dwelling units | 10 | 5 | 0.12 | - |
| Lobbies/prefunction | 30 | 7.5 | 0.06 | — |
| Multipurpose assembly | 120 | 5 | 0.06 | — |
| Offices |  |  |  |  |
| Break rooms | 50 | 5 | 0.12 | - |
| Conference rooms | 50 | 5 | 0.06 | — |
| Main entry lobbies | 10 | 5 | 0.06 | — |
| Occupiable storage rooms for dry materials | 2 | 5 | 0.06 | - |
| Office spaces | 5 | 5 | 0.06 | — |
| Reception areas | 30 | 5 | 0.06 | — |
| Telephone/data entry | 60 | 5 | 0.06 | — |
| Outpatient healthcare facilitiesi, j |  |  |  |  |
| Birthing room | 15 | 10 | 0.18 | - |
| Class 1 imaging room | 5 | 5 | 0.12 | - |
| Dental operatoryk | 20 | 10 | 0.18 | - |
| General examination room | 20 | 7.5 | 0.12 | - |
| Other dental treatment areas | 5 | 5 | 0.06 | - |
| Physical therapy exercise area | 7 | 20 | 0.18 | - |
| Physical therapy individual room | 20 | 10 | 0.06 | - |
| Physical therapeutic pool area | - | - | 0.48 | - |
| Prosthetics and orthotics room | 20 | 10 | 0.18 | - |
| Psychiatric consultation room | 20 | 5 | 0.06 | - |
| Psychiatric examination room | 20 | 5 | 0.06 | - |
| Psychiatric group room | 50 | 5 | 0.06 | - |
| Psychiatric seclusion room | 5 | 10 | 0.06 | - |
| Speech therapy room | 20 | 5 | 0.06 | - |
| Urgent care examination room | 20 | 7.5 | 0.12 | - |
| Urgent care observation room | 20 | 5 | 0.06 | - |
| Urgent care treatment room | 20 | 7.5 | 0.18 | - |
| Urgent care triage room | 20 | 10 | 0.18 | - |
| Private dwellings, single and multiple |  |  |  |  |
| Garages, common for multiple units b | — | — | — | 0.75 |
| Kitchens b | — | — | — | 50 /100 f |
| Living areas c | Based on number of bedrooms. First bedroom, 2; each additional bedroom, 1 | 0.35 ACH but not less than 15 cfm/person | — | — |
| Toilet rooms and bathrooms g | — | — | — | 25 /50 f |
| Public spaces |  |  |  |  |
| Corridors | — | — | 0.06 | — |
| Courtrooms | 70 | 5 | 0.06 | — |
| Elevator car | — | — | — | 1.0 |
| Legislative chambers | 50 | 5 | 0.06 | — |
| Libraries | 10 | 5 | 0.12 | — |
| Museums (children’s) | 40 | 7.5 | 0.12 | — |
| Museums/galleries | 40 | 7.5 | 0.06 | — |
| Places of religious worship | 120 | 5 | 0.06 | — |
| Shower room (per shower head) g | — | — | — | 50/20 f |
| Smoking lounges b | 70 | 60 | — | — |
| Toilet rooms — public g | — | — | — | 50/70 e |
| Retail stores, sales floors and showroom floors |  |  |  |  |
| Dressing rooms | — | — | — | 0.25 |
| Mall common areas | 40 | 7.5 | 0.06 | — |
| Sales | 15 | 7.5 | 0.12 | — |
| Shipping and receiving | 2 | 10 | 0.12 | — |
| Smoking lounges b | 70 | 60 | — | — |
| Storage rooms | — | — | 0.12 | — |
| Warehouses (see “Storage”) | — | 10 | 0.06 | — |
| Specialty shops |  |  |  |  |
| Automotive motor fuel-dispensing stations b | — | — | — | 1.5 |
| Banks or lobbies | 15 | 7.5 | 0.06 | - |
| Barber | 25 | 7.5 | 0.06 | 0.5 |
| Beauty salons b | 25 | 20 | 0.12 | 0.6 |

| OCCUPANCY CLASSIFICATION | OCCUPANT DENSITY #/1000 FT | PEOPLE OUTDOOR AIRFLOW RATE IN BREATHING ZONE, R CFM/PERSON | AREA OUTDOOR AIRFLOW RATE IN BREATHING ZONE, R CFM/FT | EXHAUST AIRFLOW |
| --- | --- | --- | --- | --- |
|  |  |  |  | RATE CFM/FT |
| Embalming roomb | — | — | — | 2.0 |
| Nail salons b , h | 25 | 20 | 0.12 | 0.6 |
| Pet shops (animal areas)b | 10 | 7.5 | 0.18 | 0.9 |
| Supermarkets | 8 | 7.5 | 0.06 | — |
| Sports and amusement |  |  |  |  |
| Bowling alleys (seating areas) | 40 | 10 | 0.12 | — |
| Disco/dance floors | 100 | 20 | 0.06 | — |
| Game arcades | 20 | 7.5 | 0.18 | — |
| Gym, stadium, arena (play area) | 7 | 20 | 0.18 | — |
| Health club/aerobics room | 40 | 20 | 0.06 | — |
| Health club/weight room | 10 | 20 | 0.06 | — |
| Ice arenas without combustion engines | — | — | 0.30 | 0.5 |
| Spectator areas | 150 | 7.5 | 0.06 | — |
| Swimming pools (pool and deck area) | — | — | 0.48 | — |
| Storage |  |  |  |  |
| Refrigerated warehouses/freezers (<50°F) | — | 10 | — | 0.75 |
| Repair garages, enclosed parking garagesb, d | — | — | — | 0.75 |
| Warehouses | — | 10 | 0.06 | — |
| Theaters |  |  |  |  |
| Auditoriums (see “Education”) | — | — | — | — |
| Lobbies | 150 | 5 | 0.06 | — |
| Stages, studios | 70 | 10 | 0.06 | — |
| Ticket booths | 60 | 5 | 0.06 | — |
| Transportation |  |  |  |  |
| Platforms | 100 | 7.5 | 0.06 | — |
| Transportation waiting | 100 | 7.5 | 0.06 | — |
| Workrooms |  |  |  |  |
| Bank vaults/safe deposit | 5 | 5 | 0.06 | — |
| Computer (without printing) | 4 | 5 | 0.06 | — |
| Copy, printing rooms | 4 | 5 | 0.06 | 0.5 |
| Darkrooms | — | — | — | 1.0 |
| Manufacturing where hazardous materials are not used | 7 | 10 | 0.18 | - |
| Manufacturing where hazarous materials are used (excludes heavy industrial and chemical processes) | 7 | 10 | 0.18 | - |
| Meat processing c | 10 | 15 | — | — |
| Pharmacy (prep. area) | 10 | 5 | 0.18 | — |
| Photo studios | 10 | 5 | 0.12 | — |
| Sorting, packing, light assembly | 7 | 7.5 | 0.12 | - |
| Telephone closets | - | - | 0.00 | - |

For SI: 1 cubic foot per minute = 0.0004719 m3 /s, 1 ton = 908 kg, 1 cubic foot per minute per square foot = 0.00508 m 3 /(s • m 2 ), °C = [(°F) – 32]/1.8, 1 square foot = 0.0929 m 2 .

a.	Based on net occupiable floor area.

b.	Mechanical exhaust required and the recirculation of air from such spaces is prohibited. Recirculation of air that is contained completely within such spaces shall not be prohibited (see Section 403.2.1, Item 3).

c.	Spaces unheated or maintained below 50°F are not covered by these requirements unless the occupancy is continuous.

d.	Ventilation systems in enclosed parking garages shall comply with Section 404

e.	Rates are per water closet or urinal. The higher rate shall be provided where the exhaust system is designed to operate intermittently. The lower rate shall be permitted only where the exhaust system is designed to operate continuously while occupied.

f.	Rates are per room unless otherwise indicated. The higher rate shall be provided where the exhaust system is designed to operate intermittently. The lower rate shall be permitted only where the exhaust system is designed to operate continuously while occupied.

g.	Mechanical exhaust is required and recirculation from such spaces is prohibited. For occupancies other than science laboratories, where there is a wheel - type energy recovery ventilation (ERV) unit in the exhaust system design, the volume of air leaked from the exhaust airstream into the outdoor airstream within the ERV shall be less than 10 percent of the outdoor air volume. Recirculation of air that is contained completely within such spaces shall not be prohibited (see Section 403.2.1, Items 2 and 4).

h.	For nail salons, each manicure and pedicure station shall be provided with a source capture system capable of exhausting not less than 50 cfm per station. Exhaust inlets shall be located in accordance with Section 502.20. Where one or more required source capture systems operate continuously during occupancy, the exhaust rate from such systems shall be permitted to be applied to the exhaust flow rate required by Table 403.3.1.1 for the nail salon.

i.	Outpatient facilities to which the rates apply are freestanding birth centers, urgent care centers, neighborhood clinics and physicians’ offices, Class 1 imaging facilities, outpatient psychiatric facilities, outpatient rehabilitation facilities, and outpatient dental facilities.

j.	The requirements of this table provide for acceptable IAQ. The requirements of this table do not address the airborne transmission or airborne viruses, bacteria, and other infectious contagions.

k.	These rates are intended only for outpatient dental clinics where the amount of nitrous oxide is limited. They are not intended for dental operatories in institutional buildings where nitrous oxide is piped.

407.1 General. Mechanical ventilation for ambulatory care facilities and Group I-2occupancies shall be designed and installed in accordance with this code, ASHRAE/ASHE 170 and NFPA 99.

(M11297 / M21-21 AM)

###### TABLE 403.3.1.1 MINIMUM VENTILATION RATES

Portions of table not shown remain unchanged.

| OCCUPANCY CLASSIFICATION | OCCUPANT DENSITY #/1000 FT 2 a | PEOPLE OUTDOOR AIRFLOW RATE IN BREATHING ZONE, R p CFM/PERSON | AREA OUTDOOR AIRFLOW RATE IN BREATHING ZONE, R a CFM/FT 2 a | EXHAUST AIRFLOW RATE CFM/FT 2 a |
| --- | --- | --- | --- | --- |
| Storage |  |  |  |  |
| Refrigerated warehouses/freezers | — | 10 | — | 0.75 |
| Repair garages, enclosed parking garagesb, d | — | — | — | 0.75 |
| Warehousesi | — | 10 | 0.06 | — |

For SI: 1 cubic foot per minute = 0.0004719 m3 /s, 1 ton = 908 kg, 1 cubic foot per minute per square foot = 0.00508 m 3 /(s • m 2 ), °C = [(°F) – 32]/1.8, 1 square foot = 0.0929 m 2 .

a.	Based on net occupiable floor area.

b.	Mechanical exhaust required and the recirculation of air from such spaces is prohibited. Recirculation of air that is contained completely within such spaces shall not be prohibited (see Section 403.2.1, Item 3).

c.	Spaces unheated or maintained below 50°F are not covered by these requirements unless the occupancy is continuous.

d.	Ventilation systems in enclosed parking garages shall comply with Section 404.

e.	Rates are per water closet or urinal. The higher rate shall be provided where the exhaust system is designed to operate intermittently. The lower rate shall be permitted only where the exhaust system is designed to operate continuously while occupied.

f.	Rates are per room unless otherwise indicated. The higher rate shall be provided where the exhaust system is designed to operate intermittently. The lower rate shall be permitted only where the exhaust system is designed to operate continuously while occupied.

g.	Mechanical exhaust is required and recirculation from such spaces is prohibited. For occupancies other than science laboratories, where there is a wheel - type energy recovery ventilation (ERV) unit in the exhaust system design, the volume of air leaked from the exhaust airstream into the outdoor airstream within the ERV shall be less than 10 percent of the outdoor air volume. Recirculation of air that is contained completely within such spaces shall not be prohibited (see Section 403.2.1, Items 2 and 4).

h.	For nail salons, each manicure and pedicure station shall be provided with a source capture system capable of exhausting not less than 50 cfm per station. Exhaust inlets shall be located in accordance with Section 502.20. Where one or more required source capture systems operate continuously during occupancy, the exhaust rate from such systems shall be permitted to be applied to the exhaust flow rate required by Table 403.3.1.1 for the nail salon.

i.	The occupiable floor area in warehouses shall not include the floor area of self-storage units, floor areas under rack storage, or designated palletized storage floor areas.

(M11298 / M22-21 AS)

###### TABLE 403.3.2.3 MINIMUM REQUIRED LOCAL EXHAUST RATES FOR GROUP R-2, R-3 AND R-4 OCCUPANCIES

| AREA TO BE EXHAUSTED | EXHAUST RATE CAPACITY |
| --- | --- |
| Kitchens | 100 cfm intermittent or 25 50 cfm continuous |
| Bathrooms and toilet rooms | 50 cfm intermittent or 20 25 cfm continuous |

For SI: 1 cubic foot per minute = 0.0004719 m3/s.

(M11300 / M24-21 AS)

CHAPTER 5 EXHAUST SYSTEMS

501.3.1	Location of exhaust outlets. The termination point of exhaust outlets and ducts discharging to the outdoors shall be located with the following minimum distances:

1.	For ducts conveying explosive or flammable vapors, fumes or dusts: 30 feet (9144 mm) from property lines; 10 feet (3048 mm) from operable openings into buildings; 6 feet (1829 mm) from exterior walls and roofs; 30 feet (9144 mm) from combustible walls and operable openings into buildings that are in the direction of the exhaust discharge; 10 feet (3048 mm) above adjoining grade.

2.	For other product-conveying outlets: 10 feet (3048 mm) from the property lines; 3 feet (914 mm) from exterior walls and roofs; 10 feet (3048 mm) from operable openings into buildings; 10 feet (3048 mm) above adjoining grade.

3.	For all environmental air exhaust: 3 feet (914 mm) from property lines; 3 feet (914 mm) from operable openings, except where the exhaust opening is located not less than 1 foot (305 mm) above the gravity air intake opening into buildings for all occupancies other than Group U; and 10 feet (3048 mm) from mechanical air intakes. Such exhaust shall not be considered hazardous or noxious. Separation is not required between intake air openings and living space exhaust air openings of an individual dwelling unit or sleeping unit where an approved factory-built intake/exhaust combination termination fitting is used to separate the air streams in accordance with the fan manufacturer's instructions.

No change to item 4 and 5

(M11303 / M28-21 AS)/(M11294 / M16-21 AMPC1)

501.6 Common ducts. The discharge from exhaust fans serving separate dwelling or sleeping units shall not be connected to a common duct or shaft, except where the common duct or shaft is maintained at a negative pressure.

(M11304 / M29-21 Part I AS)

Revise as follows:

504.2 Exhaust penetrations. Where a clothes dryer exhaust duct penetrates a wall or ceiling membrane, the annular space shall be sealed with noncombustible material, approved fire caulking or a noncombustible dryer exhaust duct wall receptacle. Ducts that exhaust clothes dryers shall not penetrate or be located within any fireblocking, draftstopping draftstops or any wall, floor/ceiling or other assembly required by the Florida Building Code, Building to be fire-resistance rated, unless such duct is constructed of galvanized steel or aluminum of the thickness specified in Section 603.4 and the fire-resistance rating is maintained in accordance with the Florida Building Code, Building . Fire dampers, combination fire/smoke dampers and any similar devices that will obstruct the exhaust flow shall be prohibited in clothes dryer exhaust ducts.

(M11228 / FS47-21 Part III AS)

504.10 Commercial clothes dryers. The installation of dryer exhaust ducts serving commercial clothes dryers shall comply with the appliance manufacturer’s installation instructions. Exhaust fan motors installed in exhaust systems shall be located outside of the airstream. In multiple installations, the fan shall operate continuously or be interlocked to operate when any individual unit is operating. Ducts shall have a minimum clearance of 6 inches (152 mm) to combustible materials. Clothes dryer transition ducts used to connect the appliance to the exhaust duct system shall be limited to single lengths not to exceed 8 feet (2438 mm) in length and shall be listed and labeled in accordance with UL 2158A for the application. Transition ducts shall not be concealed within construction.

(M11305 / M31-21 AS)

506.2	Corrosion protection. Ducts and exhaust equipment exposed to the outside atmosphere or subject to a corrosive environment shall be protected against corrosion in an approved manner.

(M11307 / M34-21 AS)

Revise as follows:

506.3	Ducts serving Type I hoods Grease duct systems. Type I exhaust ducts shall be independent of all other exhaust systems except as provided in Section 506.3.5. Commercial kitchen Grease duct systems serving Type I hoods shall be designed, constructed and installed in accordance with Sections 506.3.1 through 506.3.13.3.

Delete without substitution:

506.3.1	 Duct materials. Ducts serving Type I hoods shall be constructed of materials in accordance with Sections 506.3.1.1 and 506.3.1.2.

Revise as follows:

506.3.1.1	506.3.1 Grease duct materials. Grease ducts serving Type I hoods shall be constructed of steel having a minimum thickness of 0.0575 inch (1.463 mm) (No. 16 gage) or stainless steel not less than 0.0450 inch (1.14 mm) (No. 18 gage) in thickness.

Exception: Factory-built commercial kitchen grease ducts listed and labeled in accordance with UL 1978 and installed in accordance with Section 304.1.

506.3.2	Joints, seams and penetrations of grease ducts. Joints, seams and penetrations of grease ducts shall be made with a continuous liquid-tight weld or braze made on the external surface of the grease duct system.

Exceptions:

1.	Penetrations shall not be required to be welded or brazed where sealed by devices that are listed for the application.

2.	Internal welding or brazing shall not be prohibited provided that the joint is formed or ground smooth and is provided with ready access for inspection.

3.	Factory-built commercial kitchen grease ducts listed and labeled in accordance with UL 1978 and installed in accordance with Section 304.1.

506.3.2.1	Grease Duct duct joint types. Grease duct Duct joints shall be butt joints, welded flange joints with a maximum flange depth of 1/2 inch (12.7 mm) or overlapping duct joints of either the telescoping or bell type. Overlapping joints shall be installed to prevent ledges and obstructions from collecting grease or interfering with gravity drainage to the intended collection point. The difference between the inside cross-sectional dimensions of overlapping sections of duct shall not exceed 1/4 inch (6.4 mm). The length of overlap for overlapping duct joints shall not exceed 2 inches (51 mm).

506.3.2.2	Grease Duct duct-to-hood joints. Grease Duct duct-to-hood joints shall be made with continuous internal or external liquid-tight welded or brazed joints. Such joints shall be smooth, accessible available for inspection, and without grease traps.

Exceptions: This section shall not apply to:

1.	A vertical duct-to-hood collar connection made in the top plane of the hood in accordance with all of the following:

1.1.	The hood duct opening the exhaust outlet of the hood shall have a 1-inch-deep (25 mm), full perimeter, welded flange turned down into the hood interior at an angle of 90 degrees (1.57 rad) from the plane of the opening.

1.2.	The grease duct shall have a 1-inch-deep (25 mm) flange made by a 1-inch by 1-inch (25 mm by 25 mm) angle iron welded to the full perimeter of the grease duct not less than 1 inch (25 mm) above the bottom end of the duct.

1.3.	A gasket rated for use at not less than 1,500ºF (816ºC) is installed between thegrease duct flange and the top of the hood.

1.4.	The grease duct-to-hood joint shall be secured by stud bolts not less than1/4 inch (6.4 mm) in diameter welded to the hood with a spacing not greater than 4 inches (102 mm) on center for the full perimeter of the opening. The bolts and nuts shall be secured with lockwashers.

2.	Listed and labeled grease duct-to-hood collar connections installed in accordance with Section 304.1.

506.3.2.3	Grease Duct duct-to-exhaust fan connections. Grease Duct duct-to-exhaust fan connections shall be flanged and gasketed at the base of the fan for vertical discharge fans; shall be flanged, gasketed and bolted to the inlet of the fan for side-inlet utility fans; and shall be flanged, gasketed and bolted to the inlet and outlet of the fan for in-line fans. Gasket and sealing materials shall be rated for continuous duty at a temperature of not less than 1,500ºF (816ºC).

506.3.2.4	Vibration isolation. A vibration isolation connector for connecting a grease duct to a fan shall consist of noncombustible packing in a metal sleeve joint of approved design or shall be a coated-fabric flexible grease duct connector listed and labeled for the application. Vibration isolation connectors shall be installed only at the connection of a grease duct to a fan inlet or outlet.

506.3.2.5	Grease duct test. A field test shall be performed Prior prior to the use or concealment of any portion of a grease duct system, a leakage test shall be performed. Grease ducts Ducts shall be considered to be concealed where installed in shafts or covered by coatings or wraps that prevent the ductwork grease ducts from being visually inspected on all sides. The permit holder shall be responsible to provide the necessary equipment and perform the grease duct leakage test. A light test shall be performed to determine that all welded and brazed joints are liquid tight. A light test shall be performed by passing a lamp having a power rating of not less than 100 watts through the entire section odf uctwork grease ducts to be tested. The lamp shall be open so as to emit light equally in all directions perpendicular to the duct walls. A test shall be performed for the entire grease duct system, including the hood-to-duct connection. The grease duct work system shall be permitted to be tested in sections, provided that every joint is tested. For listed factory-built grease ducts, this test shall be limited to duct joints assembled in the field and shall exclude factory welds.  The test shall be performed in accordance with either Section 506.3.2.5.1 or Section 506.3.2.5.2.

Add new text as follows:

506.3.2.5.1 Light test. A duct test shall be performed by passing a lamp having not less than 1600 lumens, through the entire section of ductwork to be tested. The lamp shall be open so as to emit light equally in all directions perpendicular to the duct walls. A successful test shall be where the light from the lamp is not visible at any point on the exterior of the duct.

506.3.2.5.2 Water spray test. A duct test shall be performed by simulating a cleaning operation, of the interior of the duct. A water pump, capable of a flowing outlet pressure of not less than 1200 psi ( 8,274 kPa) shall be used, along with any necessary hoses and spray nozzles, to apply high pressure water to the inside surfaces of the duct. A successful test shall be where there is no evidence of cleaning water at any point on the exterior of the duct.

506.3.3 Grease duct supports. Grease duct bracing and supports shall be of noncombustible material securely attached to the structure and designed to carry gravity and seismic loads within the stress limitations of the Florida Building Code, Building . Bolts, screws, rivets and other mechanical fasteners shall not penetrate grease duct walls.

506.3.4 Air velocity. Grease duct systems serving a Type I hood shall be designed and installed to provide an air velocity within the grease duct system of not less than 500 feet per minute (2.5 m/s).

Exception: The velocity limitations shall not apply within grease duct transitions utilized to connect grease ducts to differently sized or shaped openings in hoods and fans, provided that such transitions do not exceed 3 feet (914 mm) in length and are designed to prevent the trapping of grease.

506.3.5 Separation of grease duct system. A separate grease duct system shall be provided for each Type I hood. A separate grease duct system is not required where all of the following conditions are met:

1.	All interconnected hoods are located within the same story.

2.	All interconnected hoods are located within the same room or in adjoining rooms.

3.	Interconnecting grease ducts do not penetrate assemblies required to be fire-resistance rated.

4.	The grease duct system does not serve solid-fuel-fired appliances.

506.3.7	Prevention of grease accumulation in grease ducts. Duct Grease duct systems serving a Type I hood shall be constructed and installed so that grease cannot collect in any portion thereof, and the system shall slope not less than one-fourth unit vertical in 12 units horizontal (2-percent slope) toward the hood or toward a grease reservoir designed and installed in accordance with Section 506.3.7.1. Where horizontal grease ducts exceed 75 feet (22 860 mm) in length, the slope shall be not less than one unit vertical in 12 units horizontal (8.3-percent slope).

Exception: Factory-built grease ducts shall be installed at a slope that is in accordance with the listing and manufacturer's installation instructions.

506.3.7.1	Grease duct reservoirs. Grease duct reservoirs shall:

1.	Be constructed as required for the grease duct they serve.

2.	Be located on the bottom of the horizontal grease duct or the bottommost section of the grease duct riser.

3.	Extend across the full width of the grease duct and have a length of not less than 12 inches (305 mm).

4.	Have a depth of not less than 1 inch (25 mm).

5.	Have a bottom that slopes to a drain.

6.	Be provided with a cleanout opening constructed in accordance with Section 506.3.8 and installed to provide direct access to the reservoir. The cleanout opening shall be located on a side or on top of the grease duct so as to permit cleaning of the reservoir.

7.	Be installed in accordance with the manufacturer’s instructions where manufactured devices are utilized.

506.3.8	Grease duct cleanouts and openings. Grease duct cleanouts and openings shall comply with all of the following:

1.	Grease ducts shall not have openings except where required for the operation and maintenance of the system.

2.	Sections of grease ducts that are inaccessible from the hood or discharge openings shall be provided with cleanout openings spaced not more than 20 feet (6096 mm) apart and not more than 10 feet (3048 mm) from changes in direction greater than 45 degrees (0.79 rad).

3.	Cleanouts and openings shall be equipped with tight-fitting doors constructed of steel having a thickness not less than that required for the grease duct.

4.	Cleanout doors shall be installed liquid tight.

5.	Door assemblies including any frames and gaskets shall be approved for the application and shall not have fasteners that penetrate the grease duct.

6.	Gasket and sealing materials shall be rated for not less than 1,500ºF (816ºC).

7.	Listed door assemblies shall be installed in accordance with the manufacturer’s instructions.

506.3.8.1	Personnel entry. Where a grease duct ductwork is large enough to allow entry of personnel, not less than oneapproved or listed opening having dimensions not less than 22 inches by 20 inches (559 mm by 508 mm) shall be provided in the horizontal sections, and in the top of vertical risers. Where such entry is provided, the grease duct and its supports shall be capable of supporting the additional load, and the cleanouts specified in Section 506.3.8 are not required.

506.3.8.2	Cleanouts serving in-line fans. A cleanout shall be provided for both the inlet side and outlet side of an in-line fan except where a grease duct does not connect to the fan. Such cleanouts shall be located within 3 feet (914 mm) of the fan duct connections.

506.3.9	Grease duct horizontal cleanouts. Cleanouts serving horizontal sections of grease ducts shall:

1.	Be spaced not more than 20 feet (6096 mm) apart.

2.	Be located not more than 10 feet (3048 mm) from changes in direction that are greater than 45 degrees (0.79 rad).

3.	Be located on the bottom only where other locations are not available and shall be provided with internal damming of the opening such that grease will flow past the opening without pooling. Bottom cleanouts and openings shall be approved for the application and installed liquid tight.

4.	Not be closer than 1 inch (25 mm) from the edges of the grease duct.

5.	Have opening dimensions of not less than 12 inches by 12 inches (305 mm by 305 mm). Where such dimensions preclude installation, the opening shall be not less than 12 inches (305 mm) on one side and shall be large enough to provide access for cleaning and maintenance.

6.	Be located at grease reservoirs.

7.	Be located within 3 feet (914 mm) of horizontal discharge fans.

506.3.10	Underground grease duct installation. Underground grease duct installations shall comply with all of the following:

1.	Underground grease ducts shall be constructed of steel having a minimum thickness of 0.0575 inch (1.463 mm) (No. 16 gage) and shall be coated to provide protection from corrosion or shall be constructed of stainless steel having a minimum thickness of 0.0450 inch (1.140 mm) (No. 18 gage).

2.	The underground grease duct system shall be tested and approved in accordance with Section 506.3.2.5 prior to coating or placement in the ground.

3.	The underground grease duct system shall be completely encased in concrete with a minimum thickness of 4 inches (102 mm).

4.	Ducts shall slope toward grease reservoirs.

5.	A grease reservoir with a cleanout to allow cleaning of the reservoir shall be provided at the base of each vertical grease duct riser.

6.	Cleanouts shall be provided with access to permit cleaning and inspection of the grease duct in accordance with Section 506.3.

7.	Cleanouts in horizontal grease ducts shall be installed on the topside of the grease duct.

8.	Cleanout locations shall be legibly identified at the point of access from the interior space.

506.3.11	Grease duct enclosures. A commercial kitchen grease duct serving a Type I hood that penetrates a ceiling, wall, floor or any concealed space shall be enclosed from the point of penetration to the outlet terminal. In-line exhaust fans not located outdoors shall be enclosed as required for grease ducts. A grease duct shall penetrate exterior walls only at locations where unprotected openings are permitted by the Florida Building Code, Building. The grease duct enclosure shall serve a single grease duct and shall not contain other ducts, piping or wiring systems. Grease duct Duct enclosures shall be a shaft enclosure in accordance with Section 506.3.11.1, a field-applied enclosure assembly in accordance with Section 506.3.11.2 or a factory-built grease duct enclosure assembly in accordance with Section 506.3.11.3. Grease duct Duct enclosures shall have a fire-resistance rating of not less than that of the assembly penetrated and not less than 1 hour. Fire dampers and smoke dampers shall not be installed in grease ducts.

Exception: A grease duct enclosure shall not be required for a grease duct that penetrates only a non fire-resistance-rated roof/ceiling assembly.

506.3.11.1	Shaft enclosure. Grease ducts constructed in accordance with Section 506.3.1 shall be permitted to be enclosed in accordance with the Florida Building Code, Building requirements for shaft construction. Such grease duct systems and exhaust equipment shall have a clearance to combustible construction of not less than 18 inches (457 mm), and shall have a clearance to noncombustible construction and gypsum wallboard attached to noncombustible structures of not less than 6 inches (152 mm). Shaft Duct enclosures shall be sealed around the grease duct at the point of penetration and vented to the outside of the building through the use of weather-protected openings.

506.3.11.2	Field-applied grease duct enclosure. Grease ducts constructed in accordance with Section 506.3.1 shall be enclosed by a listed and labeled field-applied grease duct enclosure material, systems, product, or method of construction specifically evaluated for such purpose in accordance with ASTM E2336. The surface of the grease duct shall be continuously covered on all sides from the point at which the grease duct originates to the outlet terminal. Grease duct Duct penetrations shall be protected with a through-penetration firestop system tested and listed in accordance with ASTM E814 or UL 1479 and having a “F” and “T” rating equal to the fire-resistance rating of the assembly being penetrated. The grease duct enclosure and firestop system shall be installed in accordance with the listing and the manufacturer’s instructions. Partial application of a field-applied grease duct enclosure shall not be installed for the sole purpose of reducing

clearances to combustibles at isolated sections of grease duct. Exposed duct-wrap systems shall be protected where subject to physical damage.

506.3.11.3	Factory-built grease duct enclosure assemblies. Factory-built grease ducts incorporating integral enclosure materials shall be listed and labeled for use as grease duct enclosure assemblies specifically evaluated for such purpose in accordance with UL 2221. Grease duct Duct penetrations shall be protected with a through-penetration firestop system tested and listed in accordance with ASTM E814 or UL 1479 and having an "F" and "T" rating equal to the fire-resistance rating of the assembly being penetrated. The grease duct enclosure assembly and firestop system shall be installed in accordance with the listing and the manufacturer’s instructions.

506.3.12	Grease duct fire-resistive access opening. Where cleanout openings are located in grease ducts within a fire-resistance-rated enclosure, access openings shall be provided in the enclosure at each cleanout point. Access openings shall be equipped with tight-fitting sliding or hinged doors that are equal in fire-resistive protection to that of the shaft or enclosure. An approved sign shall be placed on access opening panels with wording as follows: “ACCESS PANEL. DO NOT OBSTRUCT.”

506.3.13	Exhaust outlets serving Type I hoods. Exhaust outlets for grease ducts serving Type I hoods shall conform to the requirements of Sections 506.3.13.1 through 506.3.13.3.

506.5.1	Exhaust fans. Exhaust fan housings serving a Type I hood shall be constructed as required for grease ducts in accordance with Section 506.3.1.1.

Exception: Fans listed and labeled in accordance with UL 762. UL 705

506.5.1.2 In-line fan location. Where enclosed grease duct systems are connected to in-line fans not located outdoors, the fan shall be located in a room or space having the same fire-resistance rating as the grease duct enclosure. Access shall be provided for servicing and cleaning of fan components. Such rooms or spaces shall be ventilated in accordance with the fan manufacturer’s installation instructions.

506.5.2 Pollution-control units. The installation of pollution-control units shall be in accordance with all of the following:

1.	Pollution-control units shall be listed and labeled in accordance with UL 8782.

2.	Fans serving pollution-control units shall be listed and labeled in accordance with UL 762.UL 705.

3.	Bracing and supports for pollution-control units shall be of noncombustible material securely attached to the structure and designed to carry gravity and seismic loads within the stress limitations of the Florida Building Code, Building.

4.	Pollution-control units located indoors shall be listed and labeled for such use. Where enclosed grease duct systems, as required by Section 506.3.11, are connected to a pollution control unit, such unit shall be listed and labeled, in accordance with UL 2221 or ASTM E2336, for location in an enclosure having the same fire-resistance rating as the duct enclosure. Access shall be provided for servicing and cleaning of the unit. The space or enclosure shall be ventilated in accordance with the manufacturer’s installation instructions.

5.	Clearances shall be maintained between the pollution-control unit and combustible material in accordance with the listing.

6.	Roof-mounted pollution-control units shall be listed for outdoor installation and shall be mounted not less than 18 inches (457 mm) above the roof.

7.	Exhaust outlets for pollution-control units shall be in accordance with Section 506.3.13.

8.	An airflow differential pressure control shall be provided to monitor the pressure drop across the filter sections of a pollution-control unit. When the airflow is reduced below the design velocity, the airflow differential pressure control shall activate a visual alarm located in the area where cooking operations occur.

9.	Pollution-control units shall be provided with a factory-installed fire suppression system.

10.	Service space shall be provided in accordance with the manufacturer’s instructions for the pollution control unit and the requirements of Section 306.

11.	Wash-down drains shall discharge through a grease interceptor and shall be sized for the flow. Drains shall be sealed with a trap or other approved means to prevent air bypass. Where a trap is utilized it shall have a seal depth that accounts for the system pressurization and evaporation between cleanings.

12.	Protection from freezing shall be provided for the water supply and fire suppression systems where such systems are subject to freezing.

13.	Grease duct Duct connections to pollution-control units shall be in accordance with Section 506.3.2.3. Where water splash or carryover can occur in the transition duct as a result of a washing operation, the transition duct shall slope downward toward the cabinet drain pan for a length not less than 18 inches (457 mm). Grease ducts Ducts shall transition to the full size of the unit’s inlet and outlet openings.

14.	Extra-heavy-duty appliance exhaust systems shall not be connected to pollution-control units except where such units are specifically designed and listed for use with solid fuels.

15.	Pollution-control units shall be maintained in accordance with the manufacturer’s instructions.

506.5.4 Exhaust fan mounting. Upblast fans serving Type I hoods and installed in a vertical or horizontal position shall be hinged, supplied with a flexible weatherproof electrical cable to permit inspection and cleaning and shall be equipped with a means of restraint to limit the swing of the fan on its hinge. The grease duct system ductwork shall extend not less than 18 inches (457 mm) above the roof surface.

507.2.4 Type I supports. Type I hoods shall be secured in place by noncombustible supports. Type I hood supports shall be adequate for the applied load of the hood, the unsupported grease duct system ductwork, the effluent loading and the possible weight of personnel working in or on the hood.

506.3.1.2 508.1.3 Makeup air ducts. Makeup air ducts connecting to or within 18 inches (457 mm) of a Type I hood shall be constructed and installed in accordance with Sections 603.1, 603.3, 603.4, 603.9, 603.10 and 603.12. Duct insulation installed within 18 inches (457 mm) of a Type I hood shall be noncombustible or shall be listed for the application.

(M11308 / M35-21 AS)/ (M11229 / G1-21 Part V AS)/ (M11310 / M38-21 AS)/ (M11311 / M39-21 AS)

507.1	General. Commercial kitchen exhaust hoods shall comply with the requirements of this section. Hoods shall be Type I or II and shall be designed to capture and confine cooking vapors and residues. A Type I hood shall be installed at or above appliances in accordance with Section 507.2. or A Type II hood shall be installed at or above appliances in accordance with Sections 507.2 and Section 507.3. Where any cooking appliance under a single hood requires a Type I hood, a Type I hood shall be installed. Where a Type II hood is required, a Type I or Type II hood shall be installed. Where a Type I hood is installed, the installation of the entire system, including the hood, grease ducts, exhaust equipment and makeup air system shall comply with the requirements of Sections 506, 507,and 508 and 509

Exceptions:

1. Factory-built commercial exhaust hoods that are listed and labeled in accordance with UL 710, and installed in accordance with Section 304.1, shall not be required to comply with Sections 507.1.5, 507.1.6, 507.2.3, 507.2.5, 507.2.8, 507.2.10,  507.3.1, and 507.3.1, 507.4 and 507.5.

2. A hood shall not be required at or above any of the following:

22.1. Factory-built commercial cooking recirculating systems that are listed and labeled in accordance with UL 710B, and installed in accordance with Section 304.1, shall not be required to comply with Sections 507.1.5, 507.2.3, 507.2.5, 507.2.8, 507.3.1, 507.3.3, 507.4 and 507.5. Spaces in which such systems are located shall be considered to be kitchens and shall be ventilated in accordance with Table 403.3.1.1. For the purpose of determining the floor area required to be ventilated, each individual appliance shall be considered as occupying not less than 100 square feet (9.3 m2).

3	2.2. Where cooking appliances are equipped with integral down-draft exhaust systems and such appliances and exhaust systems are listed and labeled for the application in accordance with NFPA 96, a hood shall not be required at or above them.

4	2.3. Smoker ovens with integral exhaust systems, provided that the appliance is installed in accordance with the manufacturer's installation instructions, is are listed and tested for the application, and complies with Chapter 5.

3.	Ovens listed and labeled for use with wood fuel in accordance with UL 2162 and vented in accordance with the manufacturer's instructions.

4.	An electric cooking appliance listed and labeled in accordance with UL 197 for reduced grease emissions.

5.	Commercial electric dishwashers incorporating a self-contained condensing system listed and labeled in accordance with UL 921.

6.	Where the heat and moisture loads from dishwashers and appliances that produce heat or moisture and do not produce grease or smoke as a result of the cooking process are incorporated into the HVAC system design or into the design of a separate removal system. Spaces containing such cooking appliances that do not require Type II hoods shall be provided with exhaust at a rate of 0.70 cfm per square foot (0.00356 m3/(s • m2). For the purpose of determining the floor area required to be exhausted, each individual appliance that is not required to be installed under a Type II hood shall be considered as occupying not less than 100 square feet (9.3 m2). Such additional square footage shall be provided with exhaust at a rate of 0.70 cfm per square foot [0.00356 m3/(s • m2)].

507.1.1	Operation. Commercial kitchen exhaust hood systems shall operate during the cooking operation. The hood exhaust rate shall comply with either the listing of the hood Section 507.2.10, or shall comply with Section 507.3.4 507.5. The exhaust fan serving a Type I hood shall have automatic controls that will activate the fan when any appliance that requires such Type I hood is turned on, or a means of interlock shall be provided that will prevent operation of such appliances when the exhaust fan is not turned on. Where one or more temperature or radiant energy sensors are used to activate a Type I hood exhaust fan, the fan shall activate not more than 15 minutes after the first appliance served by that hood has been turned on. A method of interlock between an exhaust hood system and appliances equipped with standing pilot burners shall not cause the pilot burners to be extinguished. A method of interlock between an exhaust hood system and cooking appliances shall not involve or depend on any component of a fire-extinguishing system. The net exhaust volumes for hoods shall be permitted to be reduced during part-load cooking conditions, where engineered or listed multispeed or variable speed controls automatically operate the exhaust system to maintain capture and removal of cooking effluents as required by this section. Reduced volumes shall not be below that required to maintain capture and removal of effluents from the idle cooking appliances that are operating in a standby mode.

507.1.2	Domestic cooking appliances used for commercial purposes. Domestic cooking appliances utilized for commercial purposes shall be provided with either Type I or Type II hoods as required for the type of appliances and processes in accordance with Sections

507.2	and 507.3. Domestic cooking appliances utilized for domestic cooking shall comply with Section 505.

507.4	507.1.6 Hood size and location. Hoods shall comply with the overhang, setback and height requirements in accordance with Sections 507.4.1 507.6.1 and 507.4.2 507.1.6.2, based on the type of hood.

507.4.1	507.1.6.1 Canopy size and location. The inside lower edge of canopy-type Type I and II commercial hoods shall overhang or extend a horizontal distance of not less than 6 inches (152 mm) beyond the edge of the top horizontal surface of the appliance on all open sides. The vertical distance between the front lower lip of the hood and such surface shall not exceed 4 feet (1219 mm).

Exception: The hood shall be permitted to be flush with the outer edge of the cooking surface where the hood is closed to theappliance side by a noncombustible wall or panel.

507.4.2	507.1.6.2 Noncanopy size and location. Noncanopy-type hoods shall be located not greater than 3 feet (914 mm) above the cooking surface. The edge of the hood shall be set back not greater than 1 foot (305 mm) from the edge of the cooking surface.

507.6	507.1.7 Performance test. A performance test shall be conducted upon completion and before final approval of the installation of a ventilation system serving commercial cooking appliances. The test shall verify the rate of exhaust airflow required by Section 507.5

507.2.10 or Section 507.3.4, makeup airflow required by Section 508 and proper operation as specified in this chapter. The permit holder shall furnish the necessary test equipment and devices required to perform the tests.

507.6.1	507.1.7.1 Capture and containment test. The permit holder shall verify capture and containment performance of the exhaust system. This field test shall be conducted with all appliances under the hood at operating temperatures, with all sources of outdoor air providing makeup air for the hood operating and with all sources of recirculated air providing conditioning for the space in which the hood is located operating. Capture and containment shall be verified visually by observing smoke or steam produced by actual or simulated cooking, such as that provided by smoke generators.

507.5	507.2.10 Capacity of Tye I hoods. Commercial food service hoods shall exhaust a minimum net quantity of air determined in accordance with this section and Sections 507.5.1 507.2.10.1 through 507.5.5 507.2.10.4. The net quantity of exhaust air shall be calculated by subtracting any airflow supplied directly to a hood cavity from the total exhaust flow rate of a hood. Where any combination of heavy-duty, medium-duty and light-duty cooking appliances are utilized under a single hood, the exhaust rate required by this section for the heaviest duty appliance covered by the hood shall be used for the entire hood.

507.5.1	507.2.10.1 Extra-heavy-duty cooking appliances. The minimum net airflow for hoods, as determined by Section 507.1, used for

extra-heavy-duty cooking appliances shall be determined as follows:

| Type of Hood | CFM per linear foot of hood |
| --- | --- |
| Backshelf/pass-over | Not allowed |
| Double island canopy (per side) | 550 |
| Eyebrow | Not allowed |
| Single island canopy | 700 |
| Wall-mounted canopy | 550 |

For SI: 1 cfm per linear foot = 1.55 L/s per linear meter.

507.5.2	507.2.10.2 Heavy-duty cooking appliances. The minimum net airflow for hoods, as determined by Section 507.1, used for

heavy-duty cooking appliances shall be determined as follows:

| Type of Hood | CFM per linear foot of hood |
| --- | --- |
| Backshelf/pass-over | 400 |
| Double island canopy (per side) | 400 |
| Eyebrow | Not allowed |
| Single island canopy | 600 |
| Wall-mounted canopy | 400 |

For SI: 1 cfm per linear foot = 1.55 L/s per linear meter.

507.5.3	507.2.10.3 Medium-duty cooking appliances. The minimum net airflow for hoods, as determined by Section 507.1, used for

medium-duty cooking appliances shall be determined as follows:

| Type of Hood | CFM per linear foot of hood |
| --- | --- |

| Backshelf/pass-over | 300 |
| --- | --- |
| Double island canopy (per side) | 300 |
| Eyebrow | 250 |
| Single island canopy | 500 |
| Wall-mounted canopy | 300 |

For SI: 1 cfm per linear foot = 1.55 L/s per linear meter.

509.1	507.2.11 Where required Fire suppression systems. Cooking appliances required by Section 507.2 to have a Type I hood shall be provided with an approved automatic fire suppression system complying with Section 904.12 of the Florida Building Code, Building and the Florida Fire Prevention Code .

507.3	Type II hoods. Type II hoods shall be installed above light-duty cooking appliances dishwashers and appliances that produce heat or moisture and do not produce grease or smoke as a result of the cooking process, except where the heat and moisture loads from such appliances are incorporated into the HVAC system design or into the design of a separate removal system. Type II hoods shall be installed above all appliances that produce products of combustion and do not produce grease or smoke as a result of the cooking process. Spaces containing cooking appliances that do not require Type II hoods shall be provided with exhaust at a rate of 0.70 cfm per square foot (0.00356 m3/(s • m2). For the purpose of determining the floor area required to be exhausted, each individual appliance that is not required to be installed under a Type II hood shall be considered as occupying not less than 100 square feet (9.3 m2). Such additional square footage shall be provided with exhaust at a rate of 0.70 cfm per square foot [0.00356 m3/(s • m2)].

Add new text as follows:

507.3.4 Capacity of Type II hoods. Type II hoods shall exhaust a minimum net quantity of air determined in accordance with this section and Sections 507.3.4.1 through 507.3.4.2. The net quantity of exhaust air shall be calculated by subtracting any airflow supplied directly to a hood cavity from the total exhaust flow rate of a hood.

Revise as follows:

507.5.4	507.3.4.1 Light-duty cooking appliances. The minimum net airflow for hoods, as determined by Section 507.1, used for light-duty

cooking appliances and food service preparation shall be determined as follows:

| Type of Hood | CFM per linear foot of hood |
| --- | --- |
| Backshelf/pass-over | 250 |
| Double island canopy (per side) | 250 |
| Eyebrow | 250 |
| Single island canopy | 400 |
| Wall-mounted canopy | 200 |

For SI: 1 cfm per linear foot = 1.55 L/s per linear meter.

507.5.5	507.3.4.2 Dishwashing appliances. The minimum net airflow for Type II hoods used for dishwashing appliances shall be 100 cfm per linear foot (155 L/s per linear meter) of hood length.

Exception: Dishwashing appliances and equipment installed in accordance with Section 507.3.

(M11312 / M40-21 AS)/ (M11308 / M35-21 AS)

507.2	Type I hoods. Type I hoods shall be installed where cooking appliances produce grease or smoke as a result of the cooking process. Type I hoods shall be installed over medium-duty, heavy-duty and extra-heavy-duty cooking appliances.

Exception: A Type I hood shall not be required for an electric cooking appliance where an approved testing agency provides documentation that the appliance effluent contains 5 mg/m3 or less of grease when tested at an exhaust flow rate of 500 cfm (0.236 m3/s) in accordance with UL 710B.

507.3	Type II hoods. Type II hoods shall be installed above dishwashers and appliances that produce heat or moisture and do not produce grease or smoke as a result of the cooking process, except where the heat and moisture loads from such appliances are incorporated into the HVAC system design or into the design of a separate removal system. Type II hoods shall be installed above all appliances that produce products of combustion and do not produce grease or smoke as a result of the cooking process. Spaces containing cooking appliances that do not require Type II hoods shall be provided with exhaust at a rate of 0.70 cfm per square foot (0.00356 m3/(s • m2). For the purpose of determining the floor area required to be exhausted, each individual appliance that is not required to be installed under a Type II hood shall be considered as occupying not less than 100 square feet (9.3 m2). Such additional square footage shall be provided with exhaust at a rate of 0.70 cfm per square foot [0.00356 m3/(s • m2)].  A Type I hood shall be permitted to be installed for a required Type II hood provided that the Type I hood installation complies with all of the requirements for a Type I hood installation. Where such a Type I hood serves only dishwashers and appliances that require a Type II hood, the Type I hood shall not be required to have fire suppression or grease filters.

507.5.5 Dishwashing appliances. The minimum net airflow for Type II hoods used for dishwashing appliances shall be 100 cfm per linear

foot (155 L/s per linear meter) of hood length.

Exception: Dishwashing appliances and equipment installed in accordance with Section 507.3.

(M11313 / M41-21 AS)/(M11314 / M42-21 AS)/(M11315 / M43-21 AS)/(M11316 / M44-21 AS)/(M11317 / M45-21 AS)/(M11318 / M46-21 AS)

507.1.3 Fuel-burning appliances. Where vented fuel-burning appliances are located in the same room or space as the hood, provisions shall be made to prevent the hood system from interfering with normal operation of the appliance vents.

507.1.3 Fuel-burning appliances. Appliances equipped with draft hoods or atmospheric burners shall not be located in the same room or space containing a Type I or Type II hood except where the appliance is located in a sealed enclosure equipped with a self-closing device with combustion air obtained from the outdoors or from other spaces in the building in accordance with Chapter 7 or the Florida Building Code,  Fuel Gas.

(M11319 / M47-21 AS)

508.1.1 Makeup air temperature. The temperature differential between makeup air and the air in the conditioned space shall not exceed 10ºF (6ºC) except where the added heating and cooling loads of the makeup air do not exceed the capacity of the HVAC system.

508.1.1 Makeup air temperature. HVAC systems that serve the kitchen space shall have the additional capacity necessary for the latent and sensible loads that are introduced by the makeup air supplied to the kitchen space, or the makeup air shall be conditioned by dedicated systems such that the difference in temperature between the makeup air supplied to the kitchen space and the design setpoint temperature in the kitchen space is not greater than 10 degrees F (6 degrees C).

Exception: Makeup air supplied to a compensating hood shall not not be required to be conditioned.

(M11321 / M49-21 AS)

CHAPTER 6 DUCT SYSTEMS

602.1	General. Supply, return, exhaust, relief and ventilation air plenums shall be in accordance with this section. limited to uninhabited crawl spaces, areas above a ceiling or below the floor, attic spaces, mechanical equipment rooms and the framing cavities addressed in Section 602.3. Plenums shall be limited to one fire area. Air systems shall be ducted from the boundary of the fire area served directly to the air-handling equipment. Fuel-fired appliances shall not be installed within a plenum.

Add new text as follows:

602.1.1	 Locations limited. Plenums shall be limited to uninhabited crawl spaces, above a ceiling or below the floor, attic spaces, mechanical equipment rooms and the framing cavities addressed in Section 602.2.

602.1.2	 Limited to a fire area. . Plenums shall be limited to one fire area. Air systems shall be ducted from the boundary of the fire area served directly to the air-handling equipment.

602.1.3	 Fuel fired appliances. . Fuel-fired appliances shall not be installed within a plenum.

Revise as follows:

602.2 Construction of plenums.. Plenum enclosure construction materials that are exposed to the airflow shall comply with the requirements of Section 703.3 of the Florida Building Code, Building or such materials shall have a flame spread index of not more than 25 and a smoke-developed index of not more than 50 when tested in accordance with ASTM E84 or UL 723.The use of gypsum boards to form plenums shall be limited to systems where the air temperatures do not exceed 125ºF (52ºC) and the building and mechanical system design conditions are such that the gypsum board surface temperature will be maintained above the airstream dew-point temperature. Supply air plenums formed by gypsum boards shall not be incorporated in air-handling systems utilizing direct evaporative cooling systems.

602.3602.2.1 Stud cavity and joist space plenums. Stud wall cavities and the spaces between solid floor joists to be utilized as air

plenums shall comply with the following conditions:

1.	Such cavities or spaces shall not be utilized as a plenum for supply air.

2.	Such cavities or spaces shall not be part of a required fire-resistance-rated assembly.

3.	Stud wall cavities shall not convey air from more than one floor level.

4.	Stud wall cavities and joist space plenums shall comply with the floor penetration protection requirements of the  Florida Building Code, Building.

5.	Stud wall cavities and joist space plenums shall be isolated from adjacent concealed spaces by approved fireblocking as required in the Florida Building Code, Building.

6.	Stud wall cavities in the outside walls of building envelope assemblies shall not be utilized as air plenums.

Delete without substitution:

602.2.1.4	 Electrical equipment in plenums. Electrical equipment exposed within a plenum shall comply with Sections 602.2.1.4.1 and 602.2.1.4.2.

602.2.1.4.1	 Equipment in metallic enclosures. Electrical equipment with metallic enclosures exposed within a plenum shall be permitted.

602.2.1.4.2	 Equipment in combustible enclosures. Electrical equipment with combustible enclosures exposed within a plenum shall be

listed and labeled for such use in accordance with UL 2043.

Revise as follows:

602.2.1	602.3 Materials within plenums. Except as required by Sections 602.2.1.1 through 602.2.1.8, mMaterials within plenums shall be noncombustible or shall be in compliance with the applicable requirements in Sections 602.3.1 through 602.3.10. listed and labeled as having a flame spread index of not more than 25 and a smoke-developed index of not more than 50 when tested in accordance with ASTM E84 or UL 723.

Exceptions: This section shall not apply to the following:

1.	Rigid and flexible ducts and connectors shall conform to Section 603.Materials exposed within plenums in one- and two-family dwellings.

2.	Duct coverings, linings, tape and connectors shall conform to Sections 603 and 604. Combustible materials fully enclosed within one of the following:

3.	This section shall not apply to materials exposed within plenums in one- and two-family dwellings.

4.	This section shall not apply to smoke detectors.

5.	Combustible materials fully enclosed within one of the following:

2.1 Continuous noncombustible raceways or enclosures.

2.2 Approved gypsum board assemblies.

2.3 Materials listed and labeled for installation within a plenum and listed for the application.

        - Materials in Group H, Division 5 fabrication areas and the areas above and below the fabrication area that share a common air recirculation path with the fabrication area.

4. PVC pipes and fittings for the removal of condensate in air handler closets used as plenums in the dwelling units of R-2 and R-3 occupancies are acceptable when complying with all the following conditions:

4.1 Acceptance is limited to schedule 40 PVC pipe and fittings of 3/4” or 1” nominal diameter.

4.2 Acceptance is limited to a total pipe length of 48” or less.

4.3 PVC pipes and fittings shall comply with ASTM standards referred to in FMC 1202.4 and 1202.5.

(Step 2 – M11880 AS) (M11324 / M55-21 AM)

602.2.1.1	602.3.3 Wiring. Combustible electrical wires and cables and optical fiber cables exposed within a plenum shall be listed and labeled as having a peak optical density not greater than 0.50, an average optical density not greater than 0.15, and a flame spread distance not greater than 5 feet (1524 mm) when tested in accordance with NFPA 262, or shall be installed in metal raceways or metal sheathed cable. Combustible optical fiber and communication raceways exposed within a plenum shall be listed and labeled as having a peak optical density not greater than 0.5, an average optical density not greater than 0.15, and a flame spread distance not greater than 5 feet (1524 mm) when tested in accordance with UL 2024. Only plenum-rated wires and cables shall be installed in plenum-rated raceways.

602.2.1.2	602.3.4 Fire sprinkler piping. Plastic fire sprinkler piping exposed within a plenum shall be used only in wet pipe systems and shall be listed and labeled as having a peak optical density not greater than 0.50, an average optical density not greater than 0.15, and a flame spread distance not greater than 5 feet (1524 mm) when tested in accordance with UL 1887.

602.2.1.3	602.3.5 Pneumatic tubing. Combustible pneumatic tubing exposed within a plenum shall be listed and labeled as having a peak optical density not greater than 0.50, an average optical density not greater than 0.15, and a flame spread distance not greater than 5 feet (1524 mm) when tested in accordance with UL 1820.

602.2.1.5	602.3.6 Discrete electrical, plumbing and mechanical products in plenums. Where discrete electrical, plumbing and mechanical products and appurtenances are located in a plenum and have exposed combustible material, they shall be listed and labeled for such use in accordance with UL 2043.

Exception: Electrical equipment with metallic enclosures exposed within a plenum.

602.2.1.6	602.3.7 Foam plastic in plenums as interior finish or interior trim. Foam plastic in plenums used as interior wall or ceiling finish or interior trim shall exhibit a flame spread index of 25 or less and a smoke-developed index of 50 or less when tested in accordance with ASTM E84 or UL 723 at the maximum thickness and density intended for use, and shall be tested in accordance with NFPA 286 and meet the acceptance criteria of Section 803.1.2 of the Florida Building Code, Building. As an alternative to testing to NFPA 286, the foam plastic shall be approved based on tests conducted in accordance with Section 2603.9 of the Florida Building Code, Building.

Exceptions:

1.	Foam plastic in plenums used as interior wall or ceiling finish or interior trim shall exhibit a flame spread index of 75 or less and a smoke-developed index of 450 or less when tested in accordance with ASTM E84 or UL 723 at the maximum thickness and density intended for use, where it is separated from the airflow in the plenum by a thermal barrier complying with Section 2603.4 of the Florida Building Code, Building.

2.	Foam plastic in plenums used as interior wall or ceiling finish or interior trim, shall exhibit a flame spread index of 75 or less and a smoke-developed index of 450 or less when tested in accordance with ASTM E84 or UL 723 at the maximum thickness and density intended for use, where it is separated from the airflow in the plenum by corrosion-resistant steel having a base metal thickness of not less than 0.0160 inch (0.4 mm).

3.	Foam plastic in plenums used as interior wall or ceiling finish or interior trim, shall exhibit a flame spread index of 75 or less and a smoke-developed index of 450 or less when tested in accordance with ASTM E84 or UL 723 at the maximum thickness and density intended for use, where it is separated from the airflow in the plenum by not less than a 1-inch (25 mm) thickness of masonry or concrete.

602.2.1.7	602.3.8 Plastic plumbing piping and tubing. Plastic piping and tubing used in plumbing systems shall be listed and labeled as having a flame spread index not greater than 25 and a smoke-developed index not greater than 50 when tested in accordance with ASTM E84 or UL 723.

Exception: Plastic water distribution piping and tubing listed and labeled in accordance with UL 2846 as having a peak optical density not greater than 0.50, an average optical density not greater than 0.15, and a flame spread distance not greater than 5 feet (1524 mm), and installed in accordance with its listing.

602.2.1.8	602.3.9 Pipe and duct insulation within plenums. Pipe and duct insulation contained within plenums, including insulation adhesives, shall have a flame spread index of not more than 25 and a smoke-developed index of not more than 50 when tested in accordance with ASTM E84 or UL 723, using the specimen preparation and mounting procedures of ASTM E2231. Pipe and duct insulation shall not flame, glow, smolder or smoke when tested in accordance with ASTM C411 at the temperature to which they are exposed in service. The test temperature shall not fall below 250°F (121°C). Pipe and duct insulation shall be listed and labeled. Pipe and duct insulation shall not be used to reduce the maximum flame spread and smoke-developed indices except where the pipe or duct and its related insulation, coatings, and adhesives are tested as a composite assembly in accordance with Section 602.2.1.7 602.3.9.

Add new text as follows:

602.3.1	Ducts, connectors, duct coverings, linings, and tape. .

Rigid and flexible ducts and connectors shall conform to Section 603. Duct coverings, linings, tape and connectors shall conform to Sections 603 and 604.

602.3.2	Smoke detectors. .

Smoke detectors shall be listed and labeled.

602.3.10 Other combustible materials. Other combustible materials not covered by Section 602.3 shall be listed and labeled as having a flame spread index of not more than 25 and a smoke-developed index of not more than 50 when tested in accordance with ASTM E84 or UL 723.

(M11324 / M55-21 AM)

604.3 Coverings and linings. Duct coverings and linings, including adhesives where used, shall have a flame spread index not more than 25 and a smoke-developed index not more than 504 50, when tested in accordance with ASTM E84 or UL 723, using the specimen preparation and mounting procedures of ASTM E2231. Duct coverings and linings shall not flame, glow, smolder or smoke when tested in accordance with ASTM C411 at the temperature to which they are exposed in service. The test temperature shall not fall below 250°F (121°C). Coverings and linings shall be listed and labeled.

Exception Exceptions:

1.	Polyurethane foam insulation that is spray applied to the exterior of ducts in attics and crawl spaces shall be subject to all of the following requirements:

1.	The foam plastic insulation shall have a flame spread index not greater than 25 and a smoke-developed index not greater than 450, when tested in accordance with ASTM E84 or UL 723, using the specimen preparation and mounting procedures of ASTM E2231.

2.	The foam plastic insulation shall not flame, glow, smolder or smoke when tested in accordance with ASTM C411 at the temperature to which they are exposed in service. The test temperature shall not fall below 250°F (121°C).

3.	The foam plastic insulation complies with the requirements of Section 2603 of the Florida Building Code, Building.

4.	The foam plastic insulation is protected against ignition in accordance with the requirements of Section 2603.4.1.6 of the Florida Building Code, Building.

2.	Duct coverings added to the outside of ducts and not contained in plenums, including adhesives where used, shall have a flame spread index not more than 25 and a smoke-developed index not more than 450, when tested in accordance with ASTM E84 or UL 723, using the specimen preparation and mounting procedures of ASTM E2231. Duct coverings shall not flame, glow, smolder or smoke when tested in accordance with ASTM C411 at the temperature to which they are exposed in service. The test temperature shall not fall below 250°F (121°C). Coverings shall be listed and labeled.

(M11325 / M60-21 AM)

Revise Section 607.5.2 to read as follows:

# 607.5.2 Fire barriers.

# P

Ducts and air transfer openings that penetrate fire barriers shall be protected with listed fire dampers installed in accordance with their listing. Ducts and air transfer openings shall not penetrate enclosures for interior exit stairways and ramps and exit passageways except as permitted by Sections 1023.5 and 1024.6, respectively, of the Florida Building Code, Building.

Exception: Fire dampers are not required at penetrations of fire barriers where any of the following apply:

1.Penetrations are tested in accordance with ASTM E119 or UL 263 as part of the fire-resistance-rated assembly.

2.Ducts are used as part of an approved smoke control system in accordance with Section 513 and where the fire damper would interfere with the operation of the smoke control system.

3.Such walls are penetrated by fully ducted HVAC systems, have a required fire-resistance rating of 1 hour or less, are in areas of other than Group H and are in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2 of the International Building Code. For the purposes of this exception, a fully ducted HVAC system shall be a duct system for the structure’s HVAC system. Such a duct system shall be constructed of sheet steel not less than 26 gage [0.0217 inch (0.55 mm)] thickness and shall be continuous from the air-handling appliance or equipment to the air outlet and inlet terminals. Flexible air connectors shall be permitted in a fully ducted system, limited to the following installations:

3.1.Nonmetallic flexible connections that connect a duct to an air handling unit or equipment located within a mechanical room in accordance with Section 603.9.

3.2.Nonmetallic flexible air connectors in accordance with Section 603.6.2 that connect an overhead metal duct to a ceiling diffuser where the metal duct and ceiling diffuser are located within the same room.

M-FBC-M-Ch.7 – Glitch #1

CHAPTER 7 COMBUSTION AIR

No change

CHAPTER 8 CHIMNEYS AND VENTS

No change

CHAPTER 9 SPECIFIC APPLIANCES, FIREPLACES AND SOLID FUEL-BURNING EQUIPMENT

907.1 General. Factory built cremation furnaces and commercial direct-fed incinerators shall be listed and labeled in accordance with UL 2790. Factory-built incinerators for domestic applications shall be listed and labeled in accordance with UL 791.Incinerators and crematories cremation furnaces shall be listed and labeled in accordance with UL 791 and shall be installed in accordance with the manufacturer’s instructions.

(M11649 / FG7-21 Part II AS)

SECTION 912

INFRARED RADIANT  ELECTRIC SPACE HEATERS

912.1	General. Permanently installed electric infrared radiant space heaters shall comply be listed and labeled in accordance with UL 499 UL 2021, and installed in accordance with the manufacturer’s instructions.

912.3 Clearances. Heaters shall be installed with clearances from combustible material in accordance with the manufacturer’s installation instructions.

Revise as follows:

912.2	Support. Infrared radiant Electric space heaters shall be fixed in a position independent of fuel and electric supply lines. Hangers and brackets shall be noncombustible material.

(M11326 / M61-21 AS)

908.1 General. A cooling tower used in conjunction with an air-conditioning appliance shall be installed in accordance with the manufacturer’s instructions. Factory-built cooling towers shall be listed in accordance with UL 1995 or UL/CSA 60335-2-40.

916.1 General. Pool and spa heaters shall be installed in accordance with the manufacturer’s instructions. Oil-fired pool and spa heaters shall be tested in accordance with UL 726. Electric pool and spa heaters shall be tested in accordance with UL 1261. Pool and spa heat pump water heaters shall comply with UL 1995, UL/CSA 60335-2-40 or CSA C22.2 No. 236.

Exception: Portable residential spas and portable residential exercise spas shall comply with UL 1563 or CSA C22.2 No. 218.1.

(Step 2 – M12146 AS)

SECTION 931 STEAM BATH EQUIPMENT

931.1	 General. Steam bath equipment shall be listed and labeled in accordance with UL 499 and shall be installed in accordance with their listing and the manufacturer’s instructions.

(M11327 / M62-21 AS)

CHAPTER 10 BOILERS, WATER HEATERS AND PRESSURE VESSELS

1001.1 Scope. This chapter shall govern the installation, alteration and repair of boilers, water heaters and pressure vessels.

Exceptions:

1. – 8 No change

9.	Pressure vessels used in specific appliances and equipment that are regulated by Chapter 9 of this code.

(M11328 / M63-21AS)

CHAPTER 11 REFRIGERATION

Add new text as follows:

1101.2.1 Group A2L, A2, A3 and B1 high probability equipment. High probability equipment using Group A2L, A2, A3, or B1 refrigerant shall comply with UL 484, UL/CSA 60335-2-40, or UL/CSA 60335-2-89.

(M11338 / M72-21 AS)

Revise section 1101.5 to read as follows:

Section 1101.6 General. Refrigeration systems shall comply with the requirements of this code and, except as modified by this code, ASHRAE 15. Ammonia-refrigerating systems shall comply with this code and, except as modified by this code, ASHRAE 15 and IIAR 2.

Exception: Refrigeration systems that use A2L refrigerant shall be designed and installed in accordance with ASHRAE 15.

Supplement 5 – Glitch

Delete and substitute as follows:

1101.8 Change in refrigerant type. The type of refrigerant in refrigeration systems having a refrigerant circuit containing more than 220 pounds (99.8 kg) of Group A1 or 30 pounds (13.6 kg) of any other group refrigerant shall not be changed without prior notification to the code official and compliance with the applicable code provisions for the new refrigerant type.

1101.8 Changing Refrigerant. Changes of refrigerant in an existing system to a refrigerant with a different refrigerant designation shall only be allowed where in accordance with the following:

1.  The owner or the owner's authorized agent shall be notified prior to making a change of refrigerant, and the change of refrigerant shall not be made where the owner objects to the change.

2.	The change in refrigerant shall be in accordance with one of the following.

2.1	Written instructions of the original equipment manufacturer.

2.2	An evaluation of the system by a registered design professional or by an approved agency that validates safety and suitability of the replacement refrigerant.

2.3	Approved by the code official.

3.	Where the replacement refrigerant is classified into the same safety group, requirements that were applicable to the existing system shall continue to apply.

4.	Where the replacement refrigerant is classified into a different safety group, the system shall comply with the requirements of this standard for a new installation, and the change of refrigerant shall require code official approval.

1102.2.1 Mixing. Refrigerants, including refrigerant blends, with different designations in ASHRAE 34 shall not be mixed in a system.

Exception: Addition of a second refrigerant is allowed where permitted by the equipment or appliance manufacturer to improve oil return at low temperatures. The refrigerant and amount added shall be in accordance with the manufacturer’s instructions.

1102.2.1 Mixing.

Refrigerants with different refrigerant designations shall only be mixed in a system in accordance with both of the following:

1.	The addition of a second refrigerant is allowed by the equipment manufacturer and is in accordance with the manufacturer’s written instructions.

2.	The resulting mixture does not change the refrigerant safety group.

(M11369 / M73-21 AMPC1)

1104.3.1 Air conditioning for human comfort. In other than industrial occupancies where the quantity in a single independent circuit does not exceed the amount in Table 1103.1, Group B1, B2 and B3 refrigerants shall not be used in high-probability systems for air conditioning for human comfort. High probability systems used for human comfort shall use Group A1 or A2L refrigerant.

Exceptions:

1.	Equipment listed for and used in residential occupancies containing a maximum of 6.6 pounds (3 kg) of refrigerant.

2.	Equipment listed for and used in commercial occupancies containing a maximum of 22 pounds (10 kg) of refrigerant.

3.	Industrial occupancies.

1104.3.2 Nonindustrial occupancies Group A2, A3, B2 and B3 refrigerants.

Group A2 and B2 refrigerants shall not be used in high-probability systems.  where the quantity of refrigerant in any independent refrigerant circuit exceeds the amount shown in Table 1104.3.2. Group A3 and B3 refrigerants shall not be used except where approved.

Exception Exceptions: This section does not apply to:

1.	laboratories Laboratories where the floor area per occupant is not less than 100 square feet (9.3 m2).

2.	Listed self contained systems having a maximum of 0.331 pounds (150 g) of Group A3 refrigerant.

3.	Industrial occupancies.

4.	Equipment listed for and used in residential occupancies containing a maximum of 6.6 pounds (3 kg) of Group A2 or B2 refrigerant.

5.	Equipment listed for and used in commercial occupancies containing a maximum of 22 pounds (10 kg) of Group A2 or B2 refrigerant.

Delete without substitution:

TABLE 1104.3.2 MAXIMUM PERMISSIBLE QUANTITIES OF REFRIGERANTS

| TYPE OF REFRIGERATION SYSTEM | MAXIMUM POUNDS FOR VARIOUS OCCUPANCIES |  |  |  |
| --- | --- | --- | --- | --- |
|  | Institutional | Public a ssembly | Residential | All other occupancies |
| Sealed absorption system |  |  |  |  |
| In exit access | 0 | 0 | 3.3 | 3.3 |
| In adjacent outdoor locations | 0 | 0 | 22 | 22 |
| In other than exit access | 0 | 6.6 | 6.6 | 6.6 |
| Unit systems |  |  |  |  |
| In other than exit access | 0 | 0 | 6.6 | 6.6 |

For SI: 1 pound = 0.454 kg.

(M11371 / M75-21 AM)

1106.4 FlammableClass 2 and 3 refrigerants. Where refrigerants of Groups A2, A3, B2 and B3 are used, the machinery room shall conform to the Class I, Division 2, hazardous location classification requirements of NFPA 70.

Exception: Machinery rooms for systems containing Group A2L refrigerants that are provided with ventilation in accordance with Section 1106.4.

(M11372 / M77-21 Part I AS)

1101.2 Factory-Built Equipment and Appliances. Listed and labeled self-contained, factory-built equipment and appliances shall be tested in accordance with UL 207, 412, 471 or 1995., UL/CSA 60335-2-40 or UL 60335-2-89 the applicable standards specified in Table 1101.2. Such equipment and appliances are deemed to meet the design, manufacture and factory test requirements of this code if installed in accordance with their listing and the manufacturer's instructions.

TABLE 1101.2

FACTORY-BUILT EQUIPMENT AND APPLIANCES

| EQUIPMENT | STANDARDS |
| --- | --- |
| Air-conditioning equipment | UL 1995 or UL/CSA 60335-2-40 |
| Packaged terminal air conditioners and heat pumps | UL 484 or UL/CSA 60335-2-40 |
| Split-system air conditioners and heat pumps | UL 1995 or UL/CSA 60335-2-40 |
| Dehumidifiers | UL 474 or UL/CSA 60335-2-40 |
| Unit coolers | UL 412 or UL/CSA 60335-2-89 |
| Commercial refrigerators, freezers, beverage coolers and walk-in coolers | UL 471 or UL/CSA 60335-2-89 |
| Refrigerating units and walk-in coolers | UL 427 or UL 60335-2-89 |
| Refrigerant-containing components and accessories | UL 207 |

1101.10 Locking access port caps. Refrigerant circuit access ports located outdoors shall be fitted with locking-type tamper-resistant caps or shall be otherwise secured to prevent unauthorized access.

Exception: This section shall not apply to refrigerant circuit access ports on equipment installed in controlled areas such as on roofs with locked access hatches or doors.

1102.3 Access port protection. Refrigerant access ports shall be protected in accordance with Section 1101.10 whenever refrigerant is added to or recovered from refrigeration or air-conditioning systems.

DELETE TABLE 1103.1 in its entirety and replace as follows:

TABLE 1103.1

REFRIGERANT CLASSIFICATION, AMOUNT AND OEL

Note: (Use text from Table 1103.1 of the 2024 IMC):

| CHEMICAL REFRIGERANT | FORMULA | CHEMICAL NAME OF BLEND | REFRIGERANT SAFETY GROUP CLASSIFICATION | AMOUNT OF REFRIGERANT PER OCCUPIED SPACE |  |  |  |  |  |  | [F] DEGREES OF HAZARD° |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | RCL |  |  | LFL |  |  | OELe |  |
|  |  |  |  | Pounds per 1,000 cubic feet lb/MCf | ppm | g/m3 | lb/MCf | ppm | g/m3 | OELe ppm |  |
| R-11d c | CCl3F | trichlorofluoromethane | A1 | 0.39 | 1,100 | 6.2 6.1 |  |  |  | C1,000 | 2-0-0b |
| R-12d c | CCl2F2 | dichlorodifluoromethane | A1 | 5.6 | 18,000 | 90 |  |  |  | 1,000 | 2-0-0b |
| R-13d c | CClF3 | chlorotrifluoromethane | A1 | — | — | — |  |  |  | 1,000 | 2-0-0b |
| R-13B1d c | CBrF3 | bromotrifluoromethane | A1 | — | — | — |  |  |  | 1,000 | 2-0-0b |
| R-13I1 | CF3I | trifluoroiodomethane | A1 | 1.0 | 2,000 | 16 |  |  |  | 500 |  |
| R-14 | CF4 | tetrafluoromethane (carbon tetrafluoride) | A1 | 25 | 110,000 | 400 |  |  |  | 1,000 | 2-0-0b |
| R-22 | CHClF2 | chlorodifluoromethane | A1 | 13 | 59,000 | 210 |  |  |  | 1,000 | 2-0-0b |
| R-23 | CHF3 | trifluoromethane (fluoroform) | A1 | 7.3 | 41,000 | 120 |  |  |  | 1,000 | 2-0-0b |
| R-30 | CH2Cl2 | dichloromethane (methylene chloride) | B1 | — | — | — |  |  |  | — | — |
| R-31 | CH2ClF | Chlorofluoromethane | — | — | — | — |  |  |  | — | — |
| R-32 | CH2F2 | difluoromethane (methylene fluoride) | A2c A2L | 4.8 | 36,000 | 77 | 19.1 | 144,000 | 306 | 1,000 | 1-4-0 |
| R-40 | CH3Cl | chloromethane (methyl chloride) | B2 | — | — | — |  |  |  | — | — |
| R-41 | CH3F | Fluoromethane (methyl fluoride) | — | — | — | — |  |  |  | — |  |
| R-50 | CH4 | methane | A3 | — | — | — |  | 50,000 |  | 1,000 | — |
| R-113d c | CCl2FCClF2 | 1,1,2-trichloro-1,2,2- trifluoroethane | A1 | 1.2 | 2,600 | 20 |  |  |  | 1,000 | 2-0-0b |
| R-114d c | CClF2CClF2 | 1,2-dichloro-1,1,2,2- tetrafluoroethane | A1 | 8.7 | 20,000 | 140 |  |  |  | 1,000 | 2-0-0b |
| R-115 | CClF2CF3 | chloropentafluoroethane | A1 | 47 | 120,000 | 760 |  |  |  | 1,000 | — |
| R-116 | CF3CF3 | hexafluoroethane | A1 | 34 | 97,000 | 550 |  |  |  | 1,000 | 1-0-0 |
| R-123 | CHCl2CF3 | 2,2-dichloro-1,1,1- trifluoroethane | B1 | 3.5 | 9,100 | 57 |  |  |  | 50 | 2-0-0b |
| R-124 | CHClFCF3 | 2-chloro-1,1,1,2- tetrafluoroethane | A1 | 3.5 | 10,000 | 56 |  |  |  | 1,000 | 2-0-0b |
| R-125 | CHF2CF3 | pentafluoroethane | A1 | 23 | 75,000 | 370 |  |  |  | 1,000 | 2-0-0b |
| R-134a | CH2FCF3 | 1,1,1,2-tetrafluoroethane | A1 | 13 | 50,000 | 210 |  |  |  | 1,000 | 2-0-0b |
| R-141b | CH3CCl2F | 1,1-dichloro-1-fluoroethane | — | 0.78 | 2,600 | 12 | 17.8 | 60,000 | 287 | 500 | 2-1-0 |
| R-142b | CH3CClF2 | 1-chloro-1, 1-difluoroethane | A2 | 5.1 | 20,000 | 83 82 | 20.4 | 80,000 | 329 | 1,000 | 2-4-0 |
| R-143a | CH3CF3 | 1,1,1-trifluoroethane | A2c A2L | 4.5 4.4 | 21,000 | 70 | 17.5 | 82,000 | 282 | 1,000 | 2-0-0b |
| R-152a | CH3CHF2 | 1,1-difluoroethane | A2 | 2.0 | 12,000 | 32 | 8.1 | 48,000 | 130 | 1,000 | 1-4-0 |
| R-170 | CH3CH3 | ethane | A3 | 0.54 | 7,000 | 8.7 8.6 | 2.4 | 31,000 | 38 | 1,000 | 2-4-0 |
| R-E170 | CH3OCH3 | Methoxymethane (dimethyl ether) | A3 | 1.0 | 8,500 | 16 | 4.0 | 34,000 | 64 | 1,000 | — |
| R-218 | CF3CF2CF3 | octafluoropropane | A1 | 43 | 90,000 | 690 |  |  |  | 1,000 | 2-0-0b |
| R-227ea | CF3CHFCF3 | 1,1,1,2,3,3,3- heptafluoropropane | A1 | 36 | 84,000 | 580 |  |  |  | 1,000 | — |
| R-236fa | CF3CH2CF3 | 1,1,1,3,3,3-hexafluoropropane | A1 | 21 | 55,000 | 340 |  |  |  | 1,000 | 2-0-0b |
| R-245fa | CHF2CH2CF3 | 1,1,1,3,3-pentafluoropropane | B1 | 12 | 34,000 | 190 |  |  |  | 300 | 2-0-0b |
| R-290 | CH3CH2CH3 | propane | A3 | 0.56 0.59 | 5,300 | 9.5 | 2.4 | 21,000 | 38 | 1,000 | 2-4-0 |
| R-C318 | -(CF2)4- | octafluorocyclobutane | A1 | 41 | 80,000 | 660 650 |  |  |  | 1,000 | — |
| R-400d c | zeotrope | R-12/114 (50.0/50.0) | A1 | 10 | 28,000 | 160 |  |  |  | 1,000 | 2-0-0b |
| R-400d c | zeotrope | R-12/114 (60.0/40.0) | A1 | 11 | 30,000 | 170 |  |  |  | 1,000 | — |
| R-401A | zeotrope | R-22/152a/124 (53.0/13.0/34.0) | A1 | 6.6 | 27,000 | 110 |  |  |  | 1,000 | 2-0-0b |
| R-401B | zeotrope | R-22/152a/124 (61.0/11.0/28.0) | A1 | 7.2 | 30,000 | 120 |  |  |  | 1,000 | 2-0-0b |
| R-401C | zeotrope | R-22/152a/124 (33.0/15.0/52.0) | A1 | 5.2 | 20,000 | 84 |  |  |  | 1,000 | 2-0-0b |

| R-402A | zeotrope | R-125/290/22 (60.0/2.0/38.0) | A1 | 17 | 66,000 | 270 |  |  |  | 1,000 | 2-0-0b |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| R-402B | zeotrope | R-125/290/22 (38.0/2.0/60.0) | A1 | 15 | 63,000 | 240 |  |  |  | 1,000 | 2-0-0b |
| R-403A | zeotrope | R-290/22/218 (5.0/75.0/20.0) | A2 | 7.6 | 33,000 | 120 |  |  |  | 1,000 | 2-0-0b |
| R-403B | zeotrope | R-290/22/218 (5.0/56.0/39.0) | A1 | 18 | 70,000 68,000 | 290 |  |  |  | 1,000 | 2-0-0b |
| R-404A | zeotrope | R-125/143a/134a (44.0/52.0/4.0) | A1 | 31 | 130,000 | 500 |  |  |  | 1,000 | 2-0-0b |
| R-405A | zeotrope | R-22/152a/142b/C318 (45.0/7.0/5.5/2.5) | — | 16 | 57,000 | 260 |  |  |  | 1,000 | — |
| R-406A | zeotrope | R-22/600a/142b (55.0/4.0/41.0) | A2 | 4.7 | 21,000 | 25 75 | 18.8 | 82,000 | 301.9 | 1,000 | — |
| R-407A | zeotrope | R-32/125/134a (20.0/40.0/40.0) | A1 | 19 | 83,000 | 300 |  |  |  | 1,000 | 2-0-0b |
| R-407B | zeotrope | R-32/125/134a (10.0/70.0/20.0) | A1 | 21 | 79,000 | 330 |  |  |  | 1,000 | 2-0-0b |
| R-407C | zeotrope | R-32/125/134a (23.0/25.0/52.0) | A1 | 18 | 81,000 | 290 |  |  |  | 1,000 | 2-0-0b |
| R-407D | zeotrope | R-32/125/134a (15.0/15.0/70.0) | A1 | 16 | 68,000 | 250 |  |  |  | 1,000 | 2-0-0b |
| R-407E | zeotrope | R-32/125/134a (25.0/15.0/60.0) | A1 | 17 | 80,000 | 280 |  |  |  | 1,000 | 2-0-0b |
| R-407F | zeotrope | R-32/125/134a (30.0/30.0/40.0) | A1 | 20 | 95,000 | 320 |  |  |  | 1,000 | — |
| R-407G | zeotrope | R-32/125/134a (2.5/2.5/95.0) | A1 | 13 | 52,000 | 210 |  |  |  | 1,000 | — |
| R-407H | zeotrope | R-32/125/134a (32.5/15.0/52.5) | A1 | 19 | 92,000 | 300 |  |  |  | 1,000 | — |
| R-407I | zeotrope | R-32/125/124a (19.5/8.5/72.0) | A1 | 16 | 71,100 | 250 |  |  |  | 1,000 |  |
| R-408A | zeotrope | R-125/143a/22 (7.0/46.0/47.0) | A1 | 21 | 95,000 94,000 | 340 330 |  |  |  | 1,000 | 2-0-0b |
| R-409A | zeotrope | R-22/124/142b (60.0/25.0/15.0) | A1 | 7.1 | 29,000 | 110 |  |  |  | 1,000 | 2-0-0b |
| R-409B | zeotrope | R-22/124/142b (65.0/25.0/10.0) | A1 | 7.3 | 30,000 | 120 |  |  |  | 1,000 | 2-0-0b |
| R-410A | zeotrope | R-32/125 (50.0/50.0) | A1 | 26 | 140,000 | 420 |  |  |  | 1,000 | 2-0-0b |
| R-410B | zeotrope | R-32/125 (45.0/55.0) | A1 | 27 | 140,000 | 430 |  |  |  | 1,000 | 2-0-0b |
| R-411A | zeotrope | R-127/22/152a (1.5/87.5/11.0) | A2 | 2.9 | 14,000 | 46 | 11.6 | 55,000 | 185.6 | 990 970 | — |
| R-411B | zeotrope | R-1270/22/152a (3.0/94.0/3.0) | A2 | 2.8 | 13,000 | 45 | 14.8 | 70,000 | 238.3 | 980 940 | — |
| R-412A | zeotrope | R-22/218/142b (70.0/5.0/25.0) | A2 | 5.1 | 22,000 | 82 | 20.5 | 87,000 | 328.6 | 1,000 | — |
| R-413A | zeotrope | R-218/134a/600a (9.0/88.0/3.0) | A2 | 5.8 | 22,000 | 94 93 | 23.4 | 88,000 | 374.9 | 1,000 | — |
| R-414A | zeotrope | R-22/124/600a/142b (51.0/28.5/4.0/16.5) | A1 | 6.4 | 26,000 | 100 |  |  |  | 1,000 | — |
| R-414B | zeotrope | R-22/124/600a/142b (50.0/39.0/1.5/9.5) | A1 | 6.0 | 23,000 | 95 96 |  |  |  | 1,000 | — |

| R-415A | zeotrope | R-22/152a (82.0/18.0) | A2 | 2.9 | 14,000 | 47 | 11.7 | 56,000 | 187.9 | 1,000 | — |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| R-415B | zeotrope | R-22/152a (25.0/75.0) | A2 | 2.1 | 12,000 | 34 | 8.4 | 47,000 | 135.1 | 1,000 | — |
| R-416A | zeotrope | R-134a/124/600 (59.0/39.5/1.5) | A1 | 3.9 | 14,000 | 62 |  |  |  | 1,000 | 2-0-0b |
| R-417A | zeotrope | R-125/134a/600 (46.6/50.0/3.4) | A1 | 3.5 | 13,000 | 56 55 |  |  |  | 1,000 | 2-0-0b |
| R-417B | zeotrope | R-125/134a/600 (79.0/18.3/2.7) | A1 | 4.3 | 15,000 | 70 69 |  |  |  | 1,000 | — |
| R-417C | zeotrope | R-125/134a/600 (19.5/78.8/1.7) | A1 | 5.4 | 21,000 | 87 |  |  |  | 1,000 | — |
| R-418A | zeotrope | R-290/22/152a (1.5/96.0/2.5) | A2 | 4.8 | 22,000 | 77 | 19.2 | 89,000 | 308.4 | 1,000 | — |
| R-419A | zeotrope | R-125/134a/E170 (77.0/19.0/4.0) | A2 | 4.2 | 15,000 | 67 | 16.7 | 60,000 | 268.6 | 1,000 | — |
| R-419B | zeotrope | R-125/134a/E170 (48.5/48.0/3.5) | A2 | 4.6 | 17,000 | 74 | 18.5 | 69,000 | 297.3 | 1,000 | — |
| R-420A | zeotrope | R-134a/142b (88.0/12.0) | A1 | 12 | 45,000 44,000 | 190 180 |  |  |  | 1,000 | 2-0-0b |
| R-421A | zeotrope | R-125/134a (58.0/42.0) | A1 | 17 | 61,000 | 280 |  |  |  | 1,000 | 2-0-0b |
| R-421B | zeotrope | R-125/134a (85.0/15.0) | A1 | 21 | 69,000 | 330 |  |  |  | 1,000 | 2-0-0b |
| R-422A | zeotrope | R-125/134a/600a (85.1/11.5/3.4) | A1 | 18 | 63,000 | 290 |  |  |  | 1,000 | 2-0-0b |
| R-422B | zeotrope | R-125/134a/600a (55.0/42.0/3.0) | A1 | 16 | 56,000 | 250 |  |  |  | 1,000 | 2-0-0b |
| R-422C | zeotrope | R-125/134a/600a (82.0/15.0/3.0) | A1 | 18 | 62,000 | 290 |  |  |  | 1,000 | 2-0-0b |
| R-422D | zeotrope | R-125/134a/600a (65.1/31.5/3.4) | A1 | 16 | 58,000 | 260 |  |  |  | 1,000 | 2-0-0b |
| R-422E | zeotrope | R-125/134a/600a (58.0/39.3/2.7) | A1 | 16 | 57,000 | 260 |  |  |  | 1,000 | — |
| R-423A | zeotrope | R-134a/227ea (52.5/47.5) | A1 | 19 | 59,000 | 310 300 |  |  |  | 1,000 | 2-0-0c |
| R-424A | zeotrope | R-125/134a/600a/600/601a (50.5/47.0/0.9/1.0/0.6) | A1 | 6.2 | 23,000 | 100 |  |  |  | 970 990 | 2-0-0b |
| R-425A | zoetrope | R-32/134a/227ea (18.5/69.5/12.0) | A1 | 16 | 72,000 | 260 |  |  |  | 1,000 | 2-0-0b |
| R-426A | zeotrope | R-125/134a/600a/601a (5.1/93.0/1.3/0.6) | A1 | 5.2 | 20,000 | 83 |  |  |  | 990 | — |
| R-427A | zeotrope | R-32/125/143a/134a (15.0/25.0/10.0/50.0) | A1 | 18 | 79,000 | 290 |  |  |  | 1,000 | 2-1-0 |
| R-428A | zeotrope | R-125/143a/290/600a (77.5/20.0/0.6/1.9) | A1 | 23 | 83,000 84,000 | 370 |  |  |  | 1,000 | — |
| R-429A | zeotrope | R-E170/152a/600a (60.0/10.0/30.0) | A3 | 0.81 | 6,300 | 13 | 3.2 | 25,000 | 83.8 | 1,000 | — |
| R-430A | zeotrope | R-152a/600a (76.0/24.0) | A3 | 1.3 | 8,000 | 21 | 5.2 | 32,000 | 44.0 | 1,000 | — |
| R-431A | zeotrope | R-290/152a (71.0/29.0) | A3 | 0.69 0.68 | 5,500 | 11 | 2.7 | 22,000 | 38.6 | 1,000 | — |
| R-432A | zeotrope | R-1270/E170 (80.0/20.0) | A3 | 0.13 | 1,200 | 2.1 | 2.4 | 22,000 | 39.2 | 700 550 | — |
| R-433A | zeotrope | R-1270/290 (30.0/70.0) | A3 | 0.34 | 3,100 | 5.5 | 2.4 | 20,000 | 32.4 | 880 760 | — |
| R-433B | zeotrope | R-1270/290 (5.0-95.0) | A3 | 0.51 0.39 | 4,500 3,500 | 8.1 6.3 | 2.0 | 18,000 | 32.1 | 950 | — |
| R-433C | zeotrope | R-1270/290 (25.0-75.0) | A3 | 0.41 | 3,600 3,700 | 6.6 6.5 | 2.0 | 18,000 | 83.8 | 790 | — |
| R-434A | zeotrope | R-125/143a/600a (63.2/18.0/16.0/2.8) | A1 | 20 | 73,000 | 320 |  |  |  | 1,000 | — |
| R-435A | zeotrope | R-E170/152a (80.0/20.0) | A3 | 1.1 | 8,500 | 17 | 4.3 | 34,000 | 68.2 | 1,000 | — |
| R-436A | zeotrope | R-290/600a (56.0/44.0) | A3 | 0.50 | 4,000 | 8.1 | 2.0 | 16,000 | 32.3 | 1,000 | — |
| R-436B | zeotrope | R-290/600a (52.0/48.0) | A3 | 0.51 | 4,000 | 8.1 8.2 | 2.0 | 16,000 | 32.7 | 1,000 | — |
| R-436C | zeotrope | R-290/600a (95.0/5.0) | A3 | 0.57 | 5,000 | 9.1 | 2.3 | 20,000 | 36.5 | 1,000 |  |
| R-437A | zeotrope | R-125/134a/600/601 (19.5/78.5/1.4/0.6) | A1 | 5.0 5.1 | 19,000 | 82 |  |  |  | 990 | — |
| R-438A | zeotrope | R-32/125/134a/600/601a (8.5/45.0/44.2/1.7/0.6) | A1 | 4.9 | 20,000 | 79 |  |  |  | 990 | — |
| R-439A | zeotrope | R-32/125/600a (50.0/47.0/3.0) | A2 | 4.7 | 26,000 | 76 | 18.9 | 104,000 | 303.3 | 990 1,000 | — |
| R-440A | zeotrope | R-290/134a/152a (0.6/1.6/97.8) | A2 | 1.9 | 12,000 | 31 | 7.8 | 46,000 | 124.7 | 1,000 | — |
| R-441A | zeotrope | R-170/290/600a/600 (3.1/54.8/6.0/36.1) | A3 | 0.39 | 3,200 | 6.3 | 2.0 | 16,000 | 31.7 | 1,000 | — |
| R-442A | zeotrope | R-32/125/134a/152a/227ea (31.0/31.0/30.0/3.0/5.0) | A1 | 21 | 100,000 | 330 |  |  |  | 1,000 | — |
| R-443A | zeotrope | R-1270/290/600a (55.0/40.0/5.0) | A3 | 0.19 | 1,700 | 3.1 | 2.2 | 20,000 | 35.6 | 580 640 | — |
| R-444A | zeotrope | R-32/152a/1234ze(E) (12.0/5.0/83.0) | A2c A2L | 5.1 | 21,000 | 81 | 19.9 | 82,000 | 324.8 | 850 | — |
| R-444B | zeotrope | R-32/152a/1234ze(E) (41.5/10.0/48.5) | A2c A2L | 4.3 | 23,000 | 69 | 17.3 | 93,000 | 277.3 | 890 930 | — |
| R-445A | zeotrope | R-744/134a/1234ze(E) (6.0/9.0/85.0) | A2c A2L | 4.2 | 16,000 | 67 | 2.7 | 63,000 | 347.4 | 930 | — |
| R-446A | zeotrope | R-32/1234ze(E)/600 (68.0/29.0/3.0) | A2c A2L | 2.5 | 16,000 | 39 | 13.5 | 62,000 | 217.4 | 960 | — |
| R-447A | zeotrope | R-32/125/1234ze(E) (68.0/3.5/28.5) | A2c A2L | 2.6 | 16,000 | 42 | 18.9 | 65,000 | 303.5 | 900 960 | — |
| R-447B | zeotrope | R-32/125/1234ze(E) (68.0/8.0/24.0) | A2c A2L | 232.6 | 30,000 16,000 | 360 42 | 20.6 | 121,000 | 312.7 | 970 |  |
| R-448A | zeotrope | R-32/125/1234yf/134a/1234ze(E) (26.0/26.0/20.0/21.0/7.0) | A1 | 24 | 110,000 | 390 |  |  |  | 890 860 | — |
| R-449A | zeotrope | R-32/125/1234yf/134a (24.3/24.7/25.3/25.7) | A1 | 23 | 100,000 | 370 |  |  |  | 830 840 | — |
| R-449B | zeotrope | R-32/125/1234yf/134a (25.2/24.3/23.2/27.3) | A1 | 23 | 100,000 | 370 |  |  |  | 850 |  |
| R-449C | zeotrope | R-32/125/1234yf/134a (20.0/20.0/31.0/29.0) | A1 | 23 | 98,000 | 360 |  |  |  | 800 |  |
| R-450A | zeotrope | R-134a/1234ze(E) (42.0/58.0) | A1 | 20 | 72,000 | 320 |  |  |  | 880 | — |
| R-451A | zeotrope | R-1234yf/134a (89.8/10.2) | A2c A2L | 5.3 5.0 | 18,000 | 81 | 20.3 | 70,000 | 326.6 | 520 530 | — |
| R-451B | zeotrope | R-1234yf/134a (88.8/11.2) | A2c A2L | 5.3 5.0 | 18,000 | 81 | 20.3 | 70,000 | 326.6 | 530 | — |
| R-452A | zeotrope | R-32/125/1234yf (11.0/59.0/30.0) | A1 | 27 | 10,000 100,000 | 440 |  |  |  | 780 790 | — |
| R-452B | zeotrope | R-32/125/1234yf (67.0/7.0/26.0) | A2c A2L | 23 4.8 | 30,000 | 360 77 | 19.3 | 119,000 | 310.5 | 870 | — |
| R-452C | zeotrope | R-32/125/1234yf (12.5/61.0/26.5) | A1 | 27 | 100,000 | 430 |  |  |  | 800 810 |  |
| R-453A | zeotrope | R-32/125/134a/227ea/600/601a (20.0/20.0/53.8/5.0/0.6/0.6) | A1 | 7.8 | 34,000 | 120 |  |  |  | 1,000 |  |
| R-454A | zeotrope | R-32/1234yf (35.0/65.0) | A2c A2L | 28 3.2 | 16,000 | 450 52 | 18.3 | 63,000 | 293.9 | 690 |  |
| R-454B | zeotrope | R-32/1234yf (68.9/31.1) | A2c A2L | 22 3.1 | 19,000 | 360 49 | 22.0 | 77,000 | 352.6 | 850 |  |
| R-454C | zeotrope | R-32/1234yf (21.5/78.5) | A2c A2L | 29 4.4 | 19,000 | 460 71 | 18.0 | 62,000 | 289.5 | 620 |  |
| R-455A | zeotrope | R-744/32/1234yf (3.0/21.5/75.5) | A2c A2L | 23 4.9 | 30,000 22,000 | 380 79 | 26.9 | 118,000 | 432.1 | 650 |  |
| R-456A | zeotrope | R-32/134a/1234ze(E) (6.0/45.0/49.0) | A1 | 20 | 77,000 | 320 |  |  |  | 900 |  |
| R-457A | zeotrope | R-32/1234yf/152a (18.0/70.0/12.0) | A2c A2L | 25 3.4 | 15,000 | 400 54 | 13.5 | 60,000 | 216.3 | 650 |  |
| R-457B | zeotrope | R-32/1234yf/152a (35.0/55.0/10.0) | A2L | 3.7 | 19,000 | 59 | 14.9 | 76,000 | 239 | 730 |  |
| R-458A | zeotrope | R-32/125/134a/227ea/236fa (20.5/4.0/61.4/13.5/0.6) | A1 | 18 | 76,000 | 280 |  |  |  | 1,000 |  |
| R-459A | zeotrope | R-32/1234yf/1234ze(E) (68.0/26.0/6.0) | A2c A2L | 23 4.3 | 27,000 | 360 69 | 17.4 | 107,000 | 278.7 | 870 |  |
| R-459B | zeotrope | R-32/1234yf/1234ze(E) (21.0/69.0/10.0) | A2c A2L | 30 | 16,000 25,000 | 470 92 | 23.3 | 99,000 | 373.5 | 640 |  |
| R-460A | zeotrope | R-32/125/134a/1234ze(E) (12.0/52.0/14.0/22.0) | A1 | 24 | 92,000 | 380 |  |  |  | 650 950 |  |
| R-460B | zeotrope | R-32/125/134a/1234ze(E) (28.0/25.0/20.0/27.0) | A1 | 25 | 120,000 | 400 |  |  |  | 950 |  |
| R-460C | zeotrope | R-32/125/134a/1234ze(E) (2.5/2.5/46.0/49.0) | A1 | 20 | 73,000 | 310 |  |  |  | 900 |  |
| R-461A | zeotrope | R-32/125/134a/1234ze(E) (2.5/2.5/46.0/49.0) | A1 | 17 | 61,000 | 270 |  |  |  | 1,000 |  |
| R-462A | zeotrope | R-125/143a/134a/227ea/600a (55.0/5.0/32.0/5.0/3.0) | A2 | 3.9 | 16,000 | 62 | 16.6 | 105,000 | 265.8 | 1,000 |  |
| R-463A | zeotrope | R-744/32/125/1234yf/134a (6.0/36.0/30.0/14.0/14.0) | A1 | 19 | 98,000 | 300 |  |  |  | 990 |  |
| R-464A | zeotrope | R-32/125/1234ze(E)/227ea (27.0/27.0/40.0/6.0) | A1 | 27 | 120,000 | 430 |  |  |  | 930 |  |
| R-465A | zeotrope | R-32/290/1234yf (21.0/7.9/71.1) | A2 | 2.5 | 12,000 | 40 | 10.0 | 98,000 | 160.9 | 660 |  |
| R-466A | zeotrope | R-32/125/13I1 (49.0/11.5/39.5) | A1 | 6.2 | 30,000 | 99 |  |  |  | 860 |  |
| R-467A | zeotrope | R-32/125/134a/600a (22.0/5.0/72.4/0.6) | A2L | 6.7 | 31,000 | 110 |  |  |  | 1,000 |  |
| R-468A | zeotrope | R-1132a/32/1234yf (3.5/21.5/75.0) | A2L | 4.1 | 18,000 | 66 |  |  |  | 610 |  |
| R-469A | zeotrope | R-744/R-32/R-125 (35.0/32.5/32.5) | A1 | 8 | 53,000 | 130 |  |  |  | 1,600 |  |
| R-470A | zeotrope | R-744/32/125/134a/1234ze(E)/227ea (10.0/17.0/19.0/7.0/44.0/3.0) | A1 | 17 | 77,000 | 270 |  |  |  | 1,100 |  |
| R-470B | zeotrope | R-744/32/125/134a/1234ze(E)/227ea (10.0/11.5/11.5/3.0/57.0/7.0) | A1 | 16 | 72,000 | 260 |  |  |  | 1,100 |  |
| R-471A | zeotrope | R-1234ze(E)/227ea/1336mzz(E) (78.7/4.3/17.0) | A1 | 9.7 | 31,000 | 160 |  |  |  | 710 |  |
| R-472A | zeotrope | R-744/32/134a (69.0/12.0/19.0) | A1 | 4.5 | 35,000 | 72 |  |  |  | 2,700 |  |
| R-500e d | azeotrope | R-744/32/125/1234yf/134a (6.0/36.0/30.0/14.0/14.0) | A1 | 7.6 7.4 | 30,000 29,000 | 120 |  |  |  | 1,000 | 2-0-0b |
| R-501d c | azeotrope | R-22/12 (75.0/25.0) | A1 | 13 | 54,000 | 210 |  |  |  | 1,000 | — |
| R-502e d | azeotrope | R-22/115 (48.8/51.2) | A1 | 21 | 73,000 | 330 |  |  |  | 1,000 | 2-0-0b |
| R-503e d | azeotrope | R-23/13 (40.1/59.9) | — | — | — | — |  |  |  | 1,000 | 2-0-0b |
| R-504d c | azeotrope | R-32/115 (48.2/51.8) | — | 28 | 140,000 | 450 |  |  |  | 1,000 | — |
| R-507A | azeotrope | R-125/143a (50.0/50.0) | A1 | 32 | 130,000 | 520 510 |  |  |  | 1,000 | 2-0-0b |
| R-508A | azeotrope | R-23/116 (39.0/61.0) | A1 | 14 | 55,000 | 220 |  |  |  | 1,000 | 2-0-0b |
| R-508B | azeotrope | R-23/116 (46.0/54.0) | A1 | 13 | 52,000 | 200 |  |  |  | 1,000 | 2-0-0b |
| R-509A | azeotrope | R-22/218 (44.0/56.0) | A1 | 24 | 75,000 | 390 380 |  |  |  | 1,000 | 2-0-0b |
| R-510A | azeotrope | R-E170/600a (88.0/12.0) | A3 | 0.87 | 7,300 | 14 | 3.5 | 29,000 | 56.1 | 1,000 | — |
| R-511A | azeotrope | R-290/E170 (95.0/5.0) | A3 | 0.59 | 5,300 | 9.5 | 2.4 | 21,000 | 38.0 | 1,000 | — |
| R-512A | azeotrope | R-134a/152a (5.0/95.0) | A2 | 1.9 | 11,000 | 31 | 7.7 | 45,000 | 123.9 | 1,000 | — |
| R-513A | azeotrope | R-1234yf/134a (56.0/44.0) | A1 | 20 | 72,000 | 320 |  |  |  | 650 | — |
| R-513B | azeotrope | R-1234yf/134a (58.5/41.5) | A1 | 21 | 74,000 | 330 |  |  |  | 640 |  |
| R-514A | azeotrope | R-1336mzz(Z)/1130 (E) (74.7/25.3) | B1 | 0.86 | 2,400 | 14 |  |  |  | 320 |  |
| R-515A | azeotrope | R-1234ze(E)/227ea (88.0/12.0) | A1 | 19 | 62,000 63,000 | 300 |  |  |  | 810 |  |
| R-515B | azeotrope | R-1234ze(E)/227ea (91.1/8.9) | A1 | 18 | 61,000 | 290 |  |  |  | 810 |  |
| R-516A | azeotrope | R-1234yf/134a/152a (77.5/8.5/14.0) | A2 | 7.0 3.2 | 27,000 13,000 | 110 52 | 13.1 | 50,000 | 210.1 | 590 |  |
| R-600 | CH3CH2CH2CH3 | butane | A3 | 0.15 | 1,000 | 2.4 | 3.0 | 20,000 | 48 | 1,000 | 1-4-0 |
| R-600a | CH(CH3)2CH3 | 2-methylpropane (isobutane) | A3 | 0.59 | 4,000 | 9.6 9.5 | 2.4 | 16,000 | 38 | 1,000 | 2-4-0 |
| R-601 | CH3CH2CH2 CH2CH3 | pentane | A3 | 0.18 | 1,000 | 2.9 | 2.2 | 12,000 | 35 | 600 | — |
| R-601a | (CH3)2CHCH2CH3 | 2-methylbutane (isopentane) | A3 | 0.18 | 1,000 | 2.9 | 2.4 | 13,000 | 38 | 600 | — |
| R-610 | ethoxyethane (ethyl ether) | CH3CH2OCH2CH3 | — | — | — | — |  |  |  | 400 | — |
| R-611 | methyl formate | HCOOCH3 | B2 | — | — | — |  |  |  | 100 | — |
| R-718 | H2O | water | A1 | — | — | — |  |  |  | — | 0-0-0 |
| R-744 | CO2 | carbon dioxide | A1 | 4.5 | 40,000 | 72 |  |  |  | 5,000 | 2-0-0b |
| R-1130(E) | CHCl=CHCl | Trans-1,2-dichloroethene | B1B2 | 0.25 | 1,000 | 4 | 16 | 65,000 | 258 | 200 |  |
| R-1132a | CF2 = CH2 | 1, 1-difluoroethylene | A2 | 2.0 | 13,000 | 33 | 8.1 | 50,000 | 131 | 500 |  |
| R-1150 | CH2=CH2 | ethene (ethylene) | A3 | — | — | — | 2.2 | 31,000 | 36 | 200 | 1-4-2 |
| R-1224yd(Z) | CF3CF=CHCl | (Z)-1-chloro-2,3,3,3-tetrafluoropropen | A1 | 23 | 60,000 | 360 370 |  |  |  | 1,000 |  |
| R-1233zd(E) | CF3CH=CHCl | trans-1-chloro-3,3,3-trifluoro- 1-propene | A1 | 5.3 | 16,000 | 85 |  |  |  | 800 | — |
| R-1234yf | CF3CF=CH2 | 2,3,3,3-tetrafluoro-1 propene | A2c A2L | 4.7 4.5 | 16,000 | 75 | 18.0 | 62,000 | 289 | 500 | — |
| R-1234ze(E) | CF3CH=CHF CF3CH=CFH | trans-1,3,3,3-tetrafluoro-1 - propene | A2c A2L | 4.7 | 16,000 | 75 76 | 18.8 | 65,000 | 303 | 800 | — |
| R-1270 | CH3CH=CH2 | Propene (propylene) | A3 | 0.1 | 1,000 | 1.7 |  |  |  | 500 | 1-4-1 |
| R-1336mzz(E) | CF3CH=CHCF3 | trans 1,1,1,4,4,4-hexafluoro-2- butene | A1 | 3.0 | 7,200 | 48 |  |  |  | 400 |  |
| R-1336mzz(Z) | CF3CH=CHCF3 | Cis-1,1,1,4,4,4-hexaflouro-2-butene | A1 | 5.4 5.2 | 13,000 | 87 84 |  |  |  | 500 |  |

SI: 1 pound = 0.454 kg, 1 cubic foot = 0.02832 m3

  - Degrees of  hazard  are  for  health,  fire,  and  reactivity,  respectively,  in  accordance  with  NFPA  704.

  - Reduction to 1-0-0 is allowed if analysis satisfactory to the code official shows that the maximum concentration for a rupture or full loss of refrigerant charge would not exceed the IDLH, considering both the refrigerant quantity and room volume.

c. 	Class I ozone depleting substance; prohibited for new installations.

d. 	Occupational Exposure Limit based on the OSHA PEL, ACGIH TLV-TWA, the TERA WEEL or consistent value on a time-weighed average (TWA) basis (unless noted C for ceiling) for an 8 hr/d and 40 hr/wk.

1104.3.2 Nonindustrial occupancies Group A2, A3, B2 and B3 refrigerants. Group A2 and B2 refrigerants shall not be used in high-probability systems where the quantity of refrigerant in any independent refrigerant circuit exceeds the amount shown in Table 1104.3.2. Group A2 and B2 refrigerants shall not be used in high-probability systems. Group A3 and B3 refrigerants shall not be used except where approved.

Exceptions: This section does not apply to:

- Laboratories where the floor area per occupant is not less than 100 square feet (9.3 m2).

- Listed self-contained systems having a maximum of 0.331 pounds (150 g) of Group A3 refrigerant.

- Industrial occupancies.

- Equipment listed for and used in residential occupancies containing a maximum of 6.6 pounds (3 kg) of Group A2 or B2 refrigerant.

- Equipment listed for and used in commercial occupancies containing a maximum of 22 pounds (10 kg) of Group A2 or B2 refrigerant.

1105.6.1.1 Indoor exhaust opening location. Indoor mechanical exhaust intake openings shall be located where refrigerant leakage is likely to concentrate based on the refrigerant’s relative density to air, and the locations of the air current paths and refrigerating machinery.

[F] 1105.9 Emergency pressure control system. Permanently installed refrigeration systems containing more than 6.6 pounds (3 kg) of flammable, toxic or highly toxic refrigerant or ammonia shall be provided with an eEmergency pressure control system shall be provided in accordance with the Florida Fire Prevention Code.

[BE] 1105.10 Means of egress. Machinery rooms larger than 1,000 square feet (93 m2) shall have not less than two exits or exit access doorways. Where two exit access doorways are required, one such doorway is permitted to be served by a fixed ladder or an alternating tread device. Exit access doorways shall be separated by a horizontal distance equal to one-half the maximum horizontal dimension of the room. All portions of machinery rooms shall be within 150 feet (45 720 mm) of an exit or exit access doorway. An increase in exit access travel distance is permitted in accordance with Section 1017.1 of the Florida Building Code. Exit and exit access doorways shall swing in the direction of egress travel and shall be equipped with panic hardware, regardless of the occupant load served. Exit and exit access doorways shall be tight fitting and self-closing.

1106.4 Flammable Class 2 and 3 refrigerants. Where refrigerants of Groups A2, A3, B2 and B3 are used, the machinery room shall conform to the Class I, Division 2, hazardous location classification requirements of NFPA 70.

Exceptions: Ammonia machinery rooms that are provided with ventilation in accordance with Section 1106.3.

DELETE SECTIONS [F] 1106.5 thru [F] 1106.6 in their entirety and replace with SECTION 1106.5 thru [F] 1106.7 as follows:

1106.5 Group A2L and B2L refrigerant. Machinery rooms for Group A2L and B2L refrigerant shall comply with Sections 1106.5.1 through Section 1106.5.3.

1106.5.1 Elevated temperatures. Open flame-producing devices or continuously operating hot surfaces over 1290 °F (700 °C) shall not be permanently installed in the room.

1106.5.2 Refrigerant detector. In addition to the requirements of Section 1105.3, refrigerant detectors shall signal an alarm and activate the ventilation system in accordance with the response time specified in Table 1106.5.2.

TABLE 1106.5.2 GROUP A2L and B2L DETECTOR ACTIVATION

| Activation Level | Maximum Response Time (seconds) | ASHRAE 15 Ventilation Level | Alarm Reset | Alarm Type |
| --- | --- | --- | --- | --- |
| Less than or equal to the OEL in Table 1103.1 | 300 | 1 | Automatic | Trouble |
| Less than or equal to the refrigerant concentration level in Table 1103.1 | 15 | 2 | Manual | Emergency |

1106.5.3 Mechanical ventilation. The machinery room shall have a mechanical ventilation system complying with ASHRAE 15.

[F] 1106.5 1106.6 Remote controls. Remote control of the mechanical equipment and appliances located in the machinery room shall comply with Sections 1106.5.1 1106.6.1 and 1106.5.2 1106.6.2.

[F] 1106.5.1 1106.6.1 Refrigeration system emergency shutoff. A clearly identified switch of the break-glass type or with an approved tamper-resistant cover shall provide off-only control of refrigerant compressors, refrigerant pumps, and normally closed, automatic refrigerant valves located in the machinery room. Additionally, this equipment shall be automatically shut off whenever the refrigerant vapor concentration in the machinery room exceeds the vapor detector’s upper detection limit or 25 percent of the LEL, whichever is lower.

[F] 1106.5.2 1106.6.2 Ventilation system. A clearly identified switch of the break-glass type or with an approved tamper-resistant cover shall provide on-only control of the machinery room ventilation fans.

[F] 1106.6 1106.7 Emergency signs and labels. Refrigeration units and systems shall be provided with approved emergency signs, charts, and labels in accordance with the Florida Fire Prevention Code.

SECTION 1107

PIPING MATERIAL

1107.1 Piping. Refrigerant piping material shall conform to the requirements in this section.

1107.2 Used materials. Used pipe, fittings, valves and other materials that are to be reused shall be clean and free from foreign materials and shall be approved for reuse.

1107.3 Materials rating. Materials, joints and connections shall be rated for the operating temperature and pressure of the refrigeration system. Materials shall be suitable for the type of refrigerant and type of lubricant in the refrigeration system. Magnesium alloys shall not be used in contact with any halogenated refrigerants. Aluminum, zinc, magnesium and their alloys shall not be used in contact with R-40 (methyl chloride).

1107.4 Piping materials standards. Refrigerant pipe shall conform to one or more of the standards listed in Table 1107.4. The exterior of the pipe shall be protected from corrosion and degradation.

TABLE 1107.4

REFRIGERANT PIPE

| PIPING MATERIAL | STANDARD |
| --- | --- |
| Aluminum tube | ASTM B210, ASTM B491/B491M |
| Brass (copper alloy) pipe | ASTM B43 |
| Copper linesets | ASTM B280, ASTM B1003 |
| Copper pipe | ASTM B42, ASTM B302 |
| Copper tubea | ASTM B68, ASTM B75, ASTM B88, ASTM B280, ASTM B819 |
| Steel pipeb | ASTM A53, ASTM A106, ASTM A333 |
| Steel tube | ASTM A254, ASTM A334 |

a. Soft annealed copper tubing larger than 13/8 inch (35 mm) O.D. shall not be used for field-assembled refrigerant piping unless it is protected from mechanical damage.

b. ASTM A53, Type F steel pipe shall only be permitted for discharge lines in pressure relief systems.

1107.4.1 Steel pipe Groups A2, A3, B2, and B3. The minimum weight of steel pipe for Group A2, A3, B2 and B3 refrigerants shall be Schedule 80 for sizes 1 1/2 inches or less in diameter.

1107.5 Pipe fittings. Refrigerant pipe fittings shall be approved for installation with the piping materials to be installed, and shall conform to one of more of the standards listed in Table 1107.5 or shall be listed and labeled as complying with UL 207.

TABLE 1107.5

REFRIGERANT PIPE FITTINGS

| FITTING MATERIAL | STANDARD |
| --- | --- |
| Aluminum | ASTM B361 |
| Copper and copper alloy (brass) | ASME B16.15, ASME B16.18, ASME B16.22, ASME B16.24, ASME B16.26, ASME B16.50 |
| Steel | ASTM A105, ASTM A181, ASTM A193, ASTM A234, ASTM A420, ASTM A707 |

1107.5.1 Copper brazed field swaged. The minimum and maximum cup depth of field-fabricated copper brazed swaged fitting connections shall comply with Table 1107.5.1.

TABLE 1107.5.1

COPPER BRAZED SWAGED CUP DEPTHS

| FITTING SIZE (inch) | MINIMUM DEPTH (inch) | MAXIMUM DEPTH (inch) |
| --- | --- | --- |
| 1/8 | 0.15 | 0.23 |
| 3/16 | 0.16 | 0.24 |
| 1/4 | 0.17 | 0.26 |
| 3/8 | 0.20 | 0.30 |
| 1/2 | 0.22 | 0.33 |
| 5/8 | 0.24 | 0.36 |
| 3/4 | 0.25 | 0.38 |
| 1 | 0.28 | 0.42 |
| 1 1/4 | 0.31 | 0.47 |
| 1 1/2 | 0.34 | 0.51 |
| 2 | 0.40 | 0.60 |
| 2 1/2 | 0.47 | 0.71 |
| 3 | 0.53 | 0.80 |
| 3 1/2 | 0.59 | 0.89 |
| 4 | 0.64 | 0.96 |

For SI: 1 inch = 25.4 mm.

1107.6 Valves. Valves shall be of materials that are compatible with the type of piping material, refrigerants and oils in the refrigeration system. Valves shall be listed and labeled and rated for the temperatures and pressures of the refrigeration systems in which the valves are installed.

1107.7 Flexible connectors, expansion and vibration compensators. Flexible connectors and expansion and vibration control devices shall be listed and labeled for use in refrigeration systems and pressures at which the components are installed.

DELETE SECTION 1108 FIELD TEST in its entirety and replace new SECTION 1108 as follows:

SECTION 1108

JOINTS AND CONNECTIONS

1108.1 Approval. Joints and connections shall be of an approved type. Joints and connections shall be tight for the pressure of the refrigeration system when tested in accordance with Section 1110.

1108.1.1 Joints between different piping materials. Joints between different piping materials shall be made with approved adapter fittings. Joints between dissimilar metallic piping materials shall be made with a dielectric fitting or a dielectric union conforming to dielectric tests of ASSE 1079. Adapter fittings with threaded ends between different materials shall be joined with thread lubricant in accordance with Section 1108.3.4.

1108.2 Preparation of pipe ends. Pipe shall be cut square, reamed and chamfered, and shall be free from burrs and obstructions. Pipe ends shall have full-bore openings and shall not be undercut.

1108.3 Joint preparation and installation. Where required by Sections 1108.4 through 1108.9, the preparation and installation of brazed, flared, mechanical, press-connect, soldered, threaded and welded joints shall comply with Sections 1108.3.1 through 1108.3.5.

1108.3.1 Brazed joints. Joint surfaces shall be cleaned. An approved flux shall be applied where required by the braze filler metal manufacturer. The piping being brazed shall be purged of air to remove the oxygen and filled with one of the following inert gases: oxygen-free nitrogen, helium or argon. The piping system shall be prepurged with an inert gas for a minimum time corresponding to five volume changes through the piping system prior to brazing. The pre-purge rate shall be at a minimum velocity of 100 feet per minute (0.508 m/s). The inert gas shall be directly connected to the tube system being brazed to prevent the entrainment of ambient air. After the pre-purge, the inert gas supply shall be maintained through the piping during the brazing operation at a minimum pressure of 1.0 psi (6.89 kPa) and a maximum pressure of 3.0 psi (20.67 kPa). The joint shall be brazed with a filler metal conforming to AWS A5.8.

1108.3.2 Mechanical joints. Mechanical joints shall be installed in accordance with the manufacturer's instructions.

1108.3.2.1 Flared joints. Flared fittings shall be installed in accordance with the manufacturer’s instructions. The flared fitting shall be used with the tube material specified by the fitting manufacturer. The flared tube end shall be made by a tool designed for that operation.

1108.3.2.2 Press-connect joints. Press-connect joints shall be installed in accordance with the manufacturer’s instructions.

1108.3.3 Soldered joints. Joint surfaces to be soldered shall be cleaned and a flux conforming to ASTM B813 shall be applied. The joint shall be soldered with a solder conforming to ASTM B32. Solder joints shall be limited to refrigeration systems using Group A1 refrigerant and having a pressure of less than or equal to 200 psi (1378 kPa).

1108.3.4 Threaded joints. Threads shall conform to ASME B1.1, ASME B1.13M, ASME B1.20.1 or ASME B1.20.3. Thread lubricant, pipe-joint compound or thread tape shall be applied on the external threads only and shall be approved for application on the piping material.

1108.3.5 Welded joints. Joint surfaces to be welded shall be cleaned by an approved procedure. Joints shall be welded with an approved filler metal.

1108.4 Aluminum tube. Joints between aluminum tubing or fittings shall be brazed, mechanical, press-connect or welded joints conforming to Section 1108.3.

1108.5 Copper pipe. Joints between copper or copper-alloy pipe or fittings shall be brazed, mechanical, press-connect, soldered, threaded or welded joints conforming to Section 1108.3.

1108.6 Copper tube. Joints between copper or copper-alloy tubing or fittings shall be brazed, flared, mechanical, press-connect or soldered joints.

1108.7 Steel pipe. Joints between steel pipe or fittings shall be mechanical joints, threaded, press-connect or welded joints conforming to Section 1108.3.

1108.8 Steel tube. Joints between steel tubing or fittings shall be flared, mechanical, press-connect or welded joints conforming to Section 1108.3.

DELETE SECTION [F] 1109 PERIODIC TESTING in its entirety and replace new SECTION 1109, SECTION 1110, AND SECTION 1111 as follows:

SECTION 1109

REFRIGERANT PIPE INSTALLATION

1109.1 General. Refrigerant piping installations, other than R-717 (ammonia) refrigeration systems, shall comply with the requirements of this section. The design of refrigerant piping shall be in accordance with ASME B31.5.

1109.2 Piping location. Refrigerant piping shall comply with the installation location requirements of Sections 1109.2.1 through 1109.2.7. Refrigerant piping for Groups A2L and B2L shall also comply with the requirements of Section 1109.3. Refrigerant piping for Groups A2, A3, B2 and B3 shall also comply with the requirements of Section 1109.4.

1109.2.1 Minimum height. Exposed refrigerant piping installed in open spaces that afford passage shall be not less than 7 feet 3 inches (2210 mm) above the finished floor.

1109.2.2 Refrigerant pipe enclosure. Refrigerant piping shall be protected by locating it within the building elements or within protective enclosures.

Exception: Piping protection within the building elements or protective enclosure shall not be required in any of the following locations:

- Where installed without ready access or located more than 7 feet 3 inches (2210 mm) above the finished floor.

- Where located within 6 feet (1829 mm) of the refrigerant unit or appliance.

- Where located in a machinery room complying with Section 1105.

- Outside the building:

  - Where protected from damage from the weather, including but not limited to hail, ice and snow loads.

  - Where protected from damage within the expected foot or traffic path.

  - Where installed underground not less than 8 inches (200 mm) below finished grade and protected against corrosion.

1109.2.3 Prohibited locations. Refrigerant piping shall not be installed in any of the following locations:

1. Exposed within a fire-resistance-rated exit access corridor.

2. Exposed within an interior exit stairway.

3. Within an interior exit ramp.

4. Within an exit passageway.

5. Within an elevator, dumbwaiter or other shaft containing a moving object.

1109.2.4 Piping in concrete floors. Refrigerant piping installed in concrete floors shall be encased in pipe, conduit or ducts. The piping shall be protected to prevent damage from vibration, stress and corrosion.

1109.2.5 Refrigerant pipe shafts. Refrigerant piping that penetrates two or more floor/ceiling assemblies shall be enclosed in a fire-resistance-rated shaft enclosure. The fire-resistance-rated shaft enclosure shall comply with Section 713 of the Florida Building Code.

Exceptions:

1. Refrigeration systems using R-718 refrigerant (water).

2. Piping in a direct refrigeration system using Group A1 refrigerant where the refrigerant quantity does not exceed the limits of Table 1103.1 for the smallest occupied space through which the piping passes.

3. Piping located on the exterior of the building where vented to the outdoors.

1109.2.6 Exposed piping surface temperature. Exposed piping having surface temperatures greater than 120°F (49°C) or less than 5°F (-15°C) with ready access to nonauthorized personnel shall be protected from contact or shall have thermal insulation that limits the exposed insulation surface temperature to a range of 5°F (-15°C) to 120°F (49°C).

1109.2.7 Pipe identification. Refrigerant pipe located in areas other than the room or space where the refrigerating equipment is located shall be identified. The pipe identification shall be located at intervals not exceeding 20 feet (6096 mm) on the refrigerant piping or pipe insulation. The minimum height of lettering of the identification label shall be 1/2 inch (12.7 mm). The identification shall indicate the refrigerant designation and safety group classification of refrigerant used in the piping system. For Group A2L and B2L refrigerants, the identification shall also include the following statement: “WARNING – Risk of Fire. Flammable Refrigerant.” For Group A2, A3, B2 and B3 refrigerants, the identification shall also include the following statement: "DANGER—Risk of Fire or Explosion. Flammable Refrigerant." For any Group B refrigerant, the identification shall also include the following statement: "DANGER—Toxic Refrigerant."

1109.3 Installation requirements for Group A2L, A2, A3, B2L, B2, or B3 refrigerant. Piping systems using Group A2L, A2, A3, B2L, B2, or B3 refrigerant shall comply with the requirements of Sections 1109.3.1 and 1109.3.2.

1109.3.1 Protection against physical damage. In addition to the requirements of Section 305.5, aluminum, copper and steel tube used for Group A2, A3, B2L, B2, and B3 refrigerants and located in concealed locations where tubing is installed in studs, joists, rafters or similar member spaces, and located less than 11/4 inches (32 mm) from the nearest edge of the member, shall be continuously protected by shield plates. Protective steel shield plates shall cover the area of the tube plus the area extending not less

than 2 inches (51 mm) beyond both sides of the tube.

1109.3.1.1 Shield plates. Shield plates shall be of steel material having a thickness of not less than 0.0575 inch (1.46 mm) (No.16 gage).

1109.3.2 Shaft ventilation. Refrigerant pipe shafts with systems using Group A2L or B2L refrigerant shall be naturally or mechanically ventilated. Refrigerant pipe shafts with one or more systems using any Group A2, A3, B2, or B3 refrigerant shall be continuously mechanically ventilated and shall include a refrigerant detector. The shaft ventilation exhaust outlet shall comply with Section 501.3.1. Naturally ventilated shafts shall have a pipe, duct or conduit not less than 4 inches (102 mm) in diameter that connects to the lowest point of the shaft and extends to the outdoors. The pipe, duct or conduit shall be level or pitched downward to the outdoors. Mechanically ventilated shafts shall have a minimum airflow velocity in accordance with Table 1109.3.2. The mechanical ventilation shall be continuously operated or activated by a refrigerant detector. Systems utilizing a refrigerant detector shall activate the mechanical ventilation at a maximum refrigerant concentration of 25 percent of the lower flammable limit of the refrigerant. The detector, or a sampling tube that draws air to the detector, shall be located in an area where refrigerant from a leak will concentrate. The shaft shall not be required to be ventilated for double-wall refrigerant pipe where the interstitial space of the double-wall pipe is vented to the outdoors.

TABLE 1109.3.2

SHAFT VENTILATION VELOCITY

| CROSS-SECTIONAL AREA OF SHAFT (square inches) | MINIMUM VENTILATION VELOCITY (feet per minute) |
| --- | --- |
| ≤ 20 | 100 |
| > 20 ≤ 250 | 200 |
| > 250 ≤ 1,250 | 300 |
| > 1,250 | 400 |

For SI: 1 square inch = 645 mm2, 1 foot per minute = 0.0058 m/s.

1109.4 Refrigerant pipe penetrations. The annular space between the outside of a refrigerant pipe and the inside of a pipe sleeve or opening in a building envelope wall, floor or ceiling assembly penetrated by a refrigerant pipe shall be sealed in an approved manner with caulking material or foam sealant or closed with a gasketing system. The caulking material, foam sealant or gasketing system shall be designed for the conditions at the penetration location and shall be compatible with the pipe, sleeve and building materials in contact with the sealing materials. Refrigerant pipes penetrating fire-resistance-rated assemblies or membranes of fire-resistance-rated assemblies shall be sealed or closed in accordance with Section 714 of the Florida Building Code.

1109.5 Stress and strain. Refrigerant piping shall be installed so as to prevent strains and stresses that exceed the structural strength of the pipe. Where necessary, provisions shall be made to protect piping from damage resulting from vibration, expansion, contraction and structural settlement.

1109.6 Stop valves. Stop valves shall be installed in specified locations in accordance with Sections 1109.6.1 and 1109.6.2. Stop valves shall be supported in accordance with Section 1109.6.3 and identified in accordance with Section 1109.6.4.

Exceptions:

1. Systems that have a refrigerant pumpout function capable of storing the entire refrigerant charge in a receiver or heat exchanger.

2. Systems that are equipped with provisions for pumping out the refrigerant using either portable or permanently installed refrigerant recovery equipment.

3. Self-contained listed and labeled systems.

1109.6.1 Refrigeration systems containing more than 6.6 pounds (3.0 kg) of refrigerant. Stop valves shall be installed in the following locations on refrigeration systems containing more than 6.6 pounds (3.0 kg) of refrigerant:

1. The suction inlet of each compressor, compressor unit or condensing unit.

2. The discharge outlet of each compressor, compressor unit or condensing unit.

3. The outlet of each liquid receiver.

1109.6.2 Refrigeration systems containing more than 100 pounds (45 kg) of refrigerant. In addition to stop valves required by Section 1109.6.1, refrigeration systems containing more than 100 pounds (45 kg) of refrigerant shall have stop valves installed in the following locations:

1. Each inlet of each liquid receiver.

2. Each inlet and each outlet of each condenser where more than one condenser is used in parallel.

Exceptions:

1. Stop valves shall not be required at the inlet of a receiver in a condensing unit nor at the inlet of a receiver that is an integral part of the condenser.

2. Refrigeration systems utilizing nonpositive displacement compressors.

1109.6.3 Stop valve support. Stop valves shall be supported to prevent detrimental stress and strain on the refrigerant piping system. The piping system shall not be utilized to support stop valves on copper tubing or aluminum tubing 1 inch (25.4 mm) outside diameter or larger.

1109.6.4 Identification. Stop valves shall be identified where their intended purpose is not obvious. Where valves are identified by a numbering or lettering system, legend(s) or key(s) for the valve identification shall be located in the room containing the indoor refrigeration equipment. The minimum height of lettering of the identification label shall be 1/2 inch (12.7 mm).

SECTION 1110

REFRIGERATION PIPING SYSTEM TEST

1110.1 General. Refrigerant piping systems, other than R-717 (ammonia) refrigeration systems, that are erected in the field shall be pressure tested for strength and leak tested for tightness, in accordance with the requirements of this section, after installation and before being placed in operation. Tests shall include both the high- and low-pressure sides of each system.

Exception: Listed and labeled equipment, including compressors, condensers, vessels, evaporators, gas bulk storage tanks, safety devices, pressure gauges and control mechanisms, shall not be required to be tested.

1110.2 Exposure of refrigerant piping system. Refrigerant pipe and joints installed in the field shall be exposed for visual inspection and testing prior to being covered or enclosed.

1110.3 Field test gases. The medium used for field pressure testing the refrigeration system shall be one of the following inert gases: oxygen-free nitrogen, helium argon or premixed nonflammable oxygen-free nitrogen with a tracer gas of hydrogen or helium. For R-744 refrigeration systems, carbon dioxide shall be allowed as the test medium. For R-718 refrigeration systems, water shall be allowed as the test medium.

1110.3.1 Test gases not permitted. Oxygen, air, refrigerants other than those identified in Section 1110.3, combustible gases and mixtures containing such gases shall not be used as the pressure test medium.

1110.4 Factory test procedure. Factory tests shall be performed with dry nitrogen or other nonflammable, nonreactive, dried gas. Oxygen, air or mixtures containing them shall not be used. The means used to build up the test pressure shall have either a pressure-limiting device or a pressure-reducing device and a gauge on the outlet side. The pressure-relief device shall be set above the test pressure but low enough to prevent permanent deformation of the refrigeration system’s components.

Exceptions:

- Mixtures of dry nitrogen, inert gases or a combination of them with Class 1 refrigerant in concentrations of a refrigerant weight fraction (mass fraction) not exceeding 5 percent shall be permitted for tests.

- Mixtures of dry nitrogen, inert gases or a combination of them with Class 2L, Class 2 and Class 3 refrigerants in concentrations not exceeding the lower of a refrigerant weight fraction (mass fraction) of 5 percent or 25 percent of the LFL shall be permitted for tests.

- Compressed air without added refrigerants shall be permitted for tests, provided that the refrigeration system is subsequently evacuated to less than 1,000 microns (0.1333 kPa) before charging with refrigerant. The required evacuation level is atmospheric pressure for refrigeration systems using R-718 (water) or R-744 (carbon dioxide) as the refrigerant.

- Systems erected on the premises using Group A1 refrigerant and with copper tubing not exceeding 0.62 of an inch (15.7 mm) outside diameter shall be tested by means of the refrigerant charged into the system at the saturated vapor pressure of the refrigerant at not less than 68°F (20°C).

1110.5 Test apparatus. The means used to pressurize the refrigerant piping system shall have on its outlet side a test pressure measuring device and either a pressure-limiting device or a pressure-reducing device. The test pressure measuring device shall have an accuracy of ±3 percent or less of the test pressure and shall have a resolution of 5 percent or less of the test pressure.

1110.6 Piping system strength test. Refrigeration system components and refrigerant piping shall be tested in accordance with ASME B31.5 or this section. Separate tests for isolated portions of the system are permitted, provided that all required portions are tested at least once. Pressurize with test gas for a minimum of 10 minutes to not less than the lower of (a) the lowest design pressure for any system component or (b) the lowest value of set pressure for any pressure relief devices in the system. The design pressures for determination of test pressure shall be the pressure identified on the label nameplate of the condensing unit, compressor, compressor unit, pressure vessel or other system component with a nameplate. A passing test result shall have no rupture or structural failure of any system component or refrigerant piping.

Refrigerant piping and tubing greater than 3/4 inch (19 mm) in diameter shall be tested in accordance with ASHRAE 15.

1110.7 Contractor or engineer declaration. The installing contractor or registered design professional of record shall issue a certificate of test to the code official for all refrigeration systems containing 55 pounds (25 kg) or more of refrigerant. The certificate shall give the test date, name of the refrigerant, test medium and the field test pressure applied to the high-pressure side and the low-pressure side of the system. The certification of test shall be signed by the installing contractor or registered design professional and shall be made part of the public record.

[F] SECTION 1111

PERIODIC TESTING

[F] 1109.1 1111.1 Testing required. The following emergency devices and systems shall be periodically tested in accordance with the manufacturer’s instructions and as required by the code official:

1. Treatment and flaring systems.

2. Valves and appurtenances necessary to the operation of emergency refrigeration control boxes.

3. Fans and associated equipment intended to operate emergency ventilation systems.

4. Detection and alarm systems.

(Step 2 – M12147 AS)

CHAPTER 12 HYDRONIC PIPING

1201.1 Scope. The provisions of this chapter shall govern the construction, installation, alteration and repair of hydronic piping systems. This chapter shall apply to hydronic piping systems that are part of heating, ventilation and air-conditioning systems. Such piping systems shall include steam, hot water, radiant heating, radiant cooling, chilled water, steam condensate, and ground source heat pump loop systems and snow- and ice-melting. Potable cold and hot water distribution systems shall be installed in accordance with the Florida Building Code, Plumbing

Code.

(M11427 / M85-21 AS)

# Revise as follows:

TABLE 1202.4 HYDRONIC PIPE

| MATERIAL | STANDARD (see Chapter 15) |
| --- | --- |
| Lead pipe | FS WW-P-325B |

No change to the remaining text.

(M11428 / M86-21 AS)

TABLE 1202.4 HYDRONIC PIPE

| MATERIAL | STANDARD (see Chapter 15) |
| --- | --- |
| Stainless Steel pipe | ASTM A269; ASTM A312; ASTM A554; ASTM A778 |
| Stainless Steel tubing | ASTM A269; ASTM A312; ASTM A554; ASTM A778 |

No change to the remaining text.

(M11429 / M87-21 AM)

TABLE 1202.5 HYDRONIC PIPE FITTINGS

| MATERIAL | STANDARD (see Chapter 15) |
| --- | --- |
| Copper and copper alloys | ASME B16.15; ASME B16.18; ASME B16.22; ASME B16.24; ASME B16.26; ASME B16.51; ASSE 1061; ASTM F1974 ; ASTM F3226 |
| Stainless Steel | ASTM A269; ASTM A312; ASTM A554; ASTM A778; ASTM F3226 |

No change to the remaining text.

(M11430 / M88-21 AM)

# Revise as follows:

TABLE 1210.5 GROUND-SOURCE LOOP PIPE FITTINGS

| PIPE MATERIAL | STANDARD (see Chapter 15) |
| --- | --- |
| Cross-linked polyethylene (PEX) | ASTM F877; ASTM F1807; ASTM F1960; ASTM F2080; ASTM F2159; ASTM F2434; ASTM F3347; CSA B137.5; CSA C448; NSF 358-3 |
| Raised temperature polyethylene (PE-RT) | ASTM D3261; ASTM F1807; ASTM F2159;ASTM F3347; CSA B137.1; CSA C448; NSF 358-4 |

No change to the remaining text.

TABLE 1202.5 HYDRONIC PIPE FITTINGS

| MATERIAL | STANDARD (see Chapter 15) |
| --- | --- |
| PEX fittings | ASSE 1061; ASTM F877; ASTM F1807; ASTM F2159; ASTM F3253; ASTM F3347 |

No change to the remaining text.

(M11444 / M99-21 Part I AS)

1203.20 Stainless Steel Pipe. Joints between stainless steel pipe or fittings shall be mechanical joints that are made with an approved elastomeric seal, or shall be threaded or welded joints conforming to Section 1203.3.

1203.21 Stainless Steel Tubing. Joints between stainless steel tubing or fittings shall be mechanical or welded joints conforming to Section 1203.3.

(M11438 / M91-21 AS)

1203.3.4 Solvent-cemented joints. Joint surfaces shall be clean and free from moisture. An approved primer shall be applied to CPVC and PVC pipe-joint surfaces. Joints shall be made while the cement is wet. Solvent cement conforming to the following standards shall be applied to all joint surfaces:

1.	ASTM D2235 for ABS joints.

2.	ASTM F493 for CPVC joints.

3.	ASTM D2564 for PVC joints.

CPVC joints shall be made in accordance with ASTM D2846.

Exception: For CPVC pipe joint connections, a primer is not required where all of the following conditions apply:

1.	The solvent cement used is third-party certified as conforming to ASTM F493.

2.	The solvent cement is yellow or green in color.

3.	The solvent cement is used only for joining 1/2-inch (12.7 mm) through 2-inch (51 mm) diameter CPVC pipe and fittings.

4.	The CPVC pipe or fittings are manufactured in accordance with ASTM D2846.

(M11431 / M89-21 AS)

1203.11 Polybutylene plastic pipe and tubing. Joints between polybutylene plastic pipe and tubing or fittings shall be mechanical joints conforming to Section 1203.3 or heat-fusion joints conforming to Section 1203.9.1.

1203.11.1 Heat-fusion joints. Joints shall be of the socket-fusion or butt-fusion type. Joint surfaces shall be clean and free from moisture. Joint surfaces shall be heated to melt temperatures and joined. The joint shall be undisturbed until cool. Joints shall be made in accordance with ASTM D3309.

(M11434 / M90-21 AS)

1205.1 Where required. Shutoff valves shall be installed in hydronic piping systems in the locations indicated in Sections 1205.1.1 through 1205.1.6. Access shall be provided to all full open valves and shutoff valves.

(M11439 / M92-21 AS)

1209.1 Materials. Piping for heating panels shall be standard-weight steel pipe, Type L copper tubing,polybutylene or other approved

plastic pipe or tubing rated at 100 psi (689 kPa) at 180°F (82°C).

(M11441 / M95-21 AS)

1209.3.3 Polybutylene joints. Polybutylene pipe and tubing shall be installed in continuous lengths or shall be joined by heat fusion in accordance with Section 1203.9.1.

(M11442 / M96-21 AS)

1209.6 Radiant tubing placement. Hydronic tubing to be embedded for the purpose of radiant heating or cooling shall be installed in accordance with the manufacturer’s instructions and with the tube layout and spacing in accordance with the system design. Individual tubing circuit lengths shall be installed with a variance of not more than ±10 percent from the design.

1209.6.1 Radiant tubing circuit length. The maximum circuit length of radiant tubing from a supply-and-return manifold shall not exceed the lengths specified by the system design or, in the absence of manufacturer’s specifications, the lengths specified in Table 1209.6.1.

TABLE 1209.6.1 MAXIMUM CIRCUIT LENGTH OF RADIANT TUBING FROM A SUPPLY-AND-RETURN MANIFOLD ARRANGEMENT

| NOMINAL TUBE SIZE | MAXIMUM CIRCUIT LENGTH (FEET) |
| --- | --- |
| 1/4 | 125 |
| 5/16 | 200 |
| 3/8 | 250 |
| 1/2 | 300 |
| 5/8 | 400 |
| 3/4 | 500 |
| 1 | 750 |

For SI units: 1 foot = 304.8 mm

1209.6.2 Radiant tubing circuit tags. Each individual radiant tubing circuit shall have a tag or label securely affixed to each manifold outlet to indicate the length of each circuit and the areas served.

1209.6.3 Radiant tubing drawings. The radiant tubing drawings and design report shall be provided to the building owner or the designated representative of the building owner.

(M11669 / M97-21 AS)

1210.4 Piping and tubing materials standards. Ground-source heat pump ground-loop pipe and tubing shall conform to the standards listed in Table 1210.4.

Revise as follows:

| MATERIAL | STANDARD (see Chapter 15) |
| --- | --- |
| Cross-linked polyethylene (PEX) | ASTM F876; ASTM F3253; CSA B137.5; CSA C448; NSF 358-3, ASTM F877 |

###### TABLE 1210.4 GROUND-SOURCE LOOP PIPE

No change to the remaining text.

(M11440 / M93-21 AS)

###### TABLE 1210.5 GROUND-SOURCE LOOP PIPE FITTINGS

| PIPE MATERIAL | STANDARD (see Chapter 15) |
| --- | --- |
| Cross-linked polyethylene (PEX) | ASTM F877; ASTM F1807; ASTM F1960; ASTM F2080; ASTM F2159; ASTM F2434; ASTM F3347; CSA B137.5; CSA C448; NSF 358-3 |
| Raised temperature polyethylene (PE-RT) | ASTM D3261; ASTM F1807; ASTM F2159; ASTM F3347; CSA B137.1; CSA C448; NSF 358-4 |

No change to the remaining text.

TABLE 1202.5 HYDRONIC PIPE FITTINGS

| MATERIAL | STANDARD (see Chapter 15) |
| --- | --- |
| PE-RT fittings | ASSE 1061; ASTM F1807; ASTM F2098; ASTM F2159; ASTM F2735; ASTM F2769; ASTM F3347 |
| PEX fittings | ASSE 1061; ASTM F877; ASTM F1807; ASTM F2159; ASTM F3253; ASTM F3347 |

No change to the remaining text.

(M11446 / M100-21 Part I AS)

1210.6 Joints. Joints and connections shall be of an approved type. Joints and connections shall be tight for the pressure of the ground- source loop system. Joints used underground shall be of an approved type for buried applications.

(M11448 / M101-21 AS)

CHAPTER 13 FUEL OIL PIPING AND STORAGE

Revise title for Table 1302.3 as follows:

TABLE 1302.3 FUEL OIL PIPING and Fittings

M-FBC-M – Ch.13 – Errata #1

CHAPTER 14 SOLAR SYSTEMS

No Change

CHAPTER 15 REFERENCED STANDARDS

See attached

New Appendix

Appendix C Clear Air Delivery

SECTION C101—GENERAL

C101.1 Clean air delivery capability. In Group A, B, E and I occupancies, each mechanical system shall meet the

requirements in Section C101.1.1.

Exception: Occupiable spaces where 100 percent of the supply air meets high-efficiency particulate air

filtration.

C101.1.1 Airflow for increased filtration. Mechanical systems shall be sized to accommodate a design airflow

at a total static pressure drop that assumes the utilization of a supply air filter with a Minimum Efficiency Reporting Value (MERV) of not less than 13.

(M11301 / M25-21 AMPC1,2)

Appendix E Clean Air Delivery

##### Appendix D Clean Air Delivery

User Note . The provisions contained in this appendix are not mandatory unless specifically referenced in the adopting ordinance.

About this appendix: Appendix D provides criteria for an increased protection level for occupant health by delivering and monitoring clean air in occupied areas of the certain buildings.

D101 Demand control ventilation . Group A, B, E and I occupancies shall be equipped with a minimum of one carbon dioxide sensor for every 500 square feet of occupiable space. Carbon dioxide sensors installed in accordance with this section shall meet the requirements in Sections D101.1 and D101.3. Mechanical equipment serving each zone(s) shall be equipped with controls which meet the requirements in Section D101.2.

Exception: Occupiable zones less than 500 square feet.

D101.1 Carbon dioxide sensor performance specifications . Each carbon dioxide sensor installed in accordance with Section D101 shall meet the following carbon dioxide measurement specifications as certified by the equipment manufacturer:

1.	Range lower bound less than or equal to 400 parts per million

2.	Range upper bound greater than or equal to 2,000 parts per million

3.	Accuracy within ±75 parts per million at a reading of 1,000 parts per million

4.	Output resolution less than or equal to 20 parts per million

D101.2 Mechanical system controls . Controls for the mechanical equipment installed in accordance with Section D101 shall:

1.	Receive data from the carbon dioxide sensor in the occupiable zone(s) at least once per 5 minutes

2.	Be calibrated to provide pre-established outdoor airflow rates, or be equipped with the necessary instrumentation to measure the outdoor airflow rate

3.	Be capable of adjusting the outdoor airflow rate in response to an adjustable outdoor airflow setpoint

4.	Increase the amount of outdoor air provided to each occupiable zone until the carbon dioxide level in each occupiable zone falls below a maximum threshold as defined by the user

D101.3 Carbon dioxide detection threshold level . The default detection threshold level for carbon dioxide measurement above which triggers an alert in accordance with Section D101.4 shall be set to 1,100 parts per million. The end user can modify the detection threshold level based on specific operations and needs.

D101.4 Carbon dioxide detection threshold level exceeded . When carbon dioxide levels exceed the detection threshold level established in Section D101.3, the mechanical equipment shall modify the outdoor airflow rate as required in Section D101.2. When the carbon dioxide concentration remains above the detection threshold level for a period of 30 minutes or more, the occupants in the zone shall be alerted by approved audible and visual notification devices or through a building monitoring system.

(M11302 / M26-21 AMPC1)